## MappingPrinciples
Mapping Principles
Mapping Principles: In determining the Mapping of Reliability Standards & Requirements applicable to the business units, the Compliance Assurance (CA) administrators have taken into account the IESO’s registered functions with NERC and the business objects of each business unit. This information was then corroborated with information in the NERC Reliability Standards that identify the functional entities responsible for implementing those tasks. To help the business units identify their reliability obligations and to maintain the Mapping Spreadsheet, CA applies the following principles: 1) All Standards and Requirements that apply to the IESO registered functions (BA, PA, RC, RP, TOP, TP and TSP) will be mapped to their respective Business Units and Managers. The Manager responsible for the most requirements will be designated as the Steward. For a Reliability Standard mapped to only one Manager, that Manager will also be the Steward. 2) Designated by their respective Managers, Delegates (SMEs) are also mapped and assigned Reliability Requirements to assist Managers in meeting their compliance obligations. Managers are ultimately responsible for keeping up to date with the developments of Reliability Standards under their purview and are also accountable for staying informed of changes to all internal/external compliance processes (ICP, ORCP, CMEP etc.) 3) As needed, but at least quarterly, the CA SME shall review the mapping and make the necessary changes to maintain its accuracy. The Managers involved must discuss and agree with any proposed changes to the mapping of a particular requirement before the changes can become final. Any inaccuracies reflected in the mapping can be reported to the CA SME by the Manager. 4) Where there is a disagreement or uncertainty as to the correctness of the mapping, the Standard Steward or the Standard Manager must offer an alternative before it is remapped to another BU or Staff. Upon the Managers’ request, CA will provide support to coordinate meetings to address any disagreements related to Mapping. 5) CA will report the status of mapping updates at each CCT meeting. If Managers are unable to resolve mapping disagreements amongst themselves, the matter will then be referred to the Compliance Coordination Team (CCT). 6) Where a standard that is applicable to the IESO’s functional role (BA, PA, RC, RP, TOP, TP and TSP), but is not pertinent to how the IESO performs that function; the accountability will still be mapped to a Manager who is likely in the best position (based on the BU function) to develop a response and/or confirmation of evidence for non-applicability.

## NERCGopList
Standard Number | Document Title | Req't . | Text of Requirement | Functional Entities | GO | GOP | TO
BAL-005-0.2b | Automatic Generation Control | R1. | All generation, transmission, and load operating within an Interconnection must be included within the metered boundaries of a Balancing Authority Area. | GOP |  | GOP
BAL-005-0.2b | Automatic Generation Control | R1.1. | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. | GOP |  | GOP
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R3.3. | The Cyber Asset is dial-up accessible. | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R3.2. | The Cyber Asset uses a routable protocol within a control center; or, | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2. | The risk-based assessment shall consider the following assets: | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3 | Cyber Security - Critical Cyber Asset Identification | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.6. | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R3. | Critical Cyber Asset Identification— Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i), Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R3.2. | The Cyber Asset uses a routable protocol within a control center; or, | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R3.3. | The Cyber Asset is dial-up accessible. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2. | The risk-based assessment shall consider the following assets: | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i) | Cyber Security - Critical Cyber Asset Identification | R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2. | The risk-based assessment shall consider the following assets: | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3(i)b, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R3.3. | The Cyber Asset is dial-up accessible. | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R3.2. | The Cyber Asset uses a routable protocol within a control center; or, | TO, GOP, GO | GO | GOP | TO
CIP-002-3(i)b | Cyber Security - Critical Cyber Asset Identification | R1.2.6. | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R4. | Annual Approval —The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R3.2. | The Cyber Asset uses a routable protocol within a control center; or, | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1. | Critical Asset Identification Method —The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2. | The risk-based assessment shall consider the following assets: | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time interutility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | TO, GOP, GO | GO | GOP | TO
CIP-002-3a | Cyber Security - Critical Cyber Asset Identification | R3.3. | The Cyber Asset is dial-up accessible. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R3.3. | The Cyber Asset is dial-up accessible. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.3. | Generation resources that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1. | Critical Asset Identification Method — The Responsible Entity shall identify and document a risk-based assessment methodology to use to identify its Critical Assets. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.1. | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2. | The risk-based assessment shall consider the following assets: | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.1. | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R4. | Annual Approval — The senior manager or delegate(s) shall approve annually the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1, R2, and R3 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology, the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.2. | Transmission substations that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R3.2. | The Cyber Asset uses a routable protocol within a control center; or, | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.4. | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.5. | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.6. | Special Protection Systems that support the reliable operation of the Bulk Electric System. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R1.2.7. | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R2. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. The Responsible Entity shall review this list at least annually, and update it as necessary. | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R3. | Critical Cyber Asset Identification — Using the list of Critical Assets developed pursuant to Requirement R2, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. Examples at control centers and backup control centers include systems and facilities at master and remote sites that provide monitoring and control, automatic generation control, real-time power system modeling, and real-time inter-utility data exchange. The Responsible Entity shall review this list at least annually, and update it as necessary. For the purpose of Standard CIP-002-3, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: | TO, GOP, GO | GO | GOP | TO
CIP-002-3b | Cyber Security - Critical Cyber Asset Identification | R3.1. | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, | TO, GOP, GO | GO | GOP | TO
CIP-002-4 | Cyber Security — Critical Cyber Asset Identification | R1. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. | TO, GOP, GO | GO | GOP | TO
CIP-002-4 | Cyber Security — Critical Cyber Asset Identification | R3. | Annual Approval —The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | TO, GOP, GO | GO | GOP | TO
CIP-002-4 | Cyber Security — Critical Cyber Asset Identification | R2. | Critical Cyber Asset Identification— Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. | TO, GOP, GO | GO | GOP | TO
CIP-002-4a | Cyber Security — Critical Cyber Asset Identification | R1. | Critical Asset Identification — The Responsible Entity shall develop a list of its identified Critical Assets determined through an annual application of the criteria contained in CIP-002-4 Attachment 1 – Critical Asset Criteria. The Responsible Entity shall update this list as necessary, and review it at least annually. | TO, GOP, GO | GO | GOP | TO
CIP-002-4a | Cyber Security — Critical Cyber Asset Identification | R2. | Critical Cyber Asset Identification— Using the list of Critical Assets developed pursuant to Requirement R1, the Responsible Entity shall develop a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. The Responsible Entity shall update this list as necessary, and review it at least annually. For each group of generating units (including nuclear generation) at a single plant location identified in Attachment 1, criterion 1.1, the only Cyber Assets that must be considered are those shared Cyber Assets that could, within 15 minutes, adversely impact the reliable operation of any combination of units that in aggregate equal or exceed Attachment 1, criterion 1.1. For the purpose of Standard CIP-002-4, Critical Cyber Assets are further qualified to be those having at least one of the following characteristics: • The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, • The Cyber Asset uses a routable protocol within a control center; or, • The Cyber Asset is dial-up accessible. | TO, GOP, GO | GO | GOP | TO
CIP-002-4a | Cyber Security — Critical Cyber Asset Identification | R3. | Annual Approval —The senior manager or delegate(s) shall approve annually the list of Critical Assets and the list of Critical Cyber Assets. Based on Requirements R1 and R2 the Responsible Entity may determine that it has no Critical Assets or Critical Cyber Assets. The Responsible Entity shall keep a signed and dated record of the senior manager or delegate(s)’s approval of the list of Critical Assets and the list of Critical Cyber Assets (even if such lists are null.) | TO, GOP, GO | GO | GOP | TO
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: [Violation Risk Factor: High][Time Horizon: Operations Planning] i.Control Centers and backup Control Centers; ii.Transmission stations and substations; iii.Generation resources; iv.Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v.Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi.For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | TO, GOP, GO | GO | GOP | TO
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R1.1. | 1.1. Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; | TO, GOP, GO | GO | GOP | TO
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R1.2. | 1.2. Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and | TO, GOP, GO | GO | GOP | TO
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R1.3. | 1.3. Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). | TO, GOP, GO | GO | GOP | TO
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R2. | The Responsible Entity shall: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R2.1. | 2.1 Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | TO, GOP, GO | GO | GOP | TO
CIP-002-5 | Cyber Security — BES Cyber System Categorization | R2.2. | 2.2 Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R1.1. | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R2. | The Responsible Entity shall: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R1.2. | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: [Violation Risk Factor: High][Time Horizon: Operations Planning] i.Control Centers and backup Control Centers; ii.Transmission stations and substations; iii.Generation resources; iv.Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v.Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi.For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1 | Cyber Security — BES Cyber System Categorization | R1.3. | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R1. | Each Responsible Entity shall implement a process that considers each of the following assets for purposes of parts 1.1 through 1.3: [Violation Risk Factor: High][Time Horizon: Operations Planning] i.Control Centers and backup Control Centers; ii.Transmission stations and substations; iii.Generation resources; iv.Systems and facilities critical to system restoration, including Blackstart Resources and Cranking Paths and initial switching requirements; v.Special Protection Systems that support the reliable operation of the Bulk Electric System; and vi.For Distribution Providers, Protection Systems specified in Applicability section 4.2.1 above. | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R2.2. | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R2. | The Responsible Entity shall: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R1.3. | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R1.2. | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R2.1. | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and | TO, GOP, GO | GO | GOP | TO
CIP-002-5.1a | Cyber Security — BES Cyber System Categorization | R1.1. | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R2.1. | The senior manager shall be identified by name, title, and date of designation. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R2.3. | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. | TO, GOP, GO | GO | GOP | TO
CIP-003-3 | Cyber Security - Security Management Controls | R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. (Retirement approved by FERC effective January 21, 2014.) | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP- 002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R2.1. | The senior manager shall be identified by name, title, and date of designation. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). (Retirement approved by FERC effective January 21, 2014.) | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). (Retirement approved by FERC effective January 21, 2014.) | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R5. | Access Control — The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. (Retirement approved by FERC effective January 21, 2014.) | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. (Retirement approved by FERC effective January 21, 2014.) | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendorrelated changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R2. | Leadership — The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R2.3. | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. (Retirement approved by FERC effective January 21, 2014.) | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R1. | Cyber Security Policy — The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R4. | Information Protection — The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-003-3a | Cyber Security - Security Management Controls | R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R1.1. | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R1. | Cyber Security Policy —The Responsible Entity shall document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. The Responsible Entity shall, at minimum, ensure the following: | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R6. | Change Control and Configuration Management — The Responsible Entity shall establish and document a process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R5.3. | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R5.1.2. | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R5.1. | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R5.1.1. | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R2.3. | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R4.1. | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R4. | Information Protection —The Responsible Entity shall implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R3.3. | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R3.2. | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R3.1. | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R5. | Access Control —The Responsible Entity shall document and implement a program for managing access to protected Critical Cyber Asset information. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R2.4. | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R4.2. | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R2.2. | Changes to the senior manager must be documented within thirty calendar days of the effective date. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R2.1. | The senior manager shall be identified by name, title, and date of designation. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R2. | Leadership —The Responsible Entity shall assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-4 through CIP-009-4. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R1.3. | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R1.2. | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R4.3. | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R3. | Exceptions — Instances where the Responsible Entity cannot conform to its cyber security policy must be documented as exceptions and authorized by the senior manager or delegate(s). | TO, GOP, GO | GO | GOP | TO
CIP-003-4 | Cyber Security — Security Management Controls | R5.2. | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. | TO, GOP, GO | GO | GOP | TO
CIP-003-5 | Cyber Security — Security Management Controls | R4. | The Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-003-5 | Cyber Security — Security Management Controls | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-003-5 | Cyber Security — Security Management Controls | R2. | Each Responsible Entity for its assets identified in CIP-002-5, Requirement R1, Part R1.3, shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented cyber security policies that collectively address the following topics, and review and obtain CIP Senior Manager approval for those policies at least once every 15 calendar months: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] 2.1 Cyber security awareness; 2.2 Physical security controls; 2.3 Electronic access controls for external routable protocol connections and Dial-up Connectivity; and 2.4 Incident response to a Cyber Security Incident. An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. | TO, GOP, GO | GO | GOP | TO
CIP-003-5 | Cyber Security — Security Management Controls | R1. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems, shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] 1.1 Personnel & training (CIP-004); 1.2 Electronic Security Perimeters (CIP-005) including Interactive Remote Access; 1.3 Physical security of BES Cyber Systems (CIP-006); 1.4 System security management (CIP-007); 1.5 Incident reporting and response planning (CIP-008); 1.6 Recovery plans for BES Cyber Systems (CIP-009); 1.7 Configuration change management and vulnerability assessments (CIP-010); 1.8 Information protection (CIP-011); and 1.9 Declaring and responding to CIP Exceptional Circumstances. | TO, GOP, GO | GO | GOP | TO
CIP-003-6 | Cyber Security — Security Management Controls | R4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-003-6 | Cyber Security — Security Management Controls | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-003-6 | Cyber Security — Security Management Controls | R2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] Note: An inventory, list, or discrete identification of low impact BES Cyber Systems or their BES Cyber Assets is not required. Lists of authorized users are not required. | TO, GOP, GO | GO | GOP | TO
CIP-003-6 | Cyber Security — Security Management Controls | R1.2. | 1.2 For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: 1.2.1. Cyber security awareness; 1.2.2. Physical security controls; 1.2.3. Electronic access controls for Low Impact External Routable Connectivity (LERC) and Dial-up Connectivity; and 1.2.4. Cyber Security Incident response | TO, GOP, GO | GO | GOP | TO
CIP-003-6 | Cyber Security — Security Management Controls | R1.1. | 1.1 For its high impact and medium impact BES Cyber Systems, if any: 1.1.1. Personnel and training (CIP-004); 1.1.2. Electronic Security Perimeters (CIP-005) including Interactive Remote Access; 1.1.3. Physical security of BES Cyber Systems (CIP-006); 1.1.4. System security management (CIP-007); 1.1.5. Incident reporting and response planning (CIP-008); 1.1.6. Recovery plans for BES Cyber Systems (CIP-009); 1.1.7. Configuration change management and vulnerability assessments (CIP-010); 1.1.8. Information protection (CIP-011); and 1.1.9. Declaring and responding to CIP Exceptional Circumstances. | TO, GOP, GO | GO | GOP | TO
CIP-003-7 | Cyber Security — Security Management Controls | R2. | Each Responsible Entity with at least one asset identified in CIP-002 containing low impact BES Cyber Systems shall implement one or more documented cyber security plan(s) for its low impact BES Cyber Systems that include the sections in Attachment 1. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-003-7 | Cyber Security — Security Management Controls | R3. | Each Responsible Entity shall identify a CIP Senior Manager by name and document any change within 30 calendar days of the change. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-003-7 | Cyber Security — Security Management Controls | R1.2. | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: 1.2.1. Cyber security awareness; 1.2.2. Physical security controls; 1.2.3. Electronic access controls; 1.2.4. Cyber Security Incident response; 1.2.5. Transient Cyber Assets and Removable Media malicious code risk mitigation; and 1.2.6. Declaring and responding to CIP Exceptional Circumstances. | TO, GOP, GO | GO | GOP | TO
CIP-003-7 | Cyber Security — Security Management Controls | R1.1. | For its high impact and medium impact BES Cyber Systems, if any: 1.1.1. Personnel and training (CIP-004); 1.1.2. Electronic Security Perimeters (CIP-005) including Interactive Remote Access; 1.1.3. Physical security of BES Cyber Systems (CIP-006); 1.1.4. System security management (CIP-007); 1.1.5. Incident reporting and response planning (CIP-008); 1.1.6. Recovery plans for BES Cyber Systems (CIP-009); 1.1.7. Configuration change management and vulnerability assessments (CIP-010); 1.1.8. Information protection (CIP-011); and 1.1.9. Declaring and responding to CIP Exceptional Circumstances. | TO, GOP, GO | GO | GOP | TO
CIP-003-7 | Cyber Security — Security Management Controls | R1. | Each Responsible Entity shall review and obtain CIP Senior Manager approval at least once every 15 calendar months for one or more documented cyber security policies that collectively address the following topics: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-003-7 | Cyber Security — Security Management Controls | R4. | The Responsible Entity shall implement a documented process to delegate authority, unless no delegations are used. Where allowed by the CIP Standards, the CIP Senior Manager may delegate authority for specific actions to a delegate or delegates. These delegations shall be documented, including the name or title of the delegate, the specific actions delegated, and the date of the delegation; approved by the CIP Senior Manager; and updated within 30 days of any change to the delegation. Delegation changes do not need to be reinstated with a change to the delegator. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R2. | Training —The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R1. | Awareness —The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R2.2.1. | The proper use of Critical Cyber Assets; | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and sevenyear criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R4. | Access —The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. | TO, GOP, GO | GO | GOP | TO
CIP-004-3a | Cyber Security - Personnel & Training | R2.2.3. | The proper handling of Critical Cyber Asset information; and, | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R4. | Access —The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R2.2.3. | The proper handling of Critical Cyber Asset information; and, | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R2.2.1. | The proper use of Critical Cyber Assets; | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R2. | Training —The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | TO, GOP, GO | GO | GOP | TO
CIP-004-4 | Cyber Security — Personnel & Training | R1. | Awareness —The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R3.3. | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R2.2.3. | The proper handling of Critical Cyber Asset information; and, | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R2.2.4. | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R2.3. | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R3. | Personnel Risk Assessment —The Responsible Entity shall have a documented personnel risk assessment program, in accordance with federal, state, provincial, and local laws, and subject to existing collective bargaining unit agreements, for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. A personnel risk assessment shall be conducted pursuant to that program prior to such personnel being granted such access except in specified circumstances such as an emergency. The personnel risk assessment program shall at a minimum include: | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R3.1. | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R3.2. | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R2.2.2. | Physical and electronic access controls to Critical Cyber Assets; | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R2.2. | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R4. | Access —The Responsible Entity shall maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R4.1. | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R4.2. | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R2. | Training —The Responsible Entity shall establish, document, implement, and maintain an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. The cyber security training program shall be reviewed annually, at a minimum, and shall be updated whenever necessary. | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R1. | Awareness —The Responsible Entity shall establish, document, implement, and maintain a security awareness program to ensure personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets receive on-going reinforcement in sound security practices. The program shall include security awareness reinforcement on at least a quarterly basis using mechanisms such as: • Direct communications (e.g., emails, memos, computer based training, etc.); • Indirect communications (e.g., posters, intranet, brochures, etc.); • Management support and reinforcement (e.g., presentations, meetings, etc.). | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R2.1. | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. | TO, GOP, GO | GO | GOP | TO
CIP-004-4a | Cyber Security — Personnel & Training | R2.2.1. | The proper use of Critical Cyber Assets; | TO, GOP, GO | GO | GOP | TO
CIP-004-5 | Cyber Security — Personnel & Training | R4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP‐004‐5 Table R4 – Access Management Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Same Day Operations]. | TO, GOP, GO | GO | GOP | TO
CIP-004-5 | Cyber Security — Personnel & Training | R5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP‐004‐5 Table R5 – Access Revocation. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations and Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-004-5 | Cyber Security — Personnel & Training | R3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP‐004‐5 Table R3 – Personnel Risk Assessment Program. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-004-5 | Cyber Security — Personnel & Training | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP‐004‐5 Table R2 – Cyber Security Training Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-004-5 | Cyber Security — Personnel & Training | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP‐004‐5 Table R1 – Security Awareness Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-004-5.1 | Cyber Security — Personnel & Training | R3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented personnel risk assessment programs to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R3 – Personnel Risk Assessment Program. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-004-5.1 | Cyber Security — Personnel & Training | R5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access revocation programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R5 – Access Revocation. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations and Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-004-5.1 | Cyber Security — Personnel & Training | R4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented access management programs that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R4 – Access Management Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Same Day Operations]. | TO, GOP, GO | GO | GOP | TO
CIP-004-5.1 | Cyber Security — Personnel & Training | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, a cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-5.1 Table R2 – Cyber Security Training Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-004-5.1 | Cyber Security — Personnel & Training | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-5.1 Table R1 – Security Awareness Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-004-6 | Cyber Security — Personnel & Training | R2. | Each Responsible Entity shall implement one or more cyber security training program(s) appropriate to individual roles, functions, or responsibilities that collectively includes each of the applicable requirement parts in CIP-004-6 Table R2 – Cyber Security Training Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-004-6 | Cyber Security — Personnel & Training | R4. | Each Responsible Entity shall implement one or more documented access management program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R4 – Access Management Program. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning and Same Day Operations]. | TO, GOP, GO | GO | GOP | TO
CIP-004-6 | Cyber Security — Personnel & Training | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-004-6 Table R1 – Security Awareness Program. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-004-6 | Cyber Security — Personnel & Training | R5. | Each Responsible Entity shall implement one or more documented access revocation program(s) that collectively include each of the applicable requirement parts in CIP-004-6 Table R5 – Access Revocation. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations and Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-004-6 | Cyber Security — Personnel & Training | R3. | Each Responsible Entity shall implement one or more documented personnel risk assessment program(s) to attain and retain authorized electronic or authorized unescorted physical access to BES Cyber Systems that collectively include each of the applicable requirement parts in CIP-004-6 Table R3 – Personnel Risk Assessment Program. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R3. | Monitoring Electronic Access —The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4.1. | A document identifying the vulnerability assessment process; | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4.3. | The discovery of all access points to the Electronic Security Perimeter; | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4.4. | A review of controls for default accounts, passwords, and network management community strings; | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R5. | Documentation Review and Maintenance —The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-3. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.5.1. | The processes for access request and authorization. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.5.2. | The authentication methods. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1. | Electronic Security Perimeter —The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.5.4. | The controls used to secure dial-up accessible connections. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R2.5. | The required documentation shall, at least, identify and describe: | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. | TO, GOP, GO | GO | GOP | TO
CIP-005-3a | Cyber Security — Electronic Security Perimeter(s) | R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.6. | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.5.1. | The processes for access request and authorization. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.5. | The required documentation shall, at least, identify and describe: | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.4. | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.3. | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.2. | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1. | Electronic Security Perimeter —The Responsible Entity shall ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter. The Responsible Entity shall identify and document the Electronic Security Perimeter(s) and all access points to the perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2. | Electronic Access Controls — The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.5.4. | The controls used to secure dial-up accessible connections. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.5. | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4a Requirements R2 and R3; Standard CIP-006-4c Requirement R3; Standard CIP-007-4 Requirements R1 and R3 through R9; Standard CIP-008-4; and Standard CIP-009-4. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.4. | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-4a. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.3. | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.2. | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R1.1. | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.1. | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.5.3. | The review process for authorization rights, in accordance with Standard CIP-004-4 Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R5.1. | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-4a reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-4a at least annually. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.6. | Appropriate Use Banner —Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R3. | Monitoring Electronic Access —The Responsible Entity shall implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeter(s) twenty-four hours a day, seven days a week. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R3.1. | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R3.2. | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter(s) at least annually. The vulnerability assessment shall include, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4.1. | A document identifying the vulnerability assessment process; | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4.2. | A review to verify that only ports and services required for operations at these access points are enabled; | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4.3. | The discovery of all access points to the Electronic Security Perimeter; | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4.4. | A review of controls for default accounts, passwords, and network management community strings; | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R4.5. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R5. | Documentation Review and Maintenance —The Responsible Entity shall review, update, and maintain all documentation to support compliance with the requirements of Standard CIP-005-4a. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R5.2. | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R2.5.2. | The authentication methods. | TO, GOP, GO | GO | GOP | TO
CIP-005-4a | Cyber Security — Electronic Security Perimeter(s) | R5.3. | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. | TO, GOP, GO | GO | GOP | TO
CIP-005-5 | Cyber Security — Electronic Security Perimeter(s) | R2. | Each Responsible Entity allowing Interactive Remote Access to BES Cyber Systems shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP‐005‐5 Table R2 – Interactive Remote Access Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning and Same Day Operations]. | TO, GOP, GO | GO | GOP | TO
CIP-005-5 | Cyber Security — Electronic Security Perimeter(s) | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP‐005‐5 Table R1 – Electronic Security Perimeter. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning and Same Day Operations]. | TO, GOP, GO | GO | GOP | TO
CIP-005-6 | Cyber Security — Electronic Security Perimeter(s) | R1. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP-005-6 Table R1 – Electronic Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-005-6 | Cyber Security — Electronic Security Perimeter(s) | R2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts, where technically feasible, in CIP-005-6 Table R2 –Remote Access Management. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1. | Physical Security Plan — The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.8. | Annual review of the physical security plan. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R2.1. | Be protected from unauthorized physical access. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R5. | Monitoring Physical Access — The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R7. | Access Log Retention — The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-006-3c | Cyber Security — Physical Security of Critical Cyber Assets | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R2.1. | Be protected from unauthorized physical access. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1. | Physical Security Plan —The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R2.2. | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R5. | Monitoring Physical Access —The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-3. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R7. | Access Log Retention —The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. | TO, GOP, GO | GO | GOP | TO
CIP-006-3d | Cyber Security — Physical Security of Critical Cyber Assets | R1.8. | Annual review of the physical security plan. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R2.1. | Be protected from unauthorized physical access. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1. | Physical Security Plan —The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R7. | Access Log Retention —The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R5. | Monitoring Physical Access —The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R2.2. | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4a Requirements R2 and R3; Standard CIP-006-4c Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.8. | Annual review of the physical security plan. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. | TO, GOP, GO | GO | GOP | TO
CIP-006-4c | Cyber Security — Physical Security of Critical Cyber Assets | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R8.1. | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R8. | Maintenance and Testing — The Responsible Entity shall implement a maintenance and testing program to ensure that all physical security systems under Requirements R4, R5, and R6 function properly. The program must include, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1. | Physical Security Plan —The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager or delegate(s) that shall address, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R2.2. | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R8.3. | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.8. | Annual review of the physical security plan. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R7. | Access Log Retention —The Responsible Entity shall retain physical access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.3. | Processes, tools, and procedures to monitor physical access to the perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.4. | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.5. | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6. | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.1. | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R4. | Physical Access Controls — The Responsible Entity shall document and implement the operational and procedural controls to manage physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. The Responsible Entity shall implement one or more of the following physical access methods: • Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. • Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. • Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. • Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.7. | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R8.2. | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R2. | Protection of Physical Access Control Systems — Cyber Assets that authorize and/or log access to the Physical Security Perimeter(s), exclusive of hardware at the Physical Security Perimeter access point such as electronic lock control mechanisms and badge readers, shall: | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R2.1. | Be protected from unauthorized physical access. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.1. | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R3. | Protection of Electronic Access Control Systems — Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall reside within an identified Physical Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R5. | Monitoring Physical Access —The Responsible Entity shall document and implement the technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter(s) twenty-four hours a day, seven days a week. Unauthorized access attempts shall be reviewed immediately and handled in accordance with the procedures specified in Requirement CIP-008-4. One or more of the following monitoring methods shall be used: • Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. • Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R6. | Logging Physical Access — Logging shall record sufficient information to uniquely identify individuals and the time of access twenty-four hours a day, seven days a week. The Responsible Entity shall implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter(s) using one or more of the following logging methods or their equivalent: • Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. • Video Recording: Electronic capture of video images of sufficient quality to determine identity. • Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.6.2. | Continuous escorted access of visitors within the Physical Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-006-4d | Cyber Security — Physical Security of Critical Cyber Assets | R1.2. | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. | TO, GOP, GO | GO | GOP | TO
CIP-006-5 | Cyber Security — Physical Security of BES Cyber Systems | R3. | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing programs that collectively include each of the applicable requirement parts in CIP‐006‐5 Table R3 – Maintenance and Testing Program. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-006-5 | Cyber Security — Physical Security of BES Cyber Systems | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented visitor control programs that include each of the applicable requirement parts in CIP‐006‐5 Table R2 – Visitor Control Program. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations.] | TO, GOP, GO | GO | GOP | TO
CIP-006-5 | Cyber Security — Physical Security of BES Cyber Systems | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented physical security plans that collectively include all of the applicable requirement parts in CIP‐006‐5 Table R1 – Physical Security Plan. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning and Same Day Operations]. | TO, GOP, GO | GO | GOP | TO
CIP-006-6 | Cyber Security — Physical Security of BES Cyber Systems | R2. | Each Responsible Entity shall implement one or more documented visitor control program(s) that include each of the applicable requirement parts in CIP-006-6 Table R2 – Visitor Control Program. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations.] | TO, GOP, GO | GO | GOP | TO
CIP-006-6 | Cyber Security — Physical Security of BES Cyber Systems | R3. | Each Responsible Entity shall implement one or more documented Physical Access Control System maintenance and testing program(s) that collectively include each of the applicable requirement parts in CIP-006-6 Table R3 – Maintenance and Testing Program. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-006-6 | Cyber Security — Physical Security of BES Cyber Systems | R1. | Each Responsible Entity shall implement one or more documented physical security plan(s) that collectively include all of the applicable requirement parts in CIP-006-6 Table R1 – Physical Security Plan. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning and Same Day Operations]. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R1. | Test Procedures — The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.3.1. | Each password shall be a minimum of six characters. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R8.1. | A document identifying the vulnerability assessment process; | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R8.3. | A review of controls for default accounts; and, | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R1.3. | The Responsible Entity shall document test results. | TO, GOP, GO | GO | GOP | TO
CIP-007-3a | Cyber Security - Systems Security Management | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-3. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R8.1. | A document identifying the vulnerability assessment process; | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R8.3. | A review of controls for default accounts; and, | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. (Retirement approved by FERC effective January 21, 2014.) | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R9. | Documentation Review and Maintenance — The Responsible Entity shall review and update the documentation specified in Standard CIP-007-3 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.3.1. | Each password shall be a minimum of six characters. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R4. | Malicious Software Prevention — The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R1.3. | The Responsible Entity shall document test results. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R2. | Ports and Services — The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R3. | Security Patch Management — The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-3 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | TO, GOP, GO | GO | GOP | TO
CIP-007-3b | Cyber Security - Systems Security Management | R1. | Test Procedures—The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-3, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R4.2. | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.2.1. | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.3.2. | Each password shall consist of a combination of alpha, numeric, and “special” characters. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.3.1. | Each password shall be a minimum of six characters. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.3. | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.2.3. | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.2.2. | The Responsible Entity shall identify those individuals with access to shared accounts. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.2. | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.1.3. | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.1.2. | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.1.1. | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.3.3. | Each password shall be changed at least annually, or more frequently based on risk. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5. | Account Management — The Responsible Entity shall establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R5.1. | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R7.1. | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R9. | Documentation Review and Maintenance —The Responsible Entity shall review and update the documentation specified in Standard CIP-007-4 at least annually. Changes resulting from modifications to the systems or controls shall be documented within thirty calendar days of the change being completed. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R8.4. | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R8.3. | A review of controls for default accounts; and, | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R8.2. | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R8.1. | A document identifying the vulnerability assessment process; | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R6.5. | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R7.2. | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R6. | Security Status Monitoring — The Responsible Entity shall ensure that all Cyber Assets within the Electronic Security Perimeter, as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R7. | Disposal or Redeployment — The Responsible Entity shall establish and implement formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the Electronic Security Perimeter(s) as identified and documented in Standard CIP-005-4. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R4.1. | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R6.4. | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R6.3. | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R6.2. | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R6.1. | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R8. | Cyber Vulnerability Assessment — The Responsible Entity shall perform a cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter at least annually. The vulnerability assessment shall include, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R1.2. | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R7.3. | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R4. | Malicious Software Prevention —The Responsible Entity shall use anti-virus software and other malicious software (“malware”) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R1.1. | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R1.3. | The Responsible Entity shall document test results. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R2. | Ports and Services —The Responsible Entity shall establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R2.1. | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R2.2. | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R2.3. | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R3. | Security Patch Management —The Responsible Entity, either separately or as a component of the documented configuration management process specified in CIP-003-4 Requirement R6, shall establish, document and implement a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R3.1. | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R3.2. | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. | TO, GOP, GO | GO | GOP | TO
CIP-007-4a | Cyber Security — Systems Security Management | R1. | Test Procedures —The Responsible Entity shall ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. For purposes of Standard CIP-007-4, a significant change shall, at a minimum, include implementation of security patches, cumulative service packs, vendor releases, and version upgrades of operating systems, applications, database platforms, or other third-party software or firmware. | TO, GOP, GO | GO | GOP | TO
CIP-007-5 | Cyber Security — Systems Security Management | R3. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐007‐5 Table R3 – Malicious Code Prevention. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations]. | TO, GOP, GO | GO | GOP | TO
CIP-007-5 | Cyber Security — Systems Security Management | R4. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐007‐5 Table R4 – Security Event Monitoring. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations and Operations Assessment.] | TO, GOP, GO | GO | GOP | TO
CIP-007-5 | Cyber Security — Systems Security Management | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐007‐5 Table R2 – Security Patch Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-007-5 | Cyber Security — Systems Security Management | R5. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐007‐5 Table R5 – System Access Controls. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-007-5 | Cyber Security — Systems Security Management | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐007‐5 Table R1 – Ports and Services. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations.] | TO, GOP, GO | GO | GOP | TO
CIP-007-6 | Cyber Security — Systems Security Management | R5. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R5 – System Access Controls. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-007-6 | Cyber Security — Systems Security Management | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R2 – Security Patch Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-007-6 | Cyber Security — Systems Security Management | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R1 – Ports and Services. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations.] | TO, GOP, GO | GO | GOP | TO
CIP-007-6 | Cyber Security — Systems Security Management | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R3 – Malicious Code Prevention. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations]. | TO, GOP, GO | GO | GOP | TO
CIP-007-6 | Cyber Security — Systems Security Management | R4. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-007-6 Table R4 – Security Event Monitoring. [Violation Risk Factor: Medium] [Time Horizon: Same Day Operations and Operations Assessment.] | TO, GOP, GO | GO | GOP | TO
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. | TO, GOP, GO | GO | GOP | TO
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.4. | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. | TO, GOP, GO | GO | GOP | TO
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. | TO, GOP, GO | GO | GOP | TO
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. | TO, GOP, GO | GO | GOP | TO
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1. | Cyber Security Incident Response Plan — The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. | TO, GOP, GO | GO | GOP | TO
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R1.2. | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. | TO, GOP, GO | GO | GOP | TO
CIP-008-3 | Cyber Security - Incident Reporting and Response Planning | R2. | Cyber Security Incident Documentation — The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | TO, GOP, GO | GO | GOP | TO
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.1. | Procedures to characterize and classify events as reportable Cyber Security Incidents. | TO, GOP, GO | GO | GOP | TO
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.2. | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. | TO, GOP, GO | GO | GOP | TO
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.4. | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. | TO, GOP, GO | GO | GOP | TO
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.5. | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. | TO, GOP, GO | GO | GOP | TO
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.6. | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. | TO, GOP, GO | GO | GOP | TO
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R2. | Cyber Security Incident Documentation —The Responsible Entity shall keep relevant documentation related to Cyber Security Incidents reportable per Requirement R1.1 for three calendar years. | TO, GOP, GO | GO | GOP | TO
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1. | Cyber Security Incident Response Plan —The Responsible Entity shall develop and maintain a Cyber Security Incident response plan and implement the plan in response to Cyber Security Incidents. The Cyber Security Incident response plan shall address, at a minimum, the following: | TO, GOP, GO | GO | GOP | TO
CIP-008-4 | Cyber Security — Incident Reporting and Response Planning | R1.3. | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. | TO, GOP, GO | GO | GOP | TO
CIP-008-5 | Cyber Security — Incident Reporting and Response Planning | R3. | Each Responsible Entity shall maintain each of its Cyber Security Incident response plans according to each of the applicable requirement parts in CIP‐008‐5 Table R3 – Cyber Security Incident Response Plan Review, Update, and Communication. [Violation Risk Factor: Lower] [Time Horizon: Operations Assessment]. | TO, GOP, GO | GO | GOP | TO
CIP-008-5 | Cyber Security — Incident Reporting and Response Planning | R2. | Each Responsible Entity shall implement each of its documented Cyber Security Incident response plans to collectively include each of the applicable requirement parts in CIP‐008‐5 Table R2 – Cyber Security Incident Response Plan Implementation and Testing. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Real‐Time Operations]. | TO, GOP, GO | GO | GOP | TO
CIP-008-5 | Cyber Security — Incident Reporting and Response Planning | R1. | Each Responsible Entity shall document one or more Cyber Security Incident response plan(s) that collectively include each of the applicable requirement parts in CIP‐008‐5 Table R1 – Cyber Security Incident Response Plan Specifications. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | TO, GOP, GO | GO | GOP | TO
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). | TO, GOP, GO | GO | GOP | TO
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R1.2. | Define the roles and responsibilities of responders. | TO, GOP, GO | GO | GOP | TO
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R2. | Exercises — The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | TO, GOP, GO | GO | GOP | TO
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R1. | Recovery Plans — The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | TO, GOP, GO | GO | GOP | TO
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R4. | Backup and Restore — The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | TO, GOP, GO | GO | GOP | TO
CIP-009-3 | Cyber Security - Recovery Plans for Critical Cyber Assets | R3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | TO, GOP, GO | GO | GOP | TO
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R1.2. | Define the roles and responsibilities of responders. | TO, GOP, GO | GO | GOP | TO
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R1. | Recovery Plans —The Responsible Entity shall create and annually review recovery plan(s) for Critical Cyber Assets. The recovery plan(s) shall address at a minimum the following: | TO, GOP, GO | GO | GOP | TO
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R1.1. | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). | TO, GOP, GO | GO | GOP | TO
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R2. | Exercises —The recovery plan(s) shall be exercised at least annually. An exercise of the recovery plan(s) can range from a paper drill, to a full operational exercise, to recovery from an actual incident. | TO, GOP, GO | GO | GOP | TO
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R4. | Backup and Restore —The recovery plan(s) shall include processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. For example, backups may include spare electronic components or equipment, written documentation of configuration settings, tape backup, etc. | TO, GOP, GO | GO | GOP | TO
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R5. | Testing Backup Media — Information essential to recovery that is stored on backup media shall be tested at least annually to ensure that the information is available. Testing can be completed off site. | TO, GOP, GO | GO | GOP | TO
CIP-009-4 | Cyber Security — Recovery Plans for Critical Cyber Assets | R3. | Change Control — Recovery plan(s) shall be updated to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident. Updates shall be communicated to personnel responsible for the activation and implementation of the recovery plan(s) within thirty calendar days of the change being completed. | TO, GOP, GO | GO | GOP | TO
CIP-009-5 | Cyber Security — Recovery Plans for BES Cyber Systems | R3. | Each Responsible Entity shall maintain each of its recovery plans in accordance with each of the applicable requirement parts in CIP‐009‐5 Table R3 – Recovery Plan Review, Update and Communication. [Violation Risk Factor: Lower] [Time Horizon: Operations Assessment]. | TO, GOP, GO | GO | GOP | TO
CIP-009-5 | Cyber Security — Recovery Plans for BES Cyber Systems | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, its documentedrecovery plan(s) to collectively include each of the applicable requirement parts in CIP‐009‐5 Table R2 – Recovery Plan Implementation and Testing. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Real‐time Operations.] | TO, GOP, GO | GO | GOP | TO
CIP-009-5 | Cyber Security — Recovery Plans for BES Cyber Systems | R1. | Each Responsible Entity shall have one or more documented recovery plans that collectively include each of the applicable requirement parts in CIP‐009‐5 Table R1 – Recovery Plan Specifications. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-009-6 | Cyber Security — Recovery Plans for BES Cyber Systems | R2. | Each Responsible Entity shall implement its documented recovery plan(s) to collectively include each of the applicable requirement parts in CIP-009-6 Table R2 – Recovery Plan Implementation and Testing. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning and Real-time Operations.] | TO, GOP, GO | GO | GOP | TO
CIP-009-6 | Cyber Security — Recovery Plans for BES Cyber Systems | R3. | Each Responsible Entity shall maintain each of its recovery plan(s) in accordance with each of the applicable requirement parts in CIP-009-6 Table R3 – Recovery Plan Review, Update and Communication. [Violation Risk Factor: Lower] [Time Horizon: Operations Assessment]. | TO, GOP, GO | GO | GOP | TO
CIP-009-6 | Cyber Security — Recovery Plans for BES Cyber Systems | R1. | Each Responsible Entity shall have one or more documented recovery plan(s) that collectively include each of the applicable requirement parts in CIP-009-6 Table R1 – Recovery Plan Specifications. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-010-1 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R2. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R2 – Configuration Monitoring. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-010-1 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R1 – Configuration Change Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-010-1 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R3. | Each Responsible Entity shall implement one or more documented processes that collectively include each of the applicable requirement parts in CIP‐010‐1 Table R3– Vulnerability Assessments. [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning and Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-010-2 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R2 – Configuration Monitoring. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-010-2 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning and Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-010-2 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R1 – Configuration Change Management. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-010-2 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-2 Table R3– Vulnerability Assessments. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning and Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-010-3 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management. | TO, GOP, GO | GO | GOP | TO
CIP-010-3 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R4. | Each Responsible Entity, for its high impact and medium impact BES Cyber Systems and associated Protected Cyber Assets, shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) for Transient Cyber Assets and Removable Media that include the sections in Attachment 1. | TO, GOP, GO | GO | GOP | TO
CIP-010-3 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R3. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R3– Vulnerability Assessments. | TO, GOP, GO | GO | GOP | TO
CIP-010-3 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R2 – Configuration Monitoring. | TO, GOP, GO | GO | GOP | TO
CIP-010-3 | Cyber Security — Configuration Change Management and Vulnerability Assessments | R1. | Each Responsible Entity shall implement one or more documented process(es) that collectively include each of the applicable requirement parts in CIP-010-3 Table R1 – Configuration Change Management. | TO, GOP, GO | GO | GOP | TO
CIP-011-1 | Cyber Security Information Protection | R2. | Each Responsible Entity shall implement one or more documented processes that collectively include the applicable requirement parts in CIP‐011‐1 Table R2 – BES Cyber Asset Reuse and Disposal. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-011-1 | Cyber Security Information Protection | R1. | Each Responsible Entity shall implement, in a manner that identifies, assesses, and corrects deficiencies, one or more documented information protection program(s) that collectively includes each of the applicable requirement parts in CIP‐011‐1 Table R1 – Information Protection. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-011-2 | Cyber Security Information Protection | R2. | Each Responsible Entity shall implement one or more documented process(es) that collectively include the applicable requirement parts in CIP-011-2 Table R2 – BES Cyber Asset Reuse and Disposal. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-011-2 | Cyber Security Information Protection | R1. | Each Responsible Entity shall implement one or more documented information protection program(s) that collectively includes each of the applicable requirement parts in CIP-011-2 Table R1 – Information Protection. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO, GOP, GO | GO | GOP | TO
CIP-012-1 | Cyber Security – Control Center Communication Networks | R1.2. | Identification of where the Responsible Entity applied security protection for transmitting Real-time Assessment and Real-time monitoring data between Control Centers; and | TO, GOP, GO | GO | GOP | TO
CIP-012-1 | Cyber Security – Control Center Communication Networks | R1.1. | Identification of security protection used to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between Control Centers; | TO, GOP, GO | GO | GOP | TO
CIP-012-1 | Cyber Security – Control Center Communication Networks | R1.3. | If the Control Centers are owned or operated by different Responsible Entities, identification of the responsibilities of each Responsible Entity for applying security protection to the transmission of Real-time Assessment and Real-time monitoring data between those Control Centers. | TO, GOP, GO | GO | GOP | TO
CIP-012-1 | Cyber Security – Control Center Communication Networks | R1. | The Responsible Entity shall implement, except under CIP Exceptional Circumstances, one or more documented plan(s) to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between any applicable Control Centers. The Responsible Entity is not required to include oral communications in its plan. The plan shall include: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.1. | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.5. | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System; and | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2. | One or more process(es) used in procuring BES Cyber Systems that address the following, as applicable: | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.2. | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.4. | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R3. | Each Responsible Entity shall review and obtain CIP Senior Manager or delegate approval of its supply chain cyber security risk management plan(s) specified in Requirement R1 at least once every 15 calendar months. | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R2. | Each Responsible Entity shall implement its supply chain cyber security risk management plan(s) specified in Requirement R1. Note: Implementation of the plan does not require the Responsible Entity to renegotiate or abrogate existing contracts (including amendments to master agreements and purchase orders). Additionally, the following issues are beyond the scope of Requirement R2: (1) the actual terms and conditions of a procurement contract; and (2) vendor performance and adherence to a contract. | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.1. | One or more process(es) used in planning for the procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.6. | Coordination of controls for (i) vendor-initiated Interactive Remote Access, and (ii) system-to-system remote access with a vendor(s). | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1. | Each Responsible Entity shall develop one or more documented supply chain cyber security risk management plan(s) for high and medium impact BES Cyber Systems. The plan(s) shall include: | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1.2.3. | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; | TO, GOP, GO | GO | GOP | TO
CIP-013-1 | Cyber Security - Supply Chain Risk Management | R1. | Each Responsible Entity shall develop one or more documented supply chain cyber security risk management plan(s) for high and medium impact BES Cyber Systems. The plan(s) shall include: | TO, GOP, GO | GO | GOP | TO
CIP-014-1 | Physical Security | R6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. [VRF: Medium; Time-Horizon: Long-term Planning] | TO |  |  | TO
CIP-014-1 | Physical Security | R4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: [VRF: Medium; Time-Horizon: Operations Planning, Long-term Planning] | TO |  |  | TO
CIP-014-1 | Physical Security | R4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and | TO |  |  | TO
CIP-014-1 | Physical Security | R4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | TO |  |  | TO
CIP-014-1 | Physical Security | R5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: [VRF: High; Time-Horizon: Long-term Planning] | TO |  |  | TO
CIP-014-1 | Physical Security | R5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. | TO |  |  | TO
CIP-014-1 | Physical Security | R5.2. | Law enforcement contact and coordination information. | TO |  |  | TO
CIP-014-1 | Physical Security | R3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. [VRF: Lower; Time-Horizon: Long-term Planning] | TO |  |  | TO
CIP-014-1 | Physical Security | R5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | TO |  |  | TO
CIP-014-1 | Physical Security | R3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | TO |  |  | TO
CIP-014-1 | Physical Security | R6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following:  An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification.  An entity or organization approved by the ERO.  A governmental agency with physical security expertise.  An entity or organization with demonstrated law enforcement, government, or military physical security expertise. | TO |  |  | TO
CIP-014-1 | Physical Security | R6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. | TO |  |  | TO
CIP-014-1 | Physical Security | R6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation:  Modify its evaluation or security plan(s) consistent with the recommendation; or  Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. | TO |  |  | TO
CIP-014-1 | Physical Security | R6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | TO |  |  | TO
CIP-014-1 | Physical Security | R5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. | TO |  |  | TO
CIP-014-1 | Physical Security | R1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | TO |  |  | TO
CIP-014-1 | Physical Security | R4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); | TO |  |  | TO
CIP-014-1 | Physical Security | R2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | TO |  |  | TO
CIP-014-1 | Physical Security | R1.1. | Subsequent risk assessments shall be performed:  At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection; or  At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. | TO |  |  | TO
CIP-014-1 | Physical Security | R2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. [VRF: Medium; Time-Horizon: Long-term Planning] | TO |  |  | TO
CIP-014-1 | Physical Security | R2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either:  A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or  An entity that has transmission planning or analysis experience. | TO |  |  | TO
CIP-014-1 | Physical Security | R2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. | TO |  |  | TO
CIP-014-1 | Physical Security | R2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation:  Modify its identification under Requirement R1 consistent with the recommendation; or  Document the technical basis for not modifying the identification in accordance with the recommendation. | TO |  |  | TO
CIP-014-1 | Physical Security | R1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. [VRF: High; Time-Horizon: Long-term Planning] | TO |  |  | TO
CIP-014-2 | Physical Security | R4. | Each Transmission Owner that identified a Transmission station, Transmission substation, or a primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall conduct an evaluation of the potential threats and vulnerabilities of a physical attack to each of their respective Transmission station(s), Transmission substation(s), and primary control center(s) identified in Requirement R1 and verified according to Requirement R2. The evaluation shall consider the following: [VRF: Medium; Time-Horizon: Operations Planning, Long-term Planning] | TO |  |  | TO
CIP-014-2 | Physical Security | R5.3. | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. | TO |  |  | TO
CIP-014-2 | Physical Security | R5.1. | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. | TO |  |  | TO
CIP-014-2 | Physical Security | R4.1. | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); | TO |  |  | TO
CIP-014-2 | Physical Security | R3.1. | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. | TO |  |  | TO
CIP-014-2 | Physical Security | R4.2. | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and | TO |  |  | TO
CIP-014-2 | Physical Security | R4.3. | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. | TO |  |  | TO
CIP-014-2 | Physical Security | R5. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall develop and implement a documented physical security plan(s) that covers their respective Transmission station(s), Transmission substation(s), and primary control center(s). The physical security plan(s) shall be developed within 120 calendar days following the completion of Requirement R2 and executed according to the timeline specified in the physical security plan(s). The physical security plan(s) shall include the following attributes: [VRF: High; Time-Horizon: Long-term Planning] | TO |  |  | TO
CIP-014-2 | Physical Security | R6.4. | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | TO |  |  | TO
CIP-014-2 | Physical Security | R6.2. | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. | TO |  |  | TO
CIP-014-2 | Physical Security | R6.1. | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following:  An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification.  An entity or organization approved by the ERO.  A governmental agency with physical security expertise.  An entity or organization with demonstrated law enforcement, government, or military physical security expertise. | TO |  |  | TO
CIP-014-2 | Physical Security | R5.4. | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). | TO |  |  | TO
CIP-014-2 | Physical Security | R5.2. | Law enforcement contact and coordination information. | TO |  |  | TO
CIP-014-2 | Physical Security | R3. | For a primary control center(s) identified by the Transmission Owner according to Requirement R1, Part 1.2 that a) operationally controls an identified Transmission station or Transmission substation verified according to Requirement R2, and b) is not under the operational control of the Transmission Owner: the Transmission Owner shall, within seven calendar days following completion of Requirement R2, notify the Transmission Operator that has operational control of the primary control center of such identification and the date of completion of Requirement R2. [VRF: Lower; Time-Horizon: Long-term Planning] | TO |  |  | TO
CIP-014-2 | Physical Security | R6.3. | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation:  Modify its evaluation or security plan(s) consistent with the recommendation; or  Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. | TO |  |  | TO
CIP-014-2 | Physical Security | R6. | Each Transmission Owner that identified a Transmission station, Transmission substation, or primary control center in Requirement R1 and verified according to Requirement R2, and each Transmission Operator notified by a Transmission Owner according to Requirement R3, shall have an unaffiliated third party review the evaluation performed under Requirement R4 and the security plan(s) developed under Requirement R5. The review may occur concurrently with or after completion of the evaluation performed under Requirement R4 and the security plan development under Requirement R5. [VRF: Medium; Time-Horizon: Long-term Planning] | TO |  |  | TO
CIP-014-2 | Physical Security | R2.4. | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. | TO |  |  | TO
CIP-014-2 | Physical Security | R2.3. | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation:  Modify its identification under Requirement R1 consistent with the recommendation; or  Document the technical basis for not modifying the identification in accordance with the recommendation. | TO |  |  | TO
CIP-014-2 | Physical Security | R2.2. | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. | TO |  |  | TO
CIP-014-2 | Physical Security | R2.1. | Each Transmission Owner shall select an unaffiliated verifying entity that is either:  A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or  An entity that has transmission planning or analysis experience. | TO |  |  | TO
CIP-014-2 | Physical Security | R2. | Each Transmission Owner shall have an unaffiliated third party verify the risk assessment performed under Requirement R1. The verification may occur concurrent with or after the risk assessment performed under Requirement R1. [VRF: Medium; Time-Horizon: Long-term Planning] | TO |  |  | TO
CIP-014-2 | Physical Security | R1.2. | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. | TO |  |  | TO
CIP-014-2 | Physical Security | R1.1. | Subsequent risk assessments shall be performed:  At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or  At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. | TO |  |  | TO
CIP-014-2 | Physical Security | R1. | Each Transmission Owner shall perform an initial risk assessment and subsequent risk assessments of its Transmission stations and Transmission substations (existing and planned to be in service within 24 months) that meet the criteria specified in Applicability Section 4.1.1. The initial and subsequent risk assessments shall consist of a transmission analysis or transmission analyses designed to identify the Transmission station(s) and Transmission substation(s) that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. [VRF: High; Time-Horizon: Long-term Planning] | TO |  |  | TO
COM-001-2 | Communications | R8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | GOP |  | GOP
COM-001-2 | Communications | R11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | GOP |  | GOP
COM-001-2 | Communications | R8.1. | Its Balancing Authority. | GOP |  | GOP
COM-001-2.1 | Communications | R11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | GOP |  | GOP
COM-001-2.1 | Communications | R8.1. | Its Balancing Authority. | GOP |  | GOP
COM-001-2.1 | Communications | R8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): [Violation Risk Factor: High] [Time Horizon: Real-time Operations] | GOP |  | GOP
COM-001-3 | Communications | R8.1. | Its Balancing Authority. | GOP |  | GOP
COM-001-3 | Communications | R8.2. | Its Transmission Operator. | GOP |  | GOP
COM-001-3 | Communications | R8. | Each Generator Operator shall have Interpersonal Communication capability with the following entities (unless the Generator Operator detects a failure of its Interpersonal Communication capability in which case Requirement R11 shall apply): | GOP |  | GOP
COM-001-3 | Communications | R12. | Each Reliability Coordinator, Transmission Operator, Generator Operator, and Balancing Authority shall have internal Interpersonal Communication capabilities for the exchange of information necessary for the Reliable Operation of the BES. This includes communication capabilities between Control Centers within the same functional entity, and/or between a Control Center and field personnel. | GOP |  | GOP
COM-001-3 | Communications | R11. | Each Distribution Provider and Generator Operator that detects a failure of its Interpersonal Communication capability shall consult each entity affected by the failure, as identified in Requirement R7 for a Distribution Provider or Requirement R8 for a Generator Operator, to determine a mutually agreeable action for the restoration of its Interpersonal Communication capability. | GOP |  | GOP
COM-002-2 | Communications and Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. | GOP |  | GOP
COM-002-2a | Communications and Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall have communications (voice and data links) with appropriate Reliability Coordinators, Balancing Authorities, and Transmission Operators. Such communications shall be staffed and available for addressing a real-time emergency condition. | GOP |  | GOP
COM-002-3 | Communications and Coordination | R2. | Each Balancing Authority, Transmission Operator, Generator Operator, and Distribution Provider that is the recipient of a Reliability Directive shall repeat, restate, rephrase, or recapitulate the Reliability Directive. [Violation Risk Factor: High][Time Horizon: Real-Time] | GOP |  | GOP
COM-002-4 | Operating Personnel Communications Protocols | R6. | Each Balancing Authority, Distribution Provider, Generator Operator, and Transmission Operator that receives an oral two-party, person-to-person Operating Instruction during an Emergency, excluding written or oral single-party to multiple-party burst Operating Instructions, shall either: [Violation Risk Factor: High][Time Horizon: Real-time Operations]  Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or  Request that the issuer reissue the Operating Instruction. | GOP |  | GOP
COM-002-4 | Operating Personnel Communications Protocols | R3. | Each Distribution Provider and Generator Operator shall conduct initial training for each of its operating personnel who can receive an oral two-party, person-to-person Operating Instruction prior to that individual operator receiving an oral two-party, person-to-person Operating Instruction to either: [Violation Risk Factor: Low][Time Horizon: Long-term Planning]  Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct, or  Request that the issuer reissue the Operating Instruction. | GOP |  | GOP
EOP-004-2 | Event Reporting | R2. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). | TO, GOP, GO | GO | GOP | TO
EOP-004-2 | Event Reporting | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | TO, GOP, GO | GO | GOP | TO
EOP-004-2 | Event Reporting | R2. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). | TO, GOP, GO | GO | GOP | TO
EOP-004-2 | Event Reporting | R3. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. | TO, GOP, GO | GO | GOP | TO
EOP-004-2 | Event Reporting | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). | TO, GOP, GO | GO | GOP | TO
EOP-004-2 | Event Reporting | R3. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. | TO, GOP, GO | GO | GOP | TO
EOP-004-3 | Event Reporting | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-2-3 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
EOP-004-3 | Event Reporting | R2. | Each Responsible Entity shall report events per their Operating Plan within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time). [Violation Risk Factor: Medium] [Time Horizon: Operations Assessment] | TO, GOP, GO | GO | GOP | TO
EOP-004-3 | Event Reporting | R3. | Each Responsible Entity shall validate all contact information contained in the Operating Plan pursuant to Requirement R1 each calendar year. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
EOP-004-4 | Event Reporting | R1. | Each Responsible Entity shall have an event reporting Operating Plan in accordance with EOP-004-4 Attachment 1 that includes the protocol(s) for reporting to the Electric Reliability Organization and other organizations (e.g., the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, or governmental authority). [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GOP, GO | GO | GOP | TO
EOP-004-4 | Event Reporting | R2. | Each Responsible Entity shall report events specified in EOP-004-4 Attachment 1 to the entities specified per their event reporting Operating Plan by the later of 24 hours of recognition of meeting an event type threshold for reporting or by the end of the Responsible Entity’s next business day (4 p.m. local time will be considered the end of the business day). [Violation Risk Factor: Medium] [Time Horizon: Operations Assessment] | TO, GOP, GO | GO | GOP | TO
EOP-005-2 | System Restoration from Blackstart Resources | R17. | Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: | GOP |  | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R18. | Each Generator Operator shall participate in the Reliability Coordinator’s restoration drills, exercises, or simulations as requested by the Reliability Coordinator. | GOP |  | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R17.1. | System restoration plan including coordination with the Transmission Operator. | GOP |  | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R16.2. | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | GOP |  | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R16.1. | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R9. | GOP |  | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R16. | Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. | GOP |  | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R15. | Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. | GOP |  | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R14. | Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. | GOP |  | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R13. | Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. | GOP |  | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R17.2. | The procedures documented in Requirement R14. | GOP |  | GOP
EOP-005-2 | System Restoration from Blackstart Resources | R11. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. | TO |  |  | TO
EOP-005-3 | System Restoration from Blackstart Resources | R13. | Each Generator Operator with a Blackstart Resource shall notify its Transmission Operator of any known changes to the capabilities of that Blackstart Resource affecting the ability to meet the Transmission Operator’s restoration plan within 24 hours following such change. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | GOP |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R16. | Each Generator Operator shall participate in its Reliability Coordinator’s restoration drills, exercises, or simulations as requested by its Reliability Coordinator. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | GOP |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R15.2. | The procedures documented in Requirement R12 | GOP |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R15.1. | System restoration plan including coordination with the Transmission Operator | GOP |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R15. | Each Generator Operator with a Blackstart Resource shall provide a minimum of two hours of training every two calendar years to each of its operating personnel responsible for the startup of its Blackstart Resource generation units and energizing a bus. The training program shall include training on the following: [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | GOP |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R14.2. | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. | GOP |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R14. | Each Generator Operator with a Blackstart Resource shall perform Blackstart Resource tests, and maintain records of such testing, in accordance with the testing requirements set by the Transmission Operator to verify that the Blackstart Resource can perform as specified in the restoration plan. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | GOP |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R12. | Each Generator Operator with a Blackstart Resource shall have documented procedures for starting each Blackstart Resource and energizing a bus. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | GOP |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R11. | Each Transmission Operator and each Generator Operator with a Blackstart Resource shall have written Blackstart Resource Agreements or mutually agreed upon procedures or protocols, specifying the terms and conditions of their arrangement. Such Agreements shall include references to the Blackstart Resource testing requirements. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | GOP |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R14.1. | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. | GOP |  | GOP
EOP-005-3 | System Restoration from Blackstart Resources | R9. | Each Transmission Operator, each applicable Transmission Owner, and each applicable Distribution Provider shall provide a minimum of two hours of System restoration training every two calendar years to their field switching personnel identified as performing unique tasks associated with the Transmission Operator’s restoration plan that are outside of their normal tasks. [Violation Risk Factor = Medium] [Time Horizon = Operations Planning] | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.10. | Power quality impacts. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.4. | Breaker duty and surge protection. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.5. | System protection and coordination. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.6. | Metering and telecommunications. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R4. | The Transmission Owner shall maintain and update its Facility connection requirements as required. The Transmission Owner shall make documentation of these requirements available to the users of the transmission system, the Regional Entity, and ERO on request (five business days). | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.7. | Grounding and safety issues. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.16. | Communications and procedures during normal and emergency operating conditions. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.9. | Voltage, Reactive Power, and power factor control. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.11. | Equipment Ratings. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.12. | Synchronizing of Facilities. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.13. | Maintenance coordination. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.3. | Voltage level and MW and MVAR capacity or demand at point of connection. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.14. | Operational issues (abnormal frequency and voltages). | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R1.1. | Generation Facilities, | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.15. | Inspection requirements for existing or new Facilities. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.8. | Insulation and insulation coordination. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.1. | Procedures for coordinated joint studies of new Facilities and their impacts on the interconnected Transmission systems. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1. | Provide a written summary of its plans to achieve the required system performance as described in Requirements R1 or R2 throughout the planning horizon: | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3. | Each Transmission Owner and each applicable Generator Owner (in accordance with Requirement R2) shall address the following items in its Facility connection requirements: | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R2. | Each applicable Generator Owner shall, within 45 days of having an executed Agreement to evaluate the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the interconnected Transmission systems (under FAC-002-1), document and publish its Facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Entity, subregional, Power Pool, and individual Transmission Owner planning criteria and Facility connection requirements. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R1.2. | Transmission Facilities, and | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R1. | The Transmission Owner shall document, maintain, and publish Facility connection requirements to ensure compliance with NERC Reliability Standards and applicable Regional Entity, subregional, Power Pool, and individual Transmission Owner planning criteria and Facility connection requirements. The Transmission Owner’s Facility connection requirements shall address connection requirements for: | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R3.1.2. | Procedures for notification of new or modified Facilities to others (those responsible for the reliability of the interconnected Transmission systems) as soon as feasible. | TO |  |  | TO
FAC-001-1 | Facility Connection Requirements | R1.3. | End-user Facilities | TO |  |  | TO
FAC-001-2 | Facility Interconnection Requirements | R4.1. | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). | GO | GO
FAC-001-2 | Facility Interconnection Requirements | R1.2. | transmission Facilities; and | TO |  |  | TO
FAC-001-2 | Facility Interconnection Requirements | R1.3. | end-user Facilities. | TO |  |  | TO
FAC-001-2 | Facility Interconnection Requirements | R2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | GO | GO
FAC-001-2 | Facility Interconnection Requirements | R3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements: [Violation Risk Factor: Lower] [Time Horizon: Long-Term Planning] | TO |  |  | TO
FAC-001-2 | Facility Interconnection Requirements | R1.1. | generation Facilities; | TO |  |  | TO
FAC-001-2 | Facility Interconnection Requirements | R3.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. | TO |  |  | TO
FAC-001-2 | Facility Interconnection Requirements | R4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: [Violation Risk Factor: Lower] [Time Horizon: Long-Term Planning] | GO | GO
FAC-001-2 | Facility Interconnection Requirements | R3.1. | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). | TO |  |  | TO
FAC-001-2 | Facility Interconnection Requirements | R4.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. | GO | GO
FAC-001-2 | Facility Interconnection Requirements | R1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | TO |  |  | TO
FAC-001-3 | Facility Interconnection Requirements | R3. | Each Transmission Owner shall address the following items in its Facility interconnection requirements: | TO |  |  | TO
FAC-001-3 | Facility Interconnection Requirements | R4.3. | Procedures for confirming with those responsible for the reliability of affected systems that new or materially modified Facilities are within a Balancing Authority Area’s metered boundaries. | GO | GO
FAC-001-3 | Facility Interconnection Requirements | R4.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. | GO | GO
FAC-001-3 | Facility Interconnection Requirements | R4.1. | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). | GO | GO
FAC-001-3 | Facility Interconnection Requirements | R4. | Each applicable Generator Owner shall address the following items in its Facility interconnection requirements: | GO | GO
FAC-001-3 | Facility Interconnection Requirements | R3.3. | Procedures for confirming with those responsible for the reliability of affected systems that new or materially modified Facilities are within a Balancing Authority Area’s metered boundaries. | TO |  |  | TO
FAC-001-3 | Facility Interconnection Requirements | R3.1. | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). | TO |  |  | TO
FAC-001-3 | Facility Interconnection Requirements | R2. | Each applicable Generator Owner shall document Facility interconnection requirements and make them available upon request within 45 calendar days of full execution of an Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. | GO | GO
FAC-001-3 | Facility Interconnection Requirements | R1.3. | end-user Facilities. | TO |  |  | TO
FAC-001-3 | Facility Interconnection Requirements | R1.2. | transmission Facilities; and | TO |  |  | TO
FAC-001-3 | Facility Interconnection Requirements | R1. | Each Transmission Owner shall document Facility interconnection requirements, update them as needed, and make them available upon request. Each Transmission Owner’s Facility interconnection requirements shall address interconnection requirements for: | TO |  |  | TO
FAC-001-3 | Facility Interconnection Requirements | R1.1. | generation Facilities; | TO |  |  | TO
FAC-001-3 | Facility Interconnection Requirements | R3.2. | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. | TO |  |  | TO
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1. | The Generator Owner, Transmission Owner, Distribution Provider, and Load-Serving Entity seeking to integrate generation facilities, transmission facilities, and electricity end-user facilities shall each coordinate and cooperate on its assessments with its Transmission Planner and Planning Authority. The assessment shall include: | TO, GO | GO |  | TO
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1.5. | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. | TO, GO | GO |  | TO
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1.4. | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance under both normal and contingency conditions in accordance with Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. | TO, GO | GO |  | TO
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1.3. | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. | TO, GO | GO |  | TO
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1.2. | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. | TO, GO | GO |  | TO
FAC-002-1 | Coordination of Plans For New Generation, Transmission, and End-User Facilities | R1.1. | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. | TO, GO | GO |  | TO
FAC-002-2 | Facility Interconnection Studies | R5. | Each applicable Generator Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | GO | GO
FAC-002-2 | Facility Interconnection Studies | R4. | Each Transmission Owner shall coordinate and cooperate with its Transmission Planner or Planning Coordinator on studies regarding requested new or materially modified interconnections to its Facilities, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | TO |  |  | TO
FAC-002-2 | Facility Interconnection Studies | R3. | Each Transmission Owner, each Distribution Provider, and each Load-Serving Entity seeking to interconnect new transmission Facilities or electricity end-user Facilities, or to materially modify existing interconnections of transmission Facilities or electricity end-user Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | TO |  |  | TO
FAC-002-2 | Facility Interconnection Studies | R2. | Each Generator Owner seeking to interconnect new generation Facilities, or to materially modify existing interconnections of generation Facilities, shall coordinate and cooperate on studies with its Transmission Planner or Planning Coordinator, including but not limited to the provision of data as described in R1, Parts 1.1-1.4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | GO | GO
FAC-003-2 | Transmission Vegetation Management | R3. | Each Transmission Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | TO |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning]: | TO |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R4. | Each Transmission Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the Transmission Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment [Violation Risk Factor: Medium] [Time Horizon: Real-time]. | TO |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R5. | When a Transmission Owner is constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the Transmission Owner shall take corrective action to ensure continued vegetation management to prevent encroachments [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R6. | Each Transmission Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW5. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]. | TO |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R2. | Each Transmission Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below2 [Violation Risk Factor: Medium] [Time Horizon: Real-time]: 1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage,3 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage,4 3. An encroachment due to blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage,4 4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage4 | TO |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R7. | Each Transmission Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) Examples of reasons for modification to annual plan may include [Violation Risk Factor: Medium] [Time Horizon: Operations Planning]: • Change in expected growth rate/ environmental factors • Circumstances that are beyond the control of a Transmission Owner6 • Rescheduling work between growing seasons • Crew or contractor availability/ Mutual assistance agreements • Identified unanticipated high priority work • Weather conditions/Accessibility • Permitting delays • Land ownership changes/Change in land use by the landowner • Emerging technologies | TO |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R1. | Each Transmission Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below2. 1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, [Violation Risk Factor: High] [Time Horizon: Real-time]: 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage,4 4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage.4 | TO |  |  | TO
FAC-003-2 | Transmission Vegetation Management | R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; | TO |  |  | TO
FAC-003-3 | Transmission Vegetation Management | R7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) Examples of reasons for modification to annual plan may include | TO, GO | GO |  | TO
FAC-003-3 | Transmission Vegetation Management | R2. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below9 1. An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, [Violation Risk Factor: Medium] [Time Horizon: Real-time]: 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, 4. An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage | TO, GO | GO |  | TO
FAC-003-3 | Transmission Vegetation Management | R3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | TO, GO | GO |  | TO
FAC-003-3 | Transmission Vegetation Management | R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; | TO, GO | GO |  | TO
FAC-003-3 | Transmission Vegetation Management | R3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | TO, GO | GO |  | TO
FAC-003-3 | Transmission Vegetation Management | R4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment | TO, GO | GO |  | TO
FAC-003-3 | Transmission Vegetation Management | R5. | When a applicable Transmission Owner and applicable Generator Owner is constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments | TO, GO | GO |  | TO
FAC-003-3 | Transmission Vegetation Management | R6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW14 | TO, GO | GO |  | TO
FAC-003-3 | Transmission Vegetation Management | R1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below4 1. An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, [Violation Risk Factor: High] [Time Horizon: Real-time]: 2. An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, 3. An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage 4. An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage., | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7.10. | Each applicable Transmission Owner and applicable Generator Owner has evidence that it completed its annual vegetation work plan for its applicable lines. Examples of acceptable forms of evidence may include a copy of the completed annual work plan (as finally modified), dated work orders, dated invoices, or dated inspection records. | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R6. | Each applicable Transmission Owner and applicable Generator Owner shall perform a Vegetation Inspection of 100% of its applicable transmission lines (measured in units of choice - circuit, pole line, line miles or kilometers, etc.) at least once per calendar year and with no more than 18 calendar months between inspections on the same ROW14 | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7. | Each applicable Transmission Owner and applicable Generator Owner shall complete 100% of its annual vegetation work plan of applicable lines to ensure no vegetation encroachments occur within the MVCD. Modifications to the work plan in response to changing conditions or to findings from vegetation inspections may be made (provided they do not allow encroachment of vegetation into the MVCD) and must be documented. The percent completed calculation is based on the number of units actually completed divided by the number of units in the final amended plan (measured in units of choice - circuit, pole line, line miles or kilometers, etc.). Examples of reasons for modification to annual plan may include | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7.2. | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner15 | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7.4. | Crew or contractor availability/Mutual assistance agreements | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7.5. | Identified unanticipated high priority work | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7.6. | Weather conditions/Accessibility | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7.7. | Permitting delays | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R5. | When an applicable Transmission Owner and an applicable Generator Owner are constrained from performing vegetation work on an applicable line operating within its Rating and all Rated Electrical Operating Conditions, and the constraint may lead to a vegetation encroachment into the MVCD prior to the implementation of the next annual work plan, then the applicable Transmission Owner or applicable Generator Owner shall take corrective action to ensure continued vegetation management to prevent encroachments | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7.9. | Emerging technologies | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7.1. | Change in expected growth rate/environmental factors | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7.8. | Land ownership changes/Change in land use by the landowner | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R1.4. | An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R7.3. | Rescheduling work between growing seasons | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R4. | Each applicable Transmission Owner and applicable Generator Owner, without any intentional time delay, shall notify the control center holding switching authority for the associated applicable line when the applicable Transmission Owner and applicable Generator Owner has confirmed the existence of a vegetation condition that is likely to cause a Fault at any moment | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R1. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the Minimum Vegetation Clearance Distance (MVCD) of its applicable line(s) which are either an element of an IROL, or an element of a Major WECC Transfer Path; operating within their Rating and all Rated Electrical Operating Conditions of the types shown below4 : | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R1.1. | An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R1.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R2. | Each applicable Transmission Owner and applicable Generator Owner shall manage vegetation to prevent encroachments into the MVCD of its applicable line(s) which are not either an element of an IROL, or an element of a Major WECC Transfer Path; operating within its Rating and all Rated Electrical Operating Conditions of the types shown below | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R2.1. | An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R2.2. | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R2.3. | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R2.4. | An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R3. | Each applicable Transmission Owner and applicable Generator Owner shall have documented maintenance strategies or procedures or processes or specifications it uses to prevent the encroachment of vegetation into the MVCD of its applicable lines that accounts for the following: | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R3.1. | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R3.2. | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. | TO, GO | GO |  | TO
FAC-003-4 | Transmission Vegetation Management | R1.2. | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, | TO, GO | GO |  | TO
FAC-008-2 | Facility Ratings | R1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. | GO | GO
FAC-008-2 | Facility Ratings | R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | GO | GO
FAC-008-2 | Facility Ratings | R3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: | TO |  |  | TO
FAC-008-2 | Facility Ratings | R3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. | TO |  |  | TO
FAC-008-2 | Facility Ratings | R3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: | TO |  |  | TO
FAC-008-2 | Facility Ratings | R2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | GO | GO
FAC-008-2 | Facility Ratings | R2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | GO | GO
FAC-008-2 | Facility Ratings | R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. | GO | GO
FAC-008-2 | Facility Ratings | R2.2.4. | Operating limitations. | GO | GO
FAC-008-2 | Facility Ratings | R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | GO | GO
FAC-008-2 | Facility Ratings | R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | GO | GO
FAC-008-2 | Facility Ratings | R2.2.1. | Equipment Rating standard(s) used in development of this methodology. | GO | GO
FAC-008-2 | Facility Ratings | R2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: | GO | GO
FAC-008-2 | Facility Ratings | R2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. | GO | GO
FAC-008-2 | Facility Ratings | R1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | GO | GO
FAC-008-2 | Facility Ratings | R1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. | GO | GO
FAC-008-2 | Facility Ratings | R3.2.4. | Operating limitations. | TO |  |  | TO
FAC-008-2 | Facility Ratings | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. | GO | GO
FAC-008-2 | Facility Ratings | R6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | TO, GO | GO |  | TO
FAC-008-2 | Facility Ratings | R3.2.1. | Equipment Rating standard(s) used in development of this methodology. | TO |  |  | TO
FAC-008-2 | Facility Ratings | R7. | Each Transmission Owner and Generator Owner shall provide Facility Ratings for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. | TO, GO | GO |  | TO
FAC-008-2 | Facility Ratings | R5. | If a Reliability Coordinator, Transmission Operator, Transmission Planner or Planning Coordinator provides documented comments on its technical review of a Transmission Owner’s Facility Ratings methodology or Generator Owner’s documentation for determining its Facility Ratings and its Facility Rating methodology, the Transmission Owner or Generator Owner shall provide a response to that commenting entity within 45 calendar days of receipt of those comments. The response shall indicate whether a change will be made to the Facility Ratings methodology and, if no change will be made to that Facility Ratings methodology, the reason why. | TO, GO | GO |  | TO
FAC-008-2 | Facility Ratings | R4. | Each Transmission Owner shall make its Facility Ratings methodology and each Generator Owner shall each make its documentation for determining its Facility Ratings and its Facility Ratings methodology available for inspection and technical review by those Reliability Coordinators, Transmission Operators, Transmission Planners and Planning Coordinators that have responsibility for the area in which the associated Facilities are located, within 21 calendar days of receipt of a request. | TO, GO | GO |  | TO
FAC-008-2 | Facility Ratings | R3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | TO |  |  | TO
FAC-008-2 | Facility Ratings | R3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | TO |  |  | TO
FAC-008-2 | Facility Ratings | R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. | TO |  |  | TO
FAC-008-2 | Facility Ratings | R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | TO |  |  | TO
FAC-008-2 | Facility Ratings | R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | TO |  |  | TO
FAC-008-2 | Facility Ratings | R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | TO |  |  | TO
FAC-008-3 | Facility Ratings | R8.2.2. | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. | TO, GO | GO |  | TO
FAC-008-3 | Facility Ratings | R7. | Each Generator Owner shall provide Facility Ratings (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s) as scheduled by such requesting entities. | GO | GO
FAC-008-3 | Facility Ratings | R3.2.4. | Operating limitations.2 | TO |  |  | TO
FAC-008-3 | Facility Ratings | R3.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | TO |  |  | TO
FAC-008-3 | Facility Ratings | R3.4. | The process by which the Rating of equipment that comprises a Facility is determined. | TO |  |  | TO
FAC-008-3 | Facility Ratings | R3.4.1. | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | TO |  |  | TO
FAC-008-3 | Facility Ratings | R3.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | TO |  |  | TO
FAC-008-3 | Facility Ratings | R6. | Each Transmission Owner and Generator Owner shall have Facility Ratings for its solely and jointly owned Facilities that are consistent with the associated Facility Ratings methodology or documentation for determining its Facility Ratings. | TO, GO | GO |  | TO
FAC-008-3 | Facility Ratings | R8. | Each Transmission Owner (and each Generator Owner subject to Requirement R2) shall provide requested information as specified below (for its solely and jointly owned Facilities that are existing Facilities, new Facilities, modifications to existing Facilities and re-ratings of existing Facilities) to its associated Reliability Coordinator(s), Planning Coordinator(s), Transmission Planner(s), Transmission Owner(s) and Transmission Operator(s): | TO, GO | GO |  | TO
FAC-008-3 | Facility Ratings | R8.1. | As scheduled by the requesting entities: | TO, GO | GO |  | TO
FAC-008-3 | Facility Ratings | R8.1.1. | Facility Ratings | TO, GO | GO |  | TO
FAC-008-3 | Facility Ratings | R8.1.2. | Identity of the most limiting equipment of the Facilities | TO, GO | GO |  | TO
FAC-008-3 | Facility Ratings | R3.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | TO |  |  | TO
FAC-008-3 | Facility Ratings | R8.2.1. | Identity of the existing next most limiting equipment of the Facility | TO, GO | GO |  | TO
FAC-008-3 | Facility Ratings | R3.2.1. | Equipment Rating standard(s) used in development of this methodology. | TO |  |  | TO
FAC-008-3 | Facility Ratings | R8.2. | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: | TO, GO | GO |  | TO
FAC-008-3 | Facility Ratings | R2.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. | GO | GO
FAC-008-3 | Facility Ratings | R1. | Each Generator Owner shall have documentation for determining the Facility Ratings of its solely and jointly owned generator Facility(ies) up to the low side terminals of the main step up transformer if the Generator Owner does not own the main step up transformer and the high side terminals of the main step up transformer if the Generator Owner owns the main step up transformer. | GO | GO
FAC-008-3 | Facility Ratings | R1.1. | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. | GO | GO
FAC-008-3 | Facility Ratings | R3.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | TO |  |  | TO
FAC-008-3 | Facility Ratings | R2. | Each Generator Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned equipment connected between the location specified in R1 and the point of interconnection with the Transmission Owner that contains all of the following. | GO | GO
FAC-008-3 | Facility Ratings | R2.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: | GO | GO
FAC-008-3 | Facility Ratings | R2.2.1. | Equipment Rating standard(s) used in development of this methodology. | GO | GO
FAC-008-3 | Facility Ratings | R2.2.2. | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. | GO | GO
FAC-008-3 | Facility Ratings | R2.2.3. | Ambient conditions (for particular or average conditions or as they vary in real-time). | GO | GO
FAC-008-3 | Facility Ratings | R2.2.4. | Operating limitations.1 | GO | GO
FAC-008-3 | Facility Ratings | R2.3. | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | GO | GO
FAC-008-3 | Facility Ratings | R2.4. | The process by which the Rating of equipment that comprises a Facility is determined. | GO | GO
FAC-008-3 | Facility Ratings | R2.4.1. | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. | GO | GO
FAC-008-3 | Facility Ratings | R2.4.2. | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. | GO | GO
FAC-008-3 | Facility Ratings | R3. | Each Transmission Owner shall have a documented methodology for determining Facility Ratings (Facility Ratings methodology) of its solely and jointly owned Facilities (except for those generating unit Facilities addressed in R1 and R2) that contains all of the following: | TO |  |  | TO
FAC-008-3 | Facility Ratings | R3.1. | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following: • Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating. • One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. | TO |  |  | TO
FAC-008-3 | Facility Ratings | R3.2. | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: | TO |  |  | TO
FAC-008-3 | Facility Ratings | R1.2. | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. | GO | GO
IRO-001-1.1 | Reliability Coordination - Responsibilities and Authorities | R8. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. | GOP |  | GOP
IRO-001-2 | Reliability Coordination - Responsibilities and Authorities | R7. | Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall comply with Reliability Coordinator directives unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, the Transmission Operator, Balancing Authority, Generator Operator, Transmission Service Provider, Load-Serving Entity, or Purchasing-Selling Entity shall immediately inform the Reliability Coordinator of the inability to perform the directive so that the Reliability Coordinator may implement alternate remedial actions. | GOP |  | GOP
IRO-001-3 | Reliability Coordination - Responsibilities and Authorities | R2. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s direction unless compliance with the direction cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Real-time Operations, Same Day Operations and Operations Planning] | GOP |  | GOP
IRO-001-3 | Reliability Coordination - Responsibilities and Authorities | R3. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator upon recognition of its inability to perform as directed in accordance with Requirement R2. [Violation Risk Factor: High] [Time Horizon: Real-time Operations, Same Day Operations and Operations Planning] | GOP |  | GOP
IRO-001-4 | Reliability Coordination – Responsibilities | R3. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall inform its Reliability Coordinator of its inability to perform the Operating Instruction issued by its Reliability Coordinator in Requirement R1. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | GOP |  | GOP
IRO-001-4 | Reliability Coordination – Responsibilities | R2. | Each Transmission Operator, Balancing Authority, Generator Operator, and Distribution Provider shall comply with its Reliability Coordinator’s Operating Instructions unless compliance with the Operating Instructions cannot be physically implemented or unless such actions would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-time Operations] | GOP |  | GOP
IRO-005-3.1(i)a | Reliability Coordination — Current Day Operations | R10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | GOP |  | GOP
IRO-005-3.1a | Reliability Coordination — Current Day Operations | R10. | In instances where there is a difference in derived limits, the Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities shall always operate the Bulk Electric System to the most limiting parameter. | GOP |  | GOP
IRO-010-1a | Reliability Coordinator Data Specification and Collection | R3. | Each Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-serving Entity, Reliability Coordinator, Transmission Operator, and Transmission Owner shall provide data and information, as specified, to the Reliability Coordinator(s) with which it has a reliability relationship. (Violation Risk Factor: Medium) (Time Horizon: Operations Planning; Same-day Operations; Real-time Operations) | TO, GOP, GO | GO | GOP | TO
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R3. | Each Reliability Coordinator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Operator, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R2 shall satisfy the obligations of the documented specifications using: (Violation Risk Factor: Medium) (Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations) | TO, GOP, GO | GO | GOP | TO
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R3.3. | A mutually agreeable security protocol | TO, GOP, GO | GO | GOP | TO
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R3.2. | A mutually agreeable process for resolving data conflicts | TO, GOP, GO | GO | GOP | TO
IRO-010-2 | Reliability Coordinator Data Specification and Collection | R3.1. | A mutually agreeable format | TO, GOP, GO | GO | GOP | TO
MOD-010-0 | Steady-State Data for Modeling and Simulation of the Interconnected Transmission System | R1. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall provide appropriate equipment characteristics, system data, and existing and future Interchange Schedules in compliance with its respective Interconnection Regional steady-state Real-Time Applications and simulation data requirements and reporting procedures as defined in Reliability Standard MOD-011-0_R 1. | TO, GO | GO |  | TO
MOD-010-0 | Steady-State Data for Modeling and Simulation of the Interconnected Transmission System | R2. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-011-0_R1) shall provide this steady-state Real-Time Applications and simulation data to the Regional Reliability Organizations, NERC, and those entities specified within Reliability Standard MOD-011-0_R 1. If no schedule exists, then these entities shall provide the data on request (30 calendar days). | TO, GO | GO |  | TO
MOD-012-0 | Dynamics Data for Modeling and Simulation of the Interconnected Transmission System | R1. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R1) shall provide appropriate equipment characteristics and system data in compliance with the respective Interconnection-wide Regional dynamics system Real-Time Applications and simulation data requirements and reporting procedures as defined in Reliability Standard MOD-013-0_R1. | TO, GO | GO |  | TO
MOD-012-0 | Dynamics Data for Modeling and Simulation of the Interconnected Transmission System | R2. | The Transmission Owners, Transmission Planners, Generator Owners, and Resource Planners (specified in the data requirements and reporting procedures of MOD-013-0_R4) shall provide dynamics system Real-Time Applications and simulation data to its Regional Reliability Organization(s), NERC, and those entities specified within the applicable reporting procedures identified in Reliability Standard MOD-013-0_R 1. If no schedule exists, then these entities shall provide data on request (30 calendar days). | TO, GO | GO |  | TO
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R3. | The Generator Owner shall follow its Regional Reliability Organization’s procedures for verifying and reporting its gross and net Real Power generating capability per R1. | GO | GO
MOD-024-1 | Verification of Generator Gross and Net Real Power Capability | R2. | The Regional Reliability Organization shall provide its generator gross and net Real Power capability verification and reporting procedures, and any changes to those procedures, to the Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners affected by the procedure within 30 calendar days of the approval. | GOP, GO | GO | GOP
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R2. | The Regional Reliability Organization shall provide its generator gross and net Reactive Power capability verification and reporting procedures, and any changes to those procedures, to the Generator Owners, Generator Operators, Transmission Operators, Planning Authorities, and Transmission Planners affected by the procedure within 30 calendar days of the approval. | GOP, GO | GO | GOP
MOD-025-1 | Verification of Generator Gross and Net Reactive Power Capability | R3. | The Generator Owner shall follow its Regional Reliability Organization’s procedures for verifying and reporting its gross and net Reactive Power generating capability per R1. | GO | GO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R2.1. | Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. | TO, GO | GO |  | TO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R3.1. | Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. | TO, GO | GO |  | TO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R2.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | TO, GO | GO |  | TO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R2. | Each Generator Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R1.1. | Verify the Real Power capability of its generating units in accordance with Attachment 1. | TO, GO | GO |  | TO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R1. | Each Generator Owner shall provide its Transmission Planner with verification of the Real Power capability of its applicable Facilities as follows: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R3.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | TO, GO | GO |  | TO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R3. | Each Transmission Owner shall provide its Transmission Planner with verification of the Reactive Power capability of its applicable Facilities as follows: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
MOD-025-2 | Verification and Data Reporting of Generator Real and Reactive Power Capability and Synchronous Condenser Reactive Power Capability | R1.2. | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. | TO, GO | GO |  | TO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.4. | Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, | GO | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1. | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the following | GO | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R5. | Each Generator Owner shall provide a written response to its Transmission Planner, within 90 calendar days following receipt of a technically justified6 unit request from the Transmission Planner to perform a model review of a unit or plant that includes one of the following: [Violation Risk Factor: Lower] [Time Horizon: Operations Planning]  Details of plans to verify the model (in accordance with Requirement R2), or  Corrected model data including the source of revised model data such as discovery of manufacturer test values to replace generic model data or updating of data parameters based on an on-site review of the equipment. | GO | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R4. | Each Generator Owner shall provide revised model data or plans to perform model verification4 (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the excitation control system or plant volt/var control function that alter the equipment response characteristic.5 [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | GO | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R3. | Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit:  Written notification from its Transmission Planner (in accordance with Requirement R6) that the excitation control system or plant volt/var control function model is not usable,  Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the excitation control system or plant volt/var control function model, or  Written comments and supporting evidence from its Transmission Planner indicating that the simulated excitation control system or plant volt/var control function model response did not match the recorded response to a transmission system event. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification3 (in accordance with Requirement R2). [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | GO | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.5. | Compensation settings (such as droop, line drop, differential compensation), if used, and | GO | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.3. | Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, | GO | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.2. | Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), | GO | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.1. | Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, | GO | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2. | Each Generator Owner shall provide for each applicable unit, a verified generator excitation control system or plant volt/var control function model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-026 Attachment 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | GO | GO
MOD-026-1 | Verification of Models and Data for Generator Excitation Control System or Plant Volt/Var Control Functions | R2.1.6. | Model structure and data for power system stabilizer, if so equipped. | GO | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R4. | Each Generator Owner shall provide revised model data or plans to perform model verification4 (in accordance with Requirement R2) for an applicable unit to its Transmission Planner within 180 calendar days of making changes to the turbine/governor and load control or active power/frequency control system that alter the equipment response characteristic5. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | GO | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R3. | Each Generator Owner shall provide a written response to its Transmission Planner within 90 calendar days of receiving one of the following items for an applicable unit.  Written notification, from its Transmission Planner (in accordance with Requirement R5) that the turbine/governor and load control or active power/frequency control model is not “usable,”  Written comments from its Transmission Planner identifying technical concerns with the verification documentation related to the turbine/governor and load control or active power/frequency control model, or  Written comments and supporting evidence from its Transmission Planner indicating that the simulated turbine/governor and load control or active power/frequency control response did not approximate the recorded response for three or more transmission system events. The written response shall contain either the technical basis for maintaining the current model, the model changes, or a plan to perform model verification3 (in accordance with Requirement R2). [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | GO | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1.5. | Representation of the real power response effects of outer loop controls (such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. | GO | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1.2. | Type of governor and load control or active power control/frequency control1 equipment, | GO | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1.1. | Documentation comparing the applicable unit’s MW model response to the recorded MW response for either:  A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line,  A speed governor reference change with the applicable unit online, or  A partial load rejection test,2 | GO | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1. | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: | GO | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2. | Each Generator Owner shall provide, for each applicable unit, a verified turbine/governor and load control or active power/frequency control model, including documentation and data (as specified in Part 2.1) to its Transmission Planner in accordance with the periodicity specified in MOD-027 Attachment 1. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | GO | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1.4. | Model structure and data for turbine/governor and load control or active power/frequency control, and | GO | GO
MOD-027-1 | Verification of Models and Data for Turbine/Governor and Load Control or Active Power/Frequency Control Functions | R2.1.3. | A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), | GO | GO
MOD-032-1 | Data for Power System Modeling and Analysis | R3.1. | Provide either updated data or an explanation with a technical basis for maintaining the current data; | TO, GO | GO |  | TO
MOD-032-1 | Data for Power System Modeling and Analysis | R3. | Upon receipt of written notification from its Planning Coordinator or Transmission Planner regarding technical concerns with the data submitted under Requirement R2, including the technical basis or reason for the technical concerns, each notified Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, or Transmission Service Provider shall respond to the notifying Planning Coordinator or Transmission Planner as follows: [Violation Risk Factor: Lower] [Time Horizon: Long‐term Planning] | TO, GO | GO |  | TO
MOD-032-1 | Data for Power System Modeling and Analysis | R3.2. | Provide the response within 90 calendar days of receipt, unless a longer time period is agreed upon by the notifying Planning Coordinator or Transmission Planner. | TO, GO | GO |  | TO
MOD-032-1 | Data for Power System Modeling and Analysis | R2. | Each Balancing Authority, Generator Owner, Load Serving Entity, Resource Planner, Transmission Owner, and Transmission Service Provider shall provide steady‐state, dynamics, and short circuit Real-Time Applications data to its Transmission Planner(s) and Planning Coordinator(s) according to the data requirements and reporting procedures developed by its Planning Coordinator and Transmission Planner in Requirement R1. For data that has not changed since the last submission, a written confirmation that the data has not changed is sufficient. [Violation Risk Factor: Medium] [Time Horizon: Long‐term Planning] | TO, GO | GO |  | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. [Risk Factor: High] | GOP |  | GOP
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4.2. | Operate the electric system to meet the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | GOP |  | GOP
NUC-001-2.1 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4. | Communications and training: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4.5. | Provisions for personnel training, as related to NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.2. | Technical requirements and analysis: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.3.7. | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.4. | Communications and training: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt [Risk Factor: Lower] | GOP |  | GOP
NUC-001-2.1 | Nuclear Plant Interface Coordination | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements1 that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1 | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.2. | Technical requirements and analysis: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1.3. | A requirement to review the agreement(s) at least every three years. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1.2. | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1.4. | A dispute resolution mechanism. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.6. | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.3.7. | Coordination of the NPIRs with transmission system Remedial Action Schemes and underfrequency and undervoltage load shedding programs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4. | Communications and training: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4. | Communications and training: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1. | Administrative elements: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4.5. | Provisions for personnel training, as related to NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.4.1. | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements1 that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1.1. | Definitions of key terms used in the agreement. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt [Risk Factor: Lower] | GOP |  | GOP
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9.1. | Administrative elements: | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator. [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall: [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4.2. | Operate the electric system to meet the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include, as a minimum, the following elements within the agreement(s) identified in R2: [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | GOP |  | GOP
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. [Risk Factor: Medium] | TO, GOP, GO | GO | GOP | TO
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R5. | The Nuclear Plant Generator Operator shall operate per the Agreements developed in accordance with this standard. [Risk Factor: High] | GOP |  | GOP
NUC-001-2.1(i) | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design, configuration, operations, limits, Protection Systems, or capabilities that may impact the ability of the electric system to meet the NPIRs. [Risk Factor: High] | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3. | Operations and maintenance coordination | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.2.3. | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.2.2. | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. --Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. -- Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.2. | Technical requirements and analysis: | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.1. | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4. | Communications and training Administrative elements: | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.2.1. | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.2. | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.3. | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.4. | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.5. | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.6. | Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4. | Communications and training Administrative elements: | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4.1. | Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4.2. | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4.3. | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.3.7. | Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R1. | The Nuclear Plant Generator Operator shall provide the proposed NPIRs in writing to the applicable Transmission Entities and shall verify receipt. | GOP |  | GOP
NUC-001-3 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. --Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. -- Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4.5. | Provisions for personnel training, as related to NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R2. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall have in effect one or more Agreements that include mutually agreed to NPIRs and document how the Nuclear Plant Generator Operator and the applicable Transmission Entities shall address and implement these NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator.: | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R3. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall incorporate the NPIRs into their planning analyses of the electric system and shall communicate the results of these analyses to the Nuclear Plant Generator Operator.: | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R4. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9.4.4. | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R4.2. | Operate the electric system to meet the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R4.3. | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R5. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall operate the nuclear plant to meet the NPIRs. | GOP |  | GOP
NUC-001-3 | Nuclear Plant Interface Coordination | R6. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities and the Nuclear Plant Generator Operator shall coordinate outages and maintenance activities which affect the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R7. | Per the Agreements developed in accordance with this standard, the Nuclear Plant Generator Operator shall inform the applicable Transmission Entities of actual or proposed changes to nuclear plant design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | GOP |  | GOP
NUC-001-3 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R9. | The Nuclear Plant Generator Operator and the applicable Transmission Entities shall include the following elements in aggregate within the Agreement(s) identified in R2. --Where multiple Agreements with a single Transmission Entity are put into effect, the R9 elements must be addressed in aggregate within the Agreements; however, each Agreement does not have to contain each element. The Nuclear Plant Generator Operator and the Transmission Entity are responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements. -- Where Agreements with multiple Transmission Entities are required, the Nuclear Plant Generator Operator is responsible for ensuring all the R9 elements are addressed in aggregate within the Agreements with the Transmission Entities. The Agreements with each Transmission Entity do not have to contain each element; however, the Agreements with the multiple Transmission Entities, in the aggregate, must address all R9 elements. For each Agreement(s), the Nuclear Plant Generator Operator and the Transmission Entity are responsible to ensure the Agreement(s) contain(s) the elements of R9 applicable to that Transmission Entity. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R8. | Per the Agreements developed in accordance with this standard, the applicable Transmission Entities shall inform the Nuclear Plant Generator Operator of actual or proposed changes to electric system design (e.g., protective relay setpoints), configuration, operations, limits, or capabilities that may impact the ability of the electric system to meet the NPIRs. | TO, GOP, GO | GO | GOP | TO
NUC-001-3 | Nuclear Plant Interface Coordination | R4.1. | Incorporate the NPIRs into their operating analyses of the electric system. | TO, GOP, GO | GO | GOP | TO
PER-005-2 | Operations Personnel Training | R3. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify, at least once, the capabilities of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company-specific Real-time reliability-related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. | TO |  |  | TO
PER-005-2 | Operations Personnel Training | R3.1. | Within six months of a modification or addition of a BES company-specific Real-time reliability-related task, each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify the capabilities of each of its personnel identified in Requirement R1 or Requirement R2 to perform the new or modified BES company-specific Real-time reliability-related tasks identified in Requirement R1 part 1.1 or Requirement R2 part 2.1. | TO |  |  | TO
PER-005-2 | Operations Personnel Training | R4. | Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner that (1) has operational authority or control over Facilities with established Interconnection Reliability Operating Limits (IROLs), or (2) has established protection systems or operating guides to mitigate IROL violations, shall provide its personnel identified in Requirement R1 or Requirement R2 with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES. | TO |  |  | TO
PER-005-2 | Operations Personnel Training | R4.1. | A Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that did not previously meet the criteria of Requirement R4, shall comply with Requirement R4 within 12 months of meeting the criteria. | TO |  |  | TO
PER-005-2 | Operations Personnel Training | R2.4. | Each Transmission Owner shall conduct an evaluation each calendar year of the training program established in Requirement R2 to identify any needed changes to the training program and shall implement the changes identified. | TO |  |  | TO
PER-005-2 | Operations Personnel Training | R6.1. | Each Generator Operator shall conduct an evaluation each calendar year of the training established in Requirement R6 to identify and implement changes to the training. | GOP |  | GOP
PER-005-2 | Operations Personnel Training | R2. | Each Transmission Owner shall use a systematic approach to develop and implement a training program for its personnel identified in Applicability Section 4.1.4.1 of this standard as follows: | TO |  |  | TO
PER-005-2 | Operations Personnel Training | R6. | Each Generator Operator shall use a systematic approach to develop and implement training to its personnel identified in Applicability Section 4.1.5.1 of this standard, on how their job function(s) impact the reliable operations of the BES during normal and emergency operations. | GOP |  | GOP
PER-005-2 | Operations Personnel Training | R2.3. | Each Transmission Owner shall deliver training to its personnel identified in Applicability Section 4.1.4.1 of this standard according to its training program. | TO |  |  | TO
PER-005-2 | Operations Personnel Training | R2.2. | Each Transmission Owner shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 2.1. | TO |  |  | TO
PER-005-2 | Operations Personnel Training | R2.1.1. | Each Transmission Owner shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 2.1 each calendar year. | TO |  |  | TO
PER-005-2 | Operations Personnel Training | R2.1. | Each Transmission Owner shall create a list of BES company-specific Real-time reliability-related tasks based on a defined and documented methodology. | TO |  |  | TO
PER-006-1 | Specific Training for Personnel | R1. | Each Generator Operator shall provide training to personnel identified in Applicability section 4.1.1.1. on the operational functionality of Protection Systems and Remedial Action Schemes (RAS) that affect the output of the generating Facility(ies) it operates. | GO | GO
PRC-001-1.1 | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | GOP |  | GOP
PRC-001-1.1 | System Protection Coordination | R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. | GOP |  | GOP
PRC-001-1.1 | System Protection Coordination | R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | GOP |  | GOP
PRC-001-1.1 | System Protection Coordination | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | GOP |  | GOP
PRC-001-1.1 | System Protection Coordination | R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | GOP |  | GOP
PRC-001-1.1 | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | GOP |  | GOP
PRC-001-1.1 | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | GOP |  | GOP
PRC-001-1.1 | System Protection Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | GOP |  | GOP
PRC-001-1.1 | System Protection Coordination | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | GOP |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | GOP |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. | GOP |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | GOP |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | GOP |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | GOP |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | GOP |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | GOP |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | GOP |  | GOP
PRC-001-1.1(i) | System Protection Coordination | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | GOP |  | GOP
PRC-001-1.1(ii) | System Protection Coordination | R2.1. | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. | GOP |  | GOP
PRC-001-1.1(ii) | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | GOP |  | GOP
PRC-001-1.1(ii) | System Protection Coordination | R3.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. • Requirement R3.1 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | GOP |  | GOP
PRC-001-1.1(ii) | System Protection Coordination | R5. | A Generator Operator or Transmission Operator shall coordinate changes in generation, transmission, load or operating conditions that could require changes in the Protection Systems of others: | GOP |  | GOP
PRC-001-1.1(ii) | System Protection Coordination | R5.1. | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. | GOP |  | GOP
PRC-001-1.1(ii) | System Protection Coordination | R3. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | GOP |  | GOP
PRC-001-1.1(ii) | System Protection Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | GOP |  | GOP
PRC-001-1.1(ii) | System Protection Coordination | R2. | Each Generator Operator and Transmission Operator shall notify reliability entities of relay or equipment failures as follows: | GOP |  | GOP
PRC-001-2 | System Protection Coordination | R2. | A Generator Operator or Transmission Operator shall coordinate new protective systems and changes as follows. | GOP |  | GOP
PRC-001-2 | System Protection Coordination | R1. | Each Transmission Operator, Balancing Authority, and Generator Operator shall be familiar with the purpose and limitations of Protection System schemes applied in its area. | GOP |  | GOP
PRC-001-2 | System Protection Coordination | R2.1. | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. | GOP |  | GOP
PRC-001-2 | System Protection Coordination | R3. | Each Transmission Operator shall coordinate Protection Systems on major transmission lines and interconnections with neighboring Generator Operators, Transmission Operators, and Balancing Authorities. | GOP |  | GOP
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R7.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. | GO | GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R7.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | GO | GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R10.1. | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R7.1. | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. | GO | GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R9. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have DDR data that meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R7.4. | Frequency of at least one of the voltages in Requirement R7, Part 7.1. | GO | GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R8. | Each Transmission Owner and Generator Owner responsible for DDR data for the BES Elements identified in Requirement R5 shall have continuous data recording and storage. If the equipment was installed prior to the effective date of this standard and is not capable of continuous recording, triggered records must meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R8.1. | Triggered record lengths of at least three minutes. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R7. | Each Generator Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | GO | GO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R8.2. | At least one of the following three triggers:  Off nominal frequency trigger set at: Low High o Eastern Interconnection <59.75 Hz >61.0 Hz o Western Interconnection <59.55 Hz >61.0 Hz o ERCOT Interconnection <59.35 Hz >61.0 Hz o Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz  Rate of change of frequency trigger set at: o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/sec o Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/sec o ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/sec o Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec  Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R6.4. | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. | TO |  |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R9.1. | Input sampling rate of at least 960 samples per second. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R10. | Each Transmission Owner and Generator Owner shall time synchronize all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to meet the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R12. | Each Transmission Owner and Generator Owner shall, within 90-calendar days of the discovery of a failure of the recording capability for the SER, FR or DDR data, either: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning]  Restore the recording capability, or  Submit a Corrective Action Plan (CAP) to the Regional Entity and implement it. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11. | Each Transmission Owner and Generator Owner shall provide, upon request, all SER and FR data for the BES buses identified in Requirement R1 and DDR data for the BES Elements identified in Requirement R5 to the Responsible Entity, Regional Entity, or NERC in accordance with the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11.5. | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R10.2. | Synchronized device clock accuracy within ± 2 milliseconds of UTC. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R6.3. | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. | TO |  |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11.2. | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11.3. | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11.4. | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R9.2. | Output recording rate of electrical quantities of at least 30 times per second. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R1.3. | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. | TO |  |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R11.1. | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R6.2. | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. | TO |  |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R1. | Each Transmission Owner shall: [Violation Risk Factor: Lower ] [Time Horizon: Longterm Planning] | TO |  |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R1.2. | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. | TO |  |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R2. | Each Transmission Owner and Generator Owner shall have SER data for circuit breaker position (open/close) for each circuit breaker it owns connected directly to the BES buses identified in Requirement R1 and associated with the BES Elements at those BES buses. [Violation Risk Factor: Lower ] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R3. | Each Transmission Owner and Generator Owner shall have FR data to determine the following electrical quantities for each triggered FR for the BES Elements it owns connected to the BES buses identified in Requirement R1: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R3.1. | Phase-to-neutral voltage for each phase of each specified BES bus. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R3.2. | Each phase current and the residual or neutral current for the following BES Elements: | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R3.2.1. | Transformers that have a low-side operating voltage of 100kV or above. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4. | Each Transmission Owner and Generator Owner shall have FR data as specified in Requirement R3 that meets the following: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4.1. | A single record or multiple records that include: • A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or • At least two cycles of the pre-trigger data, the first three cycles of the posttrigger data, and the final cycle of the fault as seen by the fault recorder. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4.2. | A minimum recording rate of 16 samples per cycle. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4.3. | Trigger settings for at least the following: | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4.3.1. | Neutral (residual) overcurrent. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R6.1. | One phase-to-neutral or positive sequence voltage. | TO |  |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R4.3.2. | Phase undervoltage or overcurrent. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R3.2.2. | Transmission Lines. | TO, GO | GO |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R6. | Each Transmission Owner shall have DDR data to determine the following electrical quantities for each BES Element it owns for which it received notification as identified in Requirement R5: [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning ] | TO |  |  | TO
PRC-002-2 | Disturbance Monitoring and Reporting Requirements | R1.1. | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-2, Attachment 1. | TO |  |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R6.4. | Document additional triggers and deviations from the settings in 6.3.2 and 6.3.3 when local conditions dictate. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R15. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall share data within 30 days upon request. Each Reliability Coordinator, Transmission Owner, and Generator Owner shall provide recorded disturbance data from DMEs within 30 days of receipt of the request in each of the following cases: [Violation Risk Factor: Lower] [Time Horizon: Operations] | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R14.7. | A requirement to return failed units to service within 90 days. If a DME device will be out of service for greater than 90 days the owner shall keep a record of efforts aimed at restoring the DME to service. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R14.5. | Monthly verification of active analog quantities. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R14.4. | Monthly verification of time synchronization (if the loss of time synchronization is not monitored to a 24/7 control center). | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R14.3. | Monthly verification of communication channels used for accessing records remotely (if the entity relies on remote access and the channel is not monitored to a control center staffed around the clock, 24 hours a day, 7 days a week (24/7)). | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R14.2. | Summary of maintenance and testing procedures. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R14.1. | Maintenance and testing intervals and their basis. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R13. | Each Transmission Owner and Generator Owner that receives a request from the Reliability Coordinator to install a DDR shall acquire and install the DDR in accordance with R12. Reliability Coordinators, Transmission Owners, and Generator Owners shall mutually agree on an implementation schedule. [Violation Risk Factor: Medium] [Time Horizon: Planning and Operations Planning] | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R6.3.3. | Monitored phase undervoltage set at 0.85 pu or greater. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R15.1. | NERC, Regional Entity, Reliability Coordinator. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R17.4. | Operational Status. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R14. | Each Transmission Owner and Generator Owner shall establish a maintenance and testing program for stand alone DME (equipment whose only purpose is disturbance monitoring) that includes: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R17.1. | Type of DME. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R17.8. | Monitored electrical quantities. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R17.7. | All identified channels. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R17.6. | Monitored Elements. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R17.5. | Date last tested. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R14.6. | Verification of DDR and DFR settings in the software every six (6) years. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R17.2. | Make and model of equipment. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R6.3.2. | Neutral (residual) overcurrent set at 0.2 pu or less of rated CT secondary current. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R15.1. | NERC, Regional Entity, Reliability Coordinator. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R17. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall maintain, record and provide to the Regional Entity (RE), upon request, the following data on the DMEs installed to meet this standard: [Violation Risk Factor: Lower] [Time Horizon: Operations] | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R16.3. | Fault Recorder and DDR Files shall contain all monitored channels. SOE records shall contain station name, date, time resolved to milliseconds, SOE point name, status. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R16.2. | Disturbance Data files shall be named in conformance with the latest revision of IEEE Standard C37.232. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R16.1. | The data files shall be capable of being viewed, read, and analyzed with a generic COMTRADE analysis tool as per the latest revision of IEEE Standard C37.111. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R16. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall submit the data files conforming to the following format requirements: [Violation Risk Factor: Lower] [Time Horizon: Operations] | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R15.2. | Request from other Transmission Owners, Generator Owners within NPCC. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R17.3. | Installation location. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R2.3. | Shunt capacitors, shunt reactors. | TO |  |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R6.3.1. | Monitored phase overcurrents set at 1.5 pu or less of rated CT secondary current or Protective Relay tripping for all Protection Groups. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R15. | Each Reliability Coordinator, Transmission Owner and Generator Owner shall share data within 30 days upon request. Each Reliability Coordinator, Transmission Owner, and Generator Owner shall provide recorded disturbance data from DMEs within 30 days of receipt of the request in each of the following cases: [Violation Risk Factor: Lower] [Time Horizon: Operations] | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R1. | Each Transmission Owner and Generator Owner shall provide Sequence of Event (SOE) recording capability by installing Sequence of Event recorders or as part of another device, such as a Supervisory Control And Data Acquisition (SCADA) Remote Terminal Unit (RTU), a generator plant Digital (or Distributed) Control System (DCS) or part of Fault recording equipment. This capability shall: | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R1.1. | Be provided at all substations and at locations where circuit breaker operation affects continuity of service to radial Loads greater than 300MW, or the operation of which drops 50MVA Nameplate Rating or greater of Generation, or the operation of which creates a Generation/Load island. Be provided at generating units above 50MVA Nameplate Rating or series of generating units utilizing a control scheme such that the loss of 1 unit results in a loss of greater than 50MVA Nameplate Capacity, and at Generating Plants above 300MVA Name Plate Capacity. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R1.2. | Monitor the following at each location listed in 1.1: | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R1.2.1. | Transmission and Generator circuit breaker positions | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R1.2.2. | Protective Relay tripping for all Protection Groups that operate to trip circuit breakers identified in 1.2.1. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R1.2.3. | Teleprotection keying and receive | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R2. | Each Transmission Owner shall provide Fault recording capability for the following Elements at facilities where Fault recording equipment is required to be installed as per R3: [Violation Risk Factor: Medium] [Time Horizon: Planning and Operations Planning] | TO |  |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R2.2. | Autotransformers or phase-shifters connected to busses. | TO |  |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R2.4. | Individual generator line interconnections. | TO |  |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R2.5. | Dynamic VAR Devices. | TO |  |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R5.4. | Frequency. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R6.3. | Each Fault recorder shall be set to trigger for at least the following: | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R6.2. | Each Fault recorder shall have a minimum recording rate of 16 samples per cycle. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R6.1. | Each Fault recorder record duration shall be a minimum of one (1) second. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R2.1. | All transmission lines. | TO |  |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R5.5. | Real and reactive power. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R2.6. | HVDC terminals. | TO |  |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R5.3. | Polarizing currents and voltages, if used. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R5.2. | Three phase currents and neutral currents. | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R5.1. | Three phase-to-neutral voltages. (Common bus-side voltages may be used for lines.) | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R5. | Each Transmission Owner and Generator Owner shall record for Faults, sufficient electrical quantities for each monitored Element to determine the following: [Violation Risk Factor: Medium] [Time Horizon: Planning and Operations Planning] | TO, GO | GO |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R4. | Each Generator Owner shall provide Fault recording capability for Generating Plants at and above 200 MVA Capacity and connected through a generator step up (GSU) transformer to a Bulk Electric System Element unless Fault recording capability is already provided by the Transmission Owner. [Violation Risk Factor: Medium] [Time Horizon: Planning and Operations Planning] | GO | GO
PRC-002-NPCC-1 | Disturbance Monitoring | R3. | Each Transmission Owner shall have Fault recording capability that determines the Current Zero Time for loss of Bulk Electric System (BES) transmission Elements. [Violation Risk Factor: Medium] [Time Horizon: Planning and Operations Planning] | TO |  |  | TO
PRC-002-NPCC-1 | Disturbance Monitoring | R6. | Each Transmission Owner and Generator Owner shall provide Fault recording with the following capabilities: [Violation Risk Factor: Medium] [Time Horizon: Planning and Operations Planning] | TO, GO | GO |  | TO
PRC-004-2 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. | TO, GO | GO |  | TO
PRC-004-2 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | TO |  |  | TO
PRC-004-2 | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R2. | The Generator Owner shall analyze its generator Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | GO | GO
PRC-004-2.1(i)a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | TO |  |  | TO
PRC-004-2.1(i)a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures.  For Misoperations occurring on the Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES facilities, this requirement does not apply. | TO, GO | GO |  | TO
PRC-004-2.1(i)a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R2. | The Generator Owner shall analyze its generator and generator interconnection Facility Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures.  For Misoperations occurring on the Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES facilities, this requirement does not apply. | GO | GO
PRC-004-2.1a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R2. | The Generator Owner shall analyze its generator and generator interconnection Facility Protection System Misoperations, and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | GO | GO
PRC-004-2.1a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R3. | The Transmission Owner, any Distribution Provider that owns a transmission Protection System, and the Generator Owner shall each provide to its Regional Entity, documentation of its Misoperations analyses and Corrective Action Plans according to the Regional Entity’s procedures. | TO, GO | GO |  | TO
PRC-004-2.1a | Analysis and Mitigation of Transmission and Generation Protection System Misoperations | R1. | The Transmission Owner and any Distribution Provider that owns a transmission Protection System shall each analyze its transmission Protection System Misoperations and shall develop and implement a Corrective Action Plan to avoid future Misoperations of a similar nature according to the Regional Entity’s procedures. | TO |  |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Long-Term Planning]  Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or  Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: Medium][Time Horizon: Operations Planning, Long-Term Planning] | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-3 | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long-Term Planning] | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long-Term Planning] ● Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or ● Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: High] [Time Horizon: Operations Assessment, Operations Planning] ● The identification of the cause(s) of the Misoperation; or ● A declaration that no cause was identified. | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | TO, GO | GO |  | TO
PRC-004-3(i) | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: Medium] [Time Horizon: Operations Assessment, Operations Planning]  The identification of the cause(s) of the Misoperation; or  A declaration that no cause was identified. | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Long-Term Planning]  Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or  Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: Medium][Time Horizon: Operations Planning, Long-Term Planning] | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-4 | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: High] [Time Horizon: Operations Assessment, Operations Planning] ● The identification of the cause(s) of the Misoperation; or ● A declaration that no cause was identified. | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long-Term Planning] ● Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or ● Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-4(i) | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long-Term Planning] | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: Medium][Time Horizon: Operations Planning, Long‐Term Planning] | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Long‐Term Planning]  Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or  Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: Medium] [Time Horizon: Operations Assessment, Operations Planning]  The identification of the cause(s) of the Misoperation; or  A declaration that no cause was identified. | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation RisK Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: Medium][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-5 | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2.1. | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R6. | Each Transmission Owner, Generator Owner, and Distribution Provider shall implement each CAP developed in Requirement R5, and update each CAP if actions or timetables change, until completed. [Violation Risk Factor: High][Time Horizon: Operations Planning, Long‐Term Planning] | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns the Protection System component(s) that caused the Misoperation shall, within 60 calendar days of first identifying a cause of the Misoperation: [Violation Risk Factor: High] [Time Horizon: Operations Planning, Long‐Term Planning] ● Develop a Corrective Action Plan (CAP) for the identified Protection System component(s), and an evaluation of the CAP’s applicability to the entity’s other Protection Systems including other locations; or ● Explain in a declaration why corrective actions are beyond the entity’s control or would not improve BES reliability, and that no further corrective actions will be taken. | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that has not determined the cause(s) of a Misoperation, for a Misoperation identified in accordance with Requirement R1 or R3, shall perform investigative action(s) to determine the cause(s) of the Misoperation at least once every two full calendar quarters after the Misoperation was first identified, until one of the following completes the investigation: [Violation Risk Factor: High] [Time Horizon: Operations Assessment, Operations Planning] ● The identification of the cause(s) of the Misoperation; or ● A declaration that no cause was identified. | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that receives notification, pursuant to Requirement R2 shall, within the later of 60 calendar days of notification or 120 calendar days of the BES interrupting device(s) operation, identify whether its Protection System component(s) caused a Misoperation. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2.2. | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2.1.3. | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2.1.2. | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2.1.1. | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R1.3. | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R1.2. | The BES interrupting device owner owns all or part of the Composite Protection System; and | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R1.1. | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and | TO, GO | GO |  | TO
PRC-004-5(i) | Protection System Misoperation Identification and Correction | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated under the circumstances in Parts 1.1 through 1.3 shall, within 120 calendar days of the BES interrupting device operation, identify whether its Protection System component(s) caused a Misoperation: [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-004-5(I) | Protection System Misoperation Identification and Correction | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that owns a BES interrupting device that operated shall, within 120 calendar days of the BES interrupting device operation, provide notification as described in Parts 2.1 and 2.2. [Violation Risk Factor: High][Time Horizon: Operations Assessment, Operations Planning] | TO, GO | GO |  | TO
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R2.2. | Date each Protection System device was last tested/maintained. | TO, GO | GO |  | TO
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R2.1. | Evidence Protection System devices were maintained and tested within the defined intervals | TO, GO | GO |  | TO
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R1. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System shall have a Protection System maintenance and testing program for Protection Systems that affect the reliability of the BES. The program shall include: | TO, GO | GO |  | TO
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R1.1. | Maintenance and testing intervals and their basis. | TO, GO | GO |  | TO
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R1.2. | Summary of maintenance and testing procedures. | TO, GO | GO |  | TO
PRC-005-1.1b | Transmission and Generation Protection System Maintenance and Testing | R2. | Each Transmission Owner and any Distribution Provider that owns a transmission Protection System and each Generator Owner that owns a generation or generator interconnection Facility Protection System shall provide documentation of its Protection System maintenance and testing program and the implementation of that program to its Regional Entity on request (within 30 calendar days). The documentation of the program implementation shall include: | TO, GO | GO |  | TO
PRC-005-2 | Protection System Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2 | Protection System Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components | TO, GO | GO |  | TO
PRC-005-2 | Protection System Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2 | Protection System Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2 | Protection System Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2 | Protection System Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | TO, GO | GO |  | TO
PRC-005-2 | Protection System Maintenance | R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | TO, GO | GO |  | TO
PRC-005-2(i) | Protection System Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2(i) | Protection System Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | TO, GO | GO |  | TO
PRC-005-2(i) | Protection System Maintenance | R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | TO, GO | GO |  | TO
PRC-005-2(i) | Protection System Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. | TO, GO | GO |  | TO
PRC-005-2(i) | Protection System Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2(i) | Protection System Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2(i) | Protection System Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2(ii) | Protection System Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components | TO, GO | GO |  | TO
PRC-005-2(ii) | Protection System Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2(ii) | Protection System Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall maintain its Protection System Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, and Table 3. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2(ii) | Protection System Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2(ii) | Protection System Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-2(ii) | Protection System Maintenance | R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | TO, GO | GO |  | TO
PRC-005-2(ii) | Protection System Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems identified in Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | TO, GO | GO |  | TO
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R1.1. | The PSMP shall: Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | TO, GO | GO |  | TO
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. | TO, GO | GO |  | TO
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performancebased maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3 | Protection System and Automatic Reclosing Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | TO, GO | GO |  | TO
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | TO, GO | GO |  | TO
PRC-005-3(i) | Protection System and Automatic Reclosing Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. | TO, GO | GO |  | TO
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems and Automatic Reclosing identified in Facilities Section 4.2. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R1.1. | The PSMP shall: Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | TO, GO | GO |  | TO
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. | TO, GO | GO |  | TO
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performancebased maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes timebased maintenance program(s) shall maintain its Protection System and Automatic Reclosing Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System and Automatic Reclosing Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-3(ii) | Protection System and Automatic Reclosing Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | TO, GO | GO |  | TO
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance-based maintenance intervals in its PSMP shall follow the procedure established in PRC-005 Attachment A to establish and maintain its performance-based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time-based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time-based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance-based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performance-based program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.1. | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. | TO, GO | GO |  | TO
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-4 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | TO, GO | GO |  | TO
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | TO, GO | GO |  | TO
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance‐based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performancebased program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance‐based maintenance intervals in its PSMP shall follow the procedure established in PRC‐005 Attachment A to establish and maintain its performance‐based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.1. | Identify which maintenance method (time‐based, performance‐based per PRC‐005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time‐based program as described in Table 1‐4 and Table 3. | TO, GO | GO |  | TO
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | TO, GO | GO |  | TO
PRC-005-5 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time‐based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time‐based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐2, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes performance‐based maintenance program(s) in accordance with Requirement R2 shall implement and follow its PSMP for its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the performancebased program(s). [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that utilizes time‐based maintenance program(s) shall maintain its Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components that are included within the time‐based maintenance program in accordance with the minimum maintenance activities and maximum maintenance intervals prescribed within Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐3, and Table 5. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider shall demonstrate efforts to correct identified Unresolved Maintenance Issues. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a Protection System Maintenance Program (PSMP) for its Protection Systems, Automatic Reclosing, and Sudden Pressure Relaying identified in Section 4.2, Facilities. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] The PSMP shall: | TO, GO | GO |  | TO
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.1. | Identify which maintenance method (time‐based, performance‐based per PRC‐005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time‐based program as described in Table 1‐4 and Table 3. | TO, GO | GO |  | TO
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R1.2. | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1‐1 through 1‐5, Table 2, Table 3, Table 4‐1 through 4‐3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. | TO, GO | GO |  | TO
PRC-005-6 | Protection System , Automatic Reclosing and Sudden Pressure Relaying Maintenance | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses performance‐based maintenance intervals in its PSMP shall follow the procedure established in PRC‐005 Attachment A to establish and maintain its performance‐based intervals. [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-006-1 | Automatic Underfrequency Load Shedding | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | TO |  |  | TO
PRC-006-1 | Automatic Underfrequency Load Shedding | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | TO |  |  | TO
PRC-006-1 | Automatic Underfrequency Load Shedding | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | TO |  |  | TO
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | TO |  |  | TO
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for application determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | TO |  |  | TO
PRC-006-1(i) | Automatic Underfrequency Load Shedding | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for application determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | TO |  |  | TO
PRC-006-2 | Automatic Underfrequency Load Shedding | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | TO |  |  | TO
PRC-006-2 | Automatic Underfrequency Load Shedding | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | TO |  |  | TO
PRC-006-2 | Automatic Underfrequency Load Shedding | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | TO |  |  | TO
PRC-006-3 | Automatic Underfrequency Load Shedding | R8. | Each UFLS entity shall provide data to its Planning Coordinator(s) according to the format and schedule specified by the Planning Coordinator(s) to support maintenance of each Planning Coordinator’s UFLS database. | TO |  |  | TO
PRC-006-3 | Automatic Underfrequency Load Shedding | R9. | Each UFLS entity shall provide automatic tripping of Load in accordance with the UFLS program design and schedule for implementation, including any Corrective Action Plan, as determined by its Planning Coordinator(s) in each Planning Coordinator area in which it owns assets. | TO |  |  | TO
PRC-006-3 | Automatic Underfrequency Load Shedding | R10. | Each Transmission Owner shall provide automatic switching of its existing capacitor banks, Transmission Lines, and reactors to control over-voltage as a result of underfrequency load shedding if required by the UFLS program and schedule for implementation, including any Corrective Action Plan, as determined by the Planning Coordinator(s) in each Planning Coordinator area in which the Transmission Owner owns transmission. | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R10. | Each Distribution Provider and Transmission Owner shall implement the inhibit threshold settings based on the notification provided by the Planning Coordinator in accordance with Requirement R9. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R19.3. | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R16.3. | Have compensatory load shedding, as provided by a Distribution Provider or Transmission Owner that is adequate to compensate for the loss of their generator due to early tripping. | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R22. | Each Distribution Provider, Transmission Owner and Generator Owner shall implement the load distribution changes based on the notification provided by the Planning Coordinator in accordance with Requirement R21. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | TO, GO | GO |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R23. | Each Distribution Provider, Transmission Owner and Generator Owner shall develop and submit an implementation plan within 90 days of the request from the Planning Coordinator for approval by the Planning Coordinator in accordance with Requirement R21. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R16.2. | Transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator. | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R16.1. | Set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations. | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R16. | Each Generator Owner of existing non-nuclear units in service prior to the effective date of this standard that have underfrequency protections set to trip above the appropriate curve in Figure 1 shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R15.2. | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1. | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R15.1. | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 1. | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R15. | Each Generator Owner with a new generating unit, scheduled to be in service on or after the effective date of this Standard, or an existing generator increasing its net capability by greater than 10% shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R14. | Each Generator Owner shall transmit the generator underfrequency trip setting and time delay to its Planning Coordinator within 45 days of the Planning Coordinator’s request. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R13. | Each Generator Owner shall set each generator underfrequency trip relay, if so equipped, below the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, except as otherwise exempted in Requirements R16 and R19. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R12. | Each Transmission Owner and Distribution Provider shall annually provide documentation, with no more than 15 months between updates, to its Planning Coordinator of the actual net Load that would have been shed by the UFLS relays at each UFLS stage coincident with their integrated hourly peak net Load during the previous year, as determined by measuring actual metered Load through the switches that would be opened by the UFLS relays. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R5. | Each Distribution Provider or Transmission Owner that must arm its load to trip on underfrequency in order to meet its requirements as specified and by doing so exceeds the tolerances and/or deviates from the number of stages and frequency set points of the UFLS program as specified in the tables contained in Requirement R4 above, as applicable depending on its total peak net Load shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R7.2. | Québec Interconnection – 200 ms [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R19. | Each Generator Owner of existing nuclear generating plants with units that have underfrequency relay threshold settings above the Eastern Interconnection generator tripping curve in Figure 1, based on their licensing design basis, shall: [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R18. | Each Generator Owner, Distribution Provider or Transmission Owner within the Planning Coordinator area of ISO-NE or the New York ISO shall apply the criteria described in Attachment B to determine the compensatory load shedding that is required in Requirement R16.3 for generating units in its respective NPCC area. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | TO, GO | GO |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R19.1. | Set the underfrequency protection to operate at as low a frequency as possible in accordance with the plant design and licensing limitations but not greater than 57.8Hz. | GO | GO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R4. | Each Distribution Provider and Transmission Owner in the Eastern Interconnection portion of NPCC shall implement an automatic UFLS program reflecting normal operating conditions excluding outages for its Facilities based on frequency thresholds, total nominal operating time and amounts specified in Attachment C, Tables 1 through 3, or shall collectively implement by mutual agreement with one or more Distribution Providers and Transmission Owners within the same island identified in Requirement R1 and acting as a single entity, provide an aggregated automatic UFLS program that sheds their coincident peak aggregated net Load, based on frequency thresholds, total nominal operating time and amounts specified in Attachment C, Tables 1 through 3. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R5.1. | Inform its Planning Coordinator of the need to exceed the stated tolerances or the number of stages as shown in UFLS Attachment C, Table 1 if applicable and | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R5.2. | Provide its Planning Coordinator with a technical study that demonstrates that the Distribution Providers or Transmission Owners specific deviations from the requirements of UFLS Attachment C, Table 1 will not have a significant adverse impact on the bulk power system. | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R5.3. | Inform its Planning Coordinator of the need to exceed the stated tolerances of UFLS Attachment C, Table 2 or Table 3, and in the case of Attachment C, Table 2 only, the need to deviate from providing two stages of UFLS, if applicable, and | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R5.4. | Provide its Planning Coordinator with an analysis demonstrating that no alternative load shedding solution is available that would allow the Distribution Provider or Transmission Owner to comply with UFLS Attachment C Table 2 or Attachment C Table 3. | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R6. | Each Distribution Provider and Transmission Owner in the Québec Interconnection portion of NPCC shall implement an automatic UFLS program for its Facilities based on the frequency thresholds, slopes, total nominal operating time and amounts specified in Attachment C, Table 4 or shall collectively implement by mutual agreement with one or more Distribution Providers and Transmission Owners within the same island, identified in Requirement R1, an aggregated automatic UFLS program that sheds Load based on the frequency thresholds, slopes, total nominal operating time and amounts specified in Attachment C, Table 4. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R7. | Each Distribution Provider and Transmission Owner shall set each underfrequency relay that is part of its region’s UFLS program with the following minimum time delay: | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R7.1. | Eastern Interconnection – 100 ms | TO |  |  | TO
PRC-006-NPCC-1 | Automatic Underfrequency Load Shedding | R19.2. | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. | GO | GO
PRC-008-0 | Implementation and Documentation of Underfrequency Load Shedding Equipment Maintenance Program | R2. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall implement its UFLS equipment maintenance and testing program and shall provide UFLS maintenance and testing program results to its Regional Reliability Organization and NERC on request (within 30 calendar days). | TO |  |  | TO
PRC-008-0 | Implementation and Documentation of Underfrequency Load Shedding Equipment Maintenance Program | R1. | The Transmission Owner and Distribution Provider with a UFLS program (as required by its Regional Reliability Organization) shall have a UFLS equipment maintenance and testing program in place. This UFLS equipment maintenance and testing program shall include UFLS equipment identification, the schedule for UFLS equipment testing, and the schedule for UFLS equipment maintenance. | TO |  |  | TO
PRC-010-0 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | R1.1.2. | Simulations that demonstrate that the UVLS programs performance is consistent with Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0 and TPL-004-0. | TO |  |  | TO
PRC-010-0 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | R1.1.3. | A review of the voltage set points and timing. | TO |  |  | TO
PRC-010-0 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | R1.1.1. | Coordination of the UVLS programs with other protection and control systems in the Region and with other Regional Reliability Organizations, as appropriate. | TO |  |  | TO
PRC-010-0 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | R1. | The Load-Serving Entity, Transmission Owner, Transmission Operator, and Distribution Provider that owns or operates a UVLS program shall periodically (at least every five years or as required by changes in system conditions) conduct and document an assessment of the effectiveness of the UVLS program. This assessment shall be conducted with the associated Transmission Planner(s) and Planning Authority(ies). | TO |  |  | TO
PRC-010-0 | Technical Assessment of the Design and Effectiveness of Undervoltage Load Shedding Program | R1.1. | This assessment shall include, but is not limited to: | TO |  |  | TO
PRC-010-1 | Undervoltage Load Shedding | R2. | Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] | TO |  |  | TO
PRC-010-1 | Undervoltage Load Shedding | R7. | Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO |  |  | TO
PRC-010-2 | Undervoltage Load Shedding | R2. | Each UVLS entity shall adhere to the UVLS Program specifications and implementation schedule determined by its Planning Coordinator or Transmission Planner associated with UVLS Program development per Requirement R1 or with any Corrective Action Plans per Requirement R5. [Violation Risk Factor: High] [Time Horizon: Long‐term Planning] | TO |  |  | TO
PRC-010-2 | Undervoltage Load Shedding | R7. | Each UVLS entity shall provide data to its Planning Coordinator according to the format and schedule specified by the Planning Coordinator to support maintenance of a UVLS Program database. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.2. | Documentation of maintenance and testing intervals and their basis. | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R2. | The Transmission Owner and Distribution Provider that owns a UVLS system shall provide documentation of its UVLS equipment maintenance and testing program and the implementation of that UVLS equipment maintenance and testing program to its Regional Reliability Organization and NERC on request (within 30 calendar days). | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.5. | Schedule for system maintenance. | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.4. | Schedule for system testing. | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.3. | Summary of testing procedure. | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.1.3. | Communications systems, where appropriate. | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.1.2. | Instrument transformers. | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.1.1. | Relays. | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.1. | The UVLS system identification which shall include but is not limited to: | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1. | The Transmission Owner and Distribution Provider that owns a UVLS system shall have a UVLS equipment maintenance and testing program in place. This program shall include: | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.6. | Date last tested/maintained. | TO |  |  | TO
PRC-011-0 | Undervoltage Load Shedding System Maintenance and Testing | R1.1.4. | Batteries. | TO |  |  | TO
PRC-012-2 | Remedial Action Schemes | R7.3. | Notify each reviewing Reliability Coordinator if CAP actions or timetables change. | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R8. | At least once every six‐calendar years, each RAS‐owner shall perform a functional test of each RAS to verify the overall RAS performance and the proper operation of non-Protection-System Components | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R7.2. | Update the CAP if actions or timetables change. | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R7.1. | Implement the CAP. | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R7. | For each CAP submitted pursuant to Requirement R6, each RAS‐owner shall: | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R6. | Within six‐full‐calendar months of being notified of a deficiency in its RAS pursuant to Requirement R4 or Requirement R5, each RAS‐owner shall participate in developing a Corrective Action Plan (CAP) and submit the CAP to its reviewing Reliability Coordinator(s). | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R5.3. | The RAS was effective in mitigating BES performance issues it was designed to address. | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R5.2. | The RAS responded as designed. | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R5.1. | The System events and/or conditions appropriately triggered the RAS. | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R5. | Each RAS‐owner shall, within 120‐calendar days of a RAS operation or failure of a RAS to operate when expected, analyze the RAS performance and provide the results of the analysis, including any identified deficiencies, to its reviewing Reliability Coordinator(s). The RAS operational performance analysis shall determine whether: | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R3. | Following the review performed pursuant to Requirement R2, the RAS‐entity shall address each identified issue and obtain approval from each reviewing Reliability Coordinator prior to placing a new or functionally modified RAS in service or retiring an existing RAS. | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R1. | Prior to placing a new or functionally modified RAS in‐service or retiring an existing RAS, each RAS‐entity shall submit the information identified in Attachment 1 to the reviewing Reliability Coordinator(s). | TO, GO | GO |  | TO
PRC-012-2 | Remedial Action Schemes | R5.4. | The RAS operation resulted in any unintended or adverse BES response. | TO, GO | GO |  | TO
PRC-015-0 | Special Protection System Data and Documentation | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have evidence it reviewed new or functionally modified SPSs in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-0_R1 prior to being placed in service. | TO, GO | GO |  | TO
PRC-015-0 | Special Protection System Data and Documentation | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of SPS data and the results of studies that show compliance of new or functionally modified SPSs with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | TO, GO | GO |  | TO
PRC-015-0 | Special Protection System Data and Documentation | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall maintain a list of and provide data for existing and proposed SPSs as specified in Reliability Standard PRC-013-0_R 1. | TO, GO | GO |  | TO
PRC-015-1 | Remedial Action Scheme Data and Documentation | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of RAS data and the results of Studies that show compliance of new or functionally modified RAS with NERC Reliability Standards and Regional Reliability Organization criteria to affected Regional Reliability Organizations and NERC on request (within 30 calendar days). | TO, GO | GO |  | TO
PRC-015-1 | Remedial Action Scheme Data and Documentation | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall maintain a list of and provide data for existing and proposed RAS as specified in Reliability Standard PRC-013-1 R1. | TO, GO | GO |  | TO
PRC-015-1 | Remedial Action Scheme Data and Documentation | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have evidence it reviewed new or functionally modified RAS in accordance with the Regional Reliability Organization’s procedures as defined in Reliability Standard PRC-012-1_R1 prior to being placed in service. | TO, GO | GO |  | TO
PRC-016-0.1 | Special Protection System Misoperations | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | TO, GO | GO |  | TO
PRC-016-0.1 | Special Protection System Misoperations | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall analyze its SPS operations and maintain a record of all misoperations in accordance with the Regional SPS review procedure specified in Reliability Standard PRC-012-0_R1. | TO, GO | GO |  | TO
PRC-016-0.1 | Special Protection System Misoperations | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall take corrective actions to avoid future misoperations. | TO, GO | GO |  | TO
PRC-016-1 | Remedial Action Scheme Misoperations | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall analyze its RAS operations and maintain a record of all misoperations in accordance with the Regional RAS review procedure specified in Reliability Standard PRC-012-1_R1. | TO, GO | GO |  | TO
PRC-016-1 | Remedial Action Scheme Misoperations | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall take corrective actions to avoid future misoperations. | TO, GO | GO |  | TO
PRC-016-1 | Remedial Action Scheme Misoperations | R3. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of the misoperation analyses and the corrective action plans to its Regional Reliability Organization and NERC on request (within 90 calendar days). | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1.6. | Date last tested/maintained. | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1.5. | Schedule for system maintenance. | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1.4. | Schedule for system testing. | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1.1.4. | Batteries. | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1.1.3. | Communications systems, where appropriate. | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1.1.2. | Instrument transformers. | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1.1.1. | Relays. | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1.1. | SPS identification shall include but is not limited to: | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns an SPS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1.2. | Documentation of maintenance and testing intervals and their basis. | TO, GO | GO |  | TO
PRC-017-0 | Special Protection System Maintenance and Testing | R1.3. | Summary of testing procedure. | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.2. | Documentation of maintenance and testing intervals and their basis. | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R2. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall provide documentation of the program and its implementation to the appropriate Regional Reliability Organizations and NERC on request (within 30 calendar days). | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.6. | Date last tested/maintained. | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.5. | Schedule for system maintenance. | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.3. | Summary of testing procedure. | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.1.4. | Batteries. | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.1.3. | Communications systems, where appropriate. | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.1.2. | Instrument transformers. | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.1.1. | Relays. | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.1. | RAS identification shall include but is not limited to: | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1. | The Transmission Owner, Generator Owner, and Distribution Provider that owns a RAS shall have a system maintenance and testing program(s) in place. The program(s) shall include: | TO, GO | GO |  | TO
PRC-017-1 | Remedial Action Scheme Maintenance and Testing | R1.4. | Schedule for system testing. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.5. | Date last tested. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.6. | Monitored elements, such as transmission circuit, bus section, etc. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R6.2. | Summary of maintenance and testing procedures. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R6.1. | Maintenance and testing intervals and their basis. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R6. | Each Transmission Owner and Generator Owner that is required by its Regional Reliability Organization to have DMEs shall have a maintenance and testing program for those DMEs that includes: | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R5. | The Transmission Owner and Generator Owner shall each archive all data recorded by DMEs for Regional Reliability Organization-identified events for at least three years. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R4. | The Transmission Owner and Generator Owner shall each provide Disturbance data (recorded by DMEs) in accordance with its Regional Reliability Organization’s requirements (reliability standard PRC-002 Requirement 4). | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.8. | Monitored electrical quantities, such as voltage, current, etc. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R2. | The Transmission Owner and Generator Owner shall each install DMEs in accordance with its Regional Reliability Organization’s installation requirements (reliability standard PRC-002 Requirements 1 through 3). | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R1.1. | Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.7. | Monitored devices, such as circuit breaker, disconnect status, alarms, etc. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R1.2. | Recorded data from each Disturbance shall be retrievable for ten calendar days.. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3. | The Transmission Owner and Generator Owner shall each maintain, and report to its Regional Reliability Organization on request, the following data on the DMEs installed to meet that region’s installation requirements (reliability standard PRC-002 Requirements1.1, 2.1 and 3.1): | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.1. | Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.2. | Make and model of equipment. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.3. | Installation location. | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R1. | Each Transmission Owner and Generator Owner required to install DMEs by its Regional Reliability Organization (reliability standard PRC-002 Requirements 1-3) shall have DMEs installed that meet the following requirements: | TO, GO | GO |  | TO
PRC-018-1 | Disturbance Monitoring Equipment Installation and Data Reporting | R3.4. | Operational status. | TO, GO | GO |  | TO
PRC-019-1 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1. | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: | TO, GO | GO |  | TO
PRC-019-1 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1.1. | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. | TO, GO | GO |  | TO
PRC-019-1 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1.2. | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | TO, GO | GO |  | TO
PRC-019-1 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R2. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning]:  Voltage regulating settings or equipment changes;  Protection System settings or component changes;  Generating or synchronous condenser equipment capability changes; or  Generator or synchronous condenser step-up transformer changes. | TO, GO | GO |  | TO
PRC-019-1 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1. | At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service1 limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
PRC-019-2 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1. | At a maximum of every five calendar years, each Generator Owner and Transmission Owner with applicable Facilities shall coordinate the voltage regulating system controls, (including in-service1 limiters and protection functions) with the applicable equipment capabilities and settings of the applicable Protection System devices and functions. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
PRC-019-2 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R2. | Within 90 calendar days following the identification or implementation of systems, equipment or setting changes that will affect the coordination described in Requirement R1, each Generator Owner and Transmission Owner with applicable Facilities shall perform the coordination as described in Requirement R1. These possible systems, equipment or settings changes include, but are not limited to the following [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning]: • Voltage regulating settings or equipment changes; • Protection System settings or component changes; • Generating or synchronous condenser equipment capability changes; or • Generator or synchronous condenser step-up transformer changes. | TO, GO | GO |  | TO
PRC-019-2 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1.2. | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. | TO, GO | GO |  | TO
PRC-019-2 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1. | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: | TO, GO | GO |  | TO
PRC-019-2 | Coordination of Generating Unit or Plant Capabilities, Voltage Regulating Controls, and Protection | R1.1.1. | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. | TO, GO | GO |  | TO
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1. | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: | TO |  |  | TO
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1.1. | Size and location of customer load, or percent of connected load, to be interrupted. | TO |  |  | TO
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1.2. | Corresponding voltage set points and overall scheme clearing times. | TO |  |  | TO
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1.3. | Time delay from initiation to trip signal. | TO |  |  | TO
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1.4. | Breaker operating times. | TO |  |  | TO
PRC-021-1 | Under-Voltage Load Shedding Program Data | R1.5. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. | TO |  |  | TO
PRC-021-1 | Under-Voltage Load Shedding Program Data | R2. | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. | TO |  |  | TO
PRC-021-2 | Under-Voltage Load Shedding Program Data | R2. | Each Transmission Owner and Distribution Provider that owns a UVLS program shall provide its UVLS program data to the Regional Reliability Organization within 30 calendar days of a request. | TO |  |  | TO
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1.4. | Breaker operating times. | TO |  |  | TO
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1.5. | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. | TO |  |  | TO
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1.2. | Corresponding voltage set points and overall scheme clearing times. | TO |  |  | TO
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1. | Each Transmission Owner and Distribution Provider that owns a UVLS program to mitigate the risk of voltage collapse or voltage instability in the BES shall annually update its UVLS data to support the Regional UVLS program database. The following data shall be provided to the Regional Reliability Organization for each installed UVLS system: | TO |  |  | TO
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1.1. | Size and location of customer load, or percent of connected load, to be interrupted. | TO |  |  | TO
PRC-021-2 | Under-Voltage Load Shedding Program Data | R1.3. | Time delay from initiation to trip signal. | TO |  |  | TO
PRC-023-2(i) | Transmission Relay Loadability | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. | TO, GO | GO |  | TO
PRC-023-2(i) | Transmission Relay Loadability | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. (see standard for list of criteria. | TO, GO | GO |  | TO
PRC-023-2(i) | Transmission Relay Loadability | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. | TO, GO | GO |  | TO
PRC-023-2(i) | Transmission Relay Loadability | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 6, 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. | TO, GO | GO |  | TO
PRC-023-2(i) | Transmission Relay Loadability | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. | TO, GO | GO |  | TO
PRC-023-3 | Transmission Relay Loadability | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | TO, GO | GO |  | TO
PRC-023-3 | Transmission Relay Loadability | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | TO, GO | GO |  | TO
PRC-023-3 | Transmission Relay Loadability | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. [Violation Risk Factor: High] [Time Horizon: Long Term Planning]. See detailed Criteria in the standard. | TO, GO | GO |  | TO
PRC-023-3 | Transmission Relay Loadability | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | TO, GO | GO |  | TO
PRC-023-3 | Transmission Relay Loadability | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | TO, GO | GO |  | TO
PRC-023-4 | Transmission Relay Loadability | R4. | Each Transmission Owner, Generator Owner, and Distribution Provider that chooses to use Requirement R1 criterion 2 as the basis for verifying transmission line relay loadability shall provide its Planning Coordinator, Transmission Operator, and Reliability Coordinator with an updated list of circuits associated with those transmission line relays at least once each calendar year, with no more than 15 months between reports. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | TO, GO | GO |  | TO
PRC-023-4 | Transmission Relay Loadability | R5. | Each Transmission Owner, Generator Owner, and Distribution Provider that sets transmission line relays according to Requirement R1 criterion 12 shall provide an updated list of the circuits associated with those relays to its Regional Entity at least once each calendar year, with no more than 15 months between reports, to allow the ERO to compile a list of all circuits that have protective relay settings that limit circuit capability. [Violation Risk Factor: Lower] [Time Horizon: Long Term Planning] | TO, GO | GO |  | TO
PRC-023-4 | Transmission Relay Loadability | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider that uses a circuit capability with the practical limitations described in Requirement R1, criterion 7, 8, 9, 12, or 13 shall use the calculated circuit capability as the Facility Rating of the circuit and shall obtain the agreement of the Planning Coordinator, Transmission Operator, and Reliability Coordinator with the calculated circuit capability. [Violation Risk Factor: Medium] [Time Horizon: Long Term Planning] | TO, GO | GO |  | TO
PRC-023-4 | Transmission Relay Loadability | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall use any one of the following criteria (Requirement R1, criteria 1 through 13) for any specific circuit terminal to prevent its phase protective relay settings from limiting transmission system loadability while maintaining reliable protection of the BES for all fault conditions. Each Transmission Owner, Generator Owner, and Distribution Provider shall evaluate relay loadability at 0.85 per unit voltage and a power factor angle of 30 degrees. [Violation Risk Factor: High] [Time Horizon: Long Term Planning]. See detailed Criteria in the standard. | TO, GO | GO |  | TO
PRC-023-4 | Transmission Relay Loadability | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall set its out-of-step blocking elements to allow tripping of phase protective relays for faults that occur during the loading conditions used to verify transmission line relay loadability per Requirement R1. [Violation Risk Factor: High] [Time Horizon: Long Term Planning] | TO, GO | GO |  | TO
PRC-024-1 | Generator Frequency and Voltage Protective Relay Settings | R1. | Each Generator Owner that has generator frequency protective relaying1 • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | GO | GO
PRC-024-1 | Generator Frequency and Voltage Protective Relay Settings | R2. | Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection2 • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). ) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2. If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | GO | GO
PRC-024-1 | Generator Frequency and Voltage Protective Relay Settings | R3. | Each Generator Owner shall document each known regulatory or equipment limitation that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | GO | GO
PRC-024-1 | Generator Frequency and Voltage Protective Relay Settings | R3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | GO | GO
PRC-024-1 | Generator Frequency and Voltage Protective Relay Settings | R4. | Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | GO | GO
PRC-024-2 | Generator Frequency and Voltage Protective Relay Settings | R1. | Each Generator Owner that has generator frequency protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator frequency protective relaying does not trip the applicable generating unit(s) within the “no trip zone” of PRC-024 Attachment 1, subject to the following exceptions:2 [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip if the protective functions (such as out-of-step functions or loss-of-field functions) operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 1 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | GO | GO
PRC-024-2 | Generator Frequency and Voltage Protective Relay Settings | R4. | Each Generator Owner shall provide its applicable generator protection trip settings associated with Requirements R1 and R2 to the Planning Coordinator or Transmission Planner that models the associated unit within 60 calendar days of receipt of a written request for the data and within 60 calendar days of any change to those previously requested trip settings unless directed by the requesting Planning Coordinator or Transmission Planner that the reporting of relay setting changes is not required. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | GO | GO
PRC-024-2 | Generator Frequency and Voltage Protective Relay Settings | R2. | Each Generator Owner that has generator voltage protective relaying1 activated to trip its applicable generating unit(s) shall set its protective relaying such that the generator voltage protective relaying does not trip the applicable generating unit(s) as a result of a voltage excursion (at the point of interconnection3) caused by an event on the transmission system external to the generating plant that remains within the “no trip zone” of PRC-024 Attachment 2.4 If the Transmission Planner allows less stringent voltage relay settings than those required to meet PRC-024 Attachment 2, then the Generator Owner shall set its protective relaying within the voltage recovery characteristics of a location-specific Transmission Planner’s study. Requirement R2 is subject to the following exceptions: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] • Generating unit(s) may trip in accordance with a Special Protection System (SPS) or Remedial Action Scheme (RAS). • Generating unit(s) may trip if clearing a system fault necessitates disconnecting (a) generating unit(s). • Generating unit(s) may trip by action of protective functions (such as out-of-step functions or loss-of-field functions) that operate due to an impending or actual loss of synchronism or, for asynchronous generating units, due to instability in power conversion control equipment. • Generating unit(s) may trip within a portion of the “no trip zone” of PRC-024 Attachment 2 for documented and communicated regulatory or equipment limitations in accordance with Requirement R3. | GO | GO
PRC-024-2 | Generator Frequency and Voltage Protective Relay Settings | R3. | Each Generator Owner shall document each known regulatory or equipment limitation, that prevents an applicable generating unit with generator frequency or voltage protective relays from meeting the relay setting criteria in Requirements R1 or R2 including (but not limited to) study results, experience from an actual event, or manufacturer’s advice. [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | GO | GO
PRC-024-2 | Generator Frequency and Voltage Protective Relay Settings | R3.1. | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following: • Identification of a regulatory or equipment limitation. • Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation. • Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. | GO | GO
PRC-025-1 | Generator Relay Loadability | R1. | Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-1 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. [Violation Risk Factor: High] [Time Horizon: Long-Term Planning] | TO, GO | GO |  | TO
PRC-025-2 | Generator Relay Loadability | R1. | Each Generator Owner, Transmission Owner, and Distribution Provider shall apply settings that are in accordance with PRC-025-2 – Attachment 1: Relay Settings, on each load-responsive protective relay while maintaining reliable fault protection. [Violation Risk Factor: High] [Time Horizon: Long-Term Planning] | TO, GO | GO |  | TO
PRC-026-1 | Relay Performance During Stable Power Swings | R2.2. | Within 12 full calendar months of becoming aware4 of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable5 power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. | TO, GO | GO |  | TO
PRC-026-1 | Relay Performance During Stable Power Swings | R3. | Each Generator Owner and Transmission Owner shall, within six full calendar months of determining a load-responsive protective relay does not meet the PRC-026-1 – Attachment B criteria pursuant to Requirement R2, develop a Corrective Action Plan (CAP) to meet one of the following: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning] • The Protection System meets the PRC-026-1 – Attachment B criteria, while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element); or • The Protection System is excluded under the PRC-026-1 – Attachment A criteria (e.g., modifying the Protection System so that relay functions are supervised by power swing blocking or using relay systems that are immune to power swings), while maintaining dependable fault detection and dependable out-of-step tripping (if out-of-step tripping is applied at the terminal of the BES Element). | TO, GO | GO |  | TO
PRC-026-1 | Relay Performance During Stable Power Swings | R2.1. | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. | TO, GO | GO |  | TO
PRC-026-1 | Relay Performance During Stable Power Swings | R2. | Each Generator Owner and Transmission Owner shall: [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-026-1 | Relay Performance During Stable Power Swings | R1. | Each Planning Coordinator shall, at least once each calendar year, provide notification of each generator, transformer, and transmission line BES Element in its area that meets one or more of the following criteria, if any, to the respective Generator Owner and Transmission Owner: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] Criteria: 1. Generator(s) where an angular stability constraint exists that is addressed by a System Operating Limit (SOL) or a Remedial Action Scheme (RAS) and those Elements terminating at the Transmission station associated with the generator(s). 2. An Element that is monitored as part of an SOL identified by the Planning Coordinator’s methodology1 based on an angular stability constraint. 3. An Element that forms the boundary of an island in the most recent underfrequency load shedding (UFLS) design assessment based on application of the Planning Coordinator’s criteria for identifying islands, only if the island is formed by tripping the Element due to angular instability. 4. An Element identified in the most recent annual Planning Assessment where relay tripping occurs due to a stable or unstable2 power swing during a simulated disturbance. | TO, GO | GO |  | TO
PRC-026-1 | Relay Performance During Stable Power Swings | R4. | Each Generator Owner and Transmission Owner shall implement each CAP developed pursuant to Requirement R3 and update each CAP if actions or timetables change until all actions are complete. [Violation Risk Factor: Medium][Time Horizon: Long-Term Planning] | TO, GO | GO |  | TO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1. | Each Transmission Owner, Generator Owner, and Distribution Provider shall establish a process for developing new and revised Protection System settings for BES Elements, such that the Protection Systems operate in the intended sequence during Faults. The process shall include: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.3.3. | Verify that identified coordination issue(s) associated with the proposed Protection System settings for the associated BES Elements are addressed prior to implementation. | TO, GO | GO |  | TO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R3. | Each Transmission Owner, Generator Owner, and Distribution Provider shall utilize its process established in Requirement R1 to develop new and revised Protection System settings for BES Elements. [Violation Risk Factor: High] [Time Horizon: Operations Planning] | TO, GO | GO |  | TO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R2. | Each Transmission Owner, Generator Owner, and Distribution Provider shall, for each BES Element with Protection System functions identified in Attachment A: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] ● Option 1: Perform a Protection System Coordination Study in a time interval not to exceed six-calendar years; or ● Option 2: Compare present Fault current values to an established Fault current baseline and perform a Protection System Coordination Study when the comparison identifies a 15 percent or greater deviation in Fault current values (either three phase or phase to ground) at a bus to which the BES Element is connected, all in a time interval not to exceed six-calendar years;1 or, ● Option 3: Use a combination of the above. | TO, GO | GO |  | TO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.3.4. | Communicate with the other owner(s) of the electrically joined Facilities regarding revised Protection System settings resulting from unforeseen circumstances that arise during implementation or commissioning, Misoperation investigations, maintenance activities, or emergency replacements required as a result of Protection System component failure. | TO, GO | GO |  | TO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.3.2. | Respond to any owner(s) that provided its proposed Protection System settings pursuant to Requirement R1, Part 1.3.1 by identifying any coordination issue(s) or affirming that no coordination issue(s) were identified. | TO, GO | GO |  | TO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.3.1. | Provide the proposed Protection System settings to the owner(s) of the electrically joined Facilities. | TO, GO | GO |  | TO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.3. | For Protection System settings applied on BES Elements that electrically join Facilities owned by separate functional entities (Transmission Owners, Generator Owners, and Distribution Providers), provisions to: | TO, GO | GO |  | TO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.1. | A review and update of short-circuit model data for the BES Elements under study. | TO, GO | GO |  | TO
PRC-027-1 | Coordination of Protection Systems for Performance During Faults | R1.2. | A review of the developed Protection System settings. | TO, GO | GO |  | TO
TOP-001-1a | Reliability Responsibilities and Authorities | R3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall comply with reliability directives issued by the Reliability Coordinator, and each Balancing Authority and Generator Operator shall comply with reliability directives issued by the Transmission Operator, unless such actions would violate safety, equipment, regulatory or statutory requirements. Under these circumstances the Transmission Operator, Balancing Authority, or Generator Operator shall immediately inform the Reliability Coordinator or Transmission Operator of the inability to perform the directive so that the Reliability Coordinator or Transmission Operator can implement alternate remedial actions. | GOP |  | GOP
TOP-001-1a | Reliability Responsibilities and Authorities | R7.3. | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. | GOP |  | GOP
TOP-001-1a | Reliability Responsibilities and Authorities | R6. | Each Transmission Operator, Balancing Authority, and Generator Operator shall render all available emergency assistance to others as requested, provided that the requesting entity has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. | GOP |  | GOP
TOP-001-1a | Reliability Responsibilities and Authorities | R7. | Each Transmission Operator and Generator Operator shall not remove Bulk Electric System facilities from service if removing those facilities would burden neighboring systems unless: | GOP |  | GOP
TOP-001-1a | Reliability Responsibilities and Authorities | R7.1. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. | GOP |  | GOP
TOP-001-2 | Transmission Operations | R1. | Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall comply with each Reliability Directive issued and identified as such by its Transmission Operator(s), unless such action would violate safety, equipment, regulatory, or statutory requirements. | GOP |  | GOP
TOP-001-2 | Transmission Operations | R2. | Each Balancing Authority, Generator Operator, Distribution Provider, and Load-Serving Entity shall inform its Transmission Operator of its inability to perform an identified Reliability Directive issued by that Transmission Operator. | GOP |  | GOP
TOP-001-2 | Transmission Operations | R7.1. | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. | GOP |  | GOP
TOP-001-3 | Transmission Operations | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. [Violation Risk Factor: High] [Time Horizon: Same- Day Operations, Real-Time Operations] | GOP |  | GOP
TOP-001-3 | Transmission Operations | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | GOP |  | GOP
TOP-001-3 | Transmission Operations | R4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | GOP |  | GOP
TOP-001-3 | Transmission Operations | R5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | GOP |  | GOP
TOP-001-4 | Transmission Operations | R6. | Each Transmission Operator, Generator Operator, and Distribution Provider shall inform its Balancing Authority of its inability to comply with an Operating Instruction issued by its Balancing Authority. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | GOP |  | GOP
TOP-001-4 | Transmission Operations | R5. | Each Transmission Operator, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Balancing Authority, unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | GOP |  | GOP
TOP-001-4 | Transmission Operations | R3. | Each Balancing Authority, Generator Operator, and Distribution Provider shall comply with each Operating Instruction issued by its Transmission Operator(s), unless such action cannot be physically implemented or it would violate safety, equipment, regulatory, or statutory requirements. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | GOP |  | GOP
TOP-001-4 | Transmission Operations | R4. | Each Balancing Authority, Generator Operator, and Distribution Provider shall inform its Transmission Operator of its inability to comply with an Operating Instruction issued by its Transmission Operator. [Violation Risk Factor: High] [Time Horizon: Same-Day Operations, Real-Time Operations] | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R14. | Generator Operators shall, without any intentional time delay, notify their Balancing Authority and Transmission Operator of changes in capabilities and characteristics including but not limited to: | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R15. | Generation Operators shall, at the request of the Balancing Authority or Transmission Operator, provide a forecast of expected real power output to assist in operations planning (e.g., a seven-day forecast of real output). | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R14.1. | Changes in real output capabilities. | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R3. | Each Load Serving Entity and Generator Operator shall coordinate (where confidentiality agreements allow) its current-day, next-day, and seasonal operations with its Host Balancing Authority and Transmission Service Provider. Each Balancing Authority and Transmission Service Provider shall coordinate its current-day, next-day, and seasonal operations with its Transmission Operator. | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R18. | Neighboring Balancing Authorities, Transmission Operators, Generator Operators, Transmission Service Providers and Load Serving Entities shall use uniform line identifiers when referring to transmission facilities of an interconnected network. | GOP |  | GOP
TOP-002-2.1b | Normal Operations Planning | R13. | At the request of the Balancing Authority or Transmission Operator, a Generator Operator shall perform generating real and reactive capability verification that shall include, among other variables, weather, ambient air and water conditions, and fuel quality and quantity, and provide the results to the Balancing Authority or Transmission Operator operating personnel as requested. | GOP |  | GOP
TOP-003-1 | Planned Outage Coordination | R1.1. | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. | GOP |  | GOP
TOP-003-1 | Planned Outage Coordination | R2. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of system voltage regulating equipment, such as automatic voltage regulators on generators, supplementary excitation control, synchronous condensers, shunt and series capacitors, reactors, etc., among affected Balancing Authorities and Transmission Operators as required. | GOP |  | GOP
TOP-003-1 | Planned Outage Coordination | R1. | Generator Operators and Transmission Operators shall provide planned outage information. | GOP |  | GOP
TOP-003-1 | Planned Outage Coordination | R3. | Each Transmission Operator, Balancing Authority, and Generator Operator shall plan and coordinate scheduled outages of telemetering and control equipment and associated communication channels between the affected areas. | GOP |  | GOP
TOP-003-2 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications for data. | TO, GOP, GO | GO | GOP | TO
TOP-003-2 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Interchange Authority, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications for data. | TO, GOP, GO | GO | GOP | TO
TOP-003-3 | Operational Reliability Data | R5.2. | A mutually agreeable process for resolving data conflicts | TO, GOP, GO | GO | GOP | TO
TOP-003-3 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | TO, GOP, GO | GO | GOP | TO
TOP-003-3 | Operational Reliability Data | R5.3. | A mutually agreeable security protocol | TO, GOP, GO | GO | GOP | TO
TOP-003-3 | Operational Reliability Data | R5.3. | A mutually agreeable security protocol | TO, GOP, GO | GO | GOP | TO
TOP-003-3 | Operational Reliability Data | R5.2. | A mutually agreeable process for resolving data conflicts | TO, GOP, GO | GO | GOP | TO
TOP-003-3 | Operational Reliability Data | R5.1. | A mutually agreeable format | TO, GOP, GO | GO | GOP | TO
TOP-003-3 | Operational Reliability Data | R5. | Each Transmission Operator, Balancing Authority, Generator Owner, Generator Operator, Load-Serving Entity, Transmission Owner, and Distribution Provider receiving a data specification in Requirement R3 or R4 shall satisfy the obligations of the documented specifications using: [Violation Risk Factor: Medium] [Time Horizon: Operations Planning, Same-Day Operations, Real-time Operations] | TO, GOP, GO | GO | GOP | TO
TOP-003-3 | Operational Reliability Data | R5.1. | A mutually agreeable format | TO, GOP, GO | GO | GOP | TO
TOP-006-2 | Monitoring System Conditions | R1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. | GOP |  | GOP
TOP-006-3 | Monitoring System Conditions | R1.1. | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | GOP |  | GOP
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6. | Each Transmission Owner and Generator Owner shall conduct a thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The thermal impact assessment shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | TO, GO | GO |  | TO
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | TO, GO | GO |  | TO
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.2. | Document assumptions used in the analysis; | TO, GO | GO |  | TO
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.1. | Be based on the effective GIC flow information provided in Requirement R5; | TO, GO | GO |  | TO
TPL-007-1 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | TO, GO | GO |  | TO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.2. | Document assumptions used in the analysis; | TO, GO | GO |  | TO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | TO, GO | GO |  | TO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | TO, GO | GO |  | TO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.2. | Document assumptions used in the analysis; | TO, GO | GO |  | TO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10.1. | Be based on the effective GIC flow information provided in Requirement R9; | TO, GO | GO |  | TO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R10. | Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: | TO, GO | GO |  | TO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.3. | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and | TO, GO | GO |  | TO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.1. | Be based on the effective GIC flow information provided in Requirement R5; | TO, GO | GO |  | TO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6. | Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: | TO, GO | GO |  | TO
TPL-007-2 | Transmission System Planned Performance for Geomagnetic Disturbance Events | R6.4. | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | TO, GO | GO |  | TO
VAR-001-5 | Voltage and Reactive Control | R4.1. | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. | GOP |  | GOP
VAR-001-5 | Voltage and Reactive Control | R5.1. | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). | GOP |  | GOP
VAR-001-5 | Voltage and Reactive Control | R5.2. | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | GOP |  | GOP
VAR-001-5 | Voltage and Reactive Control | R5.3. | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. | GOP |  | GOP
VAR-001-5 | Voltage and Reactive Control | R6. | After consultation with the Generator Owner regarding necessary step-up transformer tap changes and the implementation schedule, the Transmission Operator shall provide documentation to the Generator Owner specifying the required tap changes, a timeframe for making the changes, and technical justification for these changes. [Violation Risk Factor: Lower] [Time Horizon: Operations Planning] | GO | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.2. | Available fixed tap ranges. | GO | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | GO | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | GOP |  | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.3. | Impedance data. | GO | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.1. | Tap settings. | GO | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R5.1. | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: | GO | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | GO | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | GOP |  | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R2.2. | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | GOP |  | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R2.1. | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. | GOP |  | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | GOP |  | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations]  That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Realtime communication or a procedure that was previously provided to the Transmission Operator; or  That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | GOP |  | GOP
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | GO | GO
VAR-002-3 | Generator Operation for Maintaining Network Voltage Schedules | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | GOP |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R2.1. | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. | GOP |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations]  Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | GOP |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | GO | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R5.1. | For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: | GO | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.3. | Impedance data. | GO | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.2. | Available fixed tap ranges. | GO | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | GO | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R2.2. | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | GOP |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | GOP |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations]  That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or  That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | GOP |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | GOP |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | GOP |  | GOP
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.1. | Tap settings. | GO | GO
VAR-002-4 | Generator Operation for Maintaining Network Voltage Schedules | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.3. | Impedance data. | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R2. | Unless exempted by the Transmission Operator, each Generator Operator shall maintain the generator voltage or Reactive Power schedule3 (within each generating Facility’s capabilities4) provided by the Transmission Operator, or otherwise shall meet the conditions of notification for deviations from the voltage or Reactive Power schedule provided by the Transmission Operator. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R6.1. | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R6. | After consultation with the Transmission Operator regarding necessary step-up transformer tap changes, the Generator Owner shall ensure that transformer tap positions are changed according to the specifications provided by the Transmission Operator, unless such action would violate safety, an equipment rating, a regulatory requirement, or a statutory requirement. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.2. | Available fixed tap ranges. | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R5.1.1. | Tap settings. | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R5.1. | For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R5. | The Generator Owner shall provide the following to its associated Transmission Operator and Transmission Planner within 30 calendar days of a request. [Violation Risk Factor: Lower] [Time Horizon: Real-time Operations] | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R4. | Each Generator Operator shall notify its associated Transmission Operator within 30 minutes of becoming aware of a change in reactive capability due to factors other than a status change described in Requirement R3. If the capability has been restored within 30 minutes of the Generator Operator becoming aware of such change, then the Generator Operator is not required to notify the Transmission Operator of the change in reactive capability. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • Reporting of status or capability changes as stated in Requirement R4 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R3. | Each Generator Operator shall notify its associated Transmission Operator of a status change on the AVR, power system stabilizer, or alternative voltage controlling device within 30 minutes of the change. If the status has been restored within 30 minutes of such change, then the Generator Operator is not required to notify the Transmission Operator of the status change. [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R2.3. | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R2.1. | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R1. | The Generator Operator shall operate each generator connected to the interconnected transmission system in the automatic voltage control mode (with its automatic voltage regulator (AVR) in service and controlling voltage) or in a different control mode as instructed by the Transmission Operator unless: 1) the generator is exempted by the Transmission Operator, or 2) the Generator Operator has notified the Transmission Operator of one of the following: [Violation Risk Factor: Medium] [Time Horizon: Real-time Operations] • That the generator is being operated in start-up,1 shutdown,2 or testing mode pursuant to a Real-time communication or a procedure that was previously provided to the Transmission Operator; or • That the generator is not being operated in automatic voltage control mode or in the control mode that was instructed by the Transmission Operator for a reason other than start-up, shutdown, or testing. | GO | GO
VAR-002-4.1 | Generator Operation for Maintaining Network Voltage Schedules | R2.2. | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. | GO | GO