## Summer Planning Net Forecast
The IRRP planning forecast accounts for the median weather gross forecast provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Subregion | Transformer Station | Net Extreme Weather Station Peak Demand Forecast, Coincident to Burlington to Nanticoke Region (MW)
|  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Brant | Brantford TS (T3/T4) | 117.5631 | 122.0946 | 127.4321 | 112.1505 | 112.4072 | 112.8843 | 113.0643 | 117.6862 | 128.0699 | 133.6225 | 139.9367 | 146.6232 | 153.4362 | 160.9476 | 168.8466 | 176.9083 | 185.7521 | 194.4186 | 197.0127 | 199.6104
| Brant TS (T1/T2) | 54.4898 | 59.7748 | 60.8651 | 61.9991 | 62.5414 | 63.1135 | 63.6298 | 65.6096 | 67.8138 | 70.2518 | 72.8741 | 75.5326 | 78.2328 | 83.3384 | 86.3949 | 89.5714 | 93.0404 | 96.4182 | 97.7394 | 99.0639
| Powerline MTS (T1/T2) | 62.3286 | 61.9027 | 69.0894 | 88.445 | 87.8278 | 88.3012 | 88.5935 | 91.9469 | 95.6001 | 99.5666 | 103.8298 | 108.4456 | 113.117 | 118.2411 | 123.997 | 129.6013 | 135.4257 | 141.4566 | 143.2755 | 145.1087
Caledonia-Norfolk | Caledonia TS (T1/T2) | 50.019 | 52.4625 | 55.0553 | 57.2371 | 58.3249 | 59.4316 | 60.051 | 60.7285 | 61.524 | 62.4181 | 63.3866 | 69.6857 | 70.7433 | 71.9877 | 73.1234 | 74.3306 | 75.5408 | 76.741 | 77.9833 | 79.2318
| Bloomsburg DS (T1/T2) | 43.2093 | 43.5204 | 43.5913 | 43.8023 | 43.9101 | 44.1615 | 44.0808 | 44.1775 | 44.3211 | 44.6483 | 45.0238 | 48.1272 | 48.5276 | 48.7526 | 49.7542 | 50.0273 | 50.2985 | 50.5629 | 50.8518 | 51.1369
| Norfolk TS (T1/T2) | 69.5176 | 71.8806 | 78.4613 | 78.8075 | 78.9444 | 79.1092 | 80.7263 | 80.849 | 83.7412 | 86.5807 | 87.3762 | 87.876 | 88.4491 | 88.9971 | 91.2972 | 91.9506 | 92.6132 | 93.2548 | 93.9314 | 94.6062
| Jarvis TS (T3/T4) | 42.6102 | 43.1169 | 45.6403 | 46.3076 | 46.6804 | 47.0944 | 47.3885 | 47.7554 | 48.3345 | 49.0837 | 50.1281 | 51.1 | 51.8088 | 52.6563 | 54.2354 | 55.2772 | 56.3832 | 57.4115 | 58.4827 | 59.562
| Caledonia-Norfolk Combined CTS | 150.5761 | 151.5761 | 162.5041 | 171.7837 | 175.4956 | 223.8218 | 409.4147 | 446.5332 | 447.5332 | 447.5332 | 447.5332 | 448.5332 | 448.5332 | 438.5332 | 439.5332 | 439.5332 | 439.5332 | 440.5332 | 440.5332 | 440.5332
Hamilton | Dundas TS 1 (T1/T2) | 96.839 | 98.563 | 100.3284 | 101.3083 | 101.6177 | 101.9518 | 102.5407 | 103.2085 | 104.3632 | 105.7423 | 107.1616 | 108.6803 | 110.3504 | 112.0732 | 114.1626 | 119.2001 | 121.0776 | 122.8589 | 129.7906 | 131.6737
| Dundas TS 2 (T5/T6) | 77.3944 | 79.2652 | 81.2066 | 81.6044 | 81.0964 | 80.6179 | 80.8259 | 81.0937 | 81.8994 | 82.7574 | 83.7716 | 84.9061 | 86.2132 | 87.4372 | 88.9343 | 90.3204 | 91.7164 | 93.1122 | 94.6195 | 96.1503
| Horning TS (T3/T4) | 73.3557 | 74.3803 | 76.0809 | 77.7867 | 79.1015 | 80.3137 | 81.3526 | 82.4913 | 83.6512 | 84.9233 | 86.3441 | 87.7764 | 89.2207 | 90.8429 | 92.7885 | 94.7503 | 96.6886 | 98.5971 | 100.6435 | 102.732
| Mohawk TS (T1/T2) | 83.3056 | 84.3724 | 86.2736 | 88.1596 | 89.5459 | 90.8287 | 91.9194 | 93.126 | 94.4139 | 95.8625 | 97.4902 | 99.0538 | 100.5944 | 102.3752 | 104.4247 | 106.6136 | 108.7819 | 110.9319 | 113.2319 | 115.5849
| Nebo TS (T1/T2) | 181.1236 | 183.5156 | 186.8737 | 190.4822 | 193.4302 | 196.3798 | 201.5203 | 204.1727 | 207.2634 | 210.6493 | 214.2167 | 217.459 | 220.548 | 223.8197 | 227.5218 | 231.4168 | 235.4465 | 239.3955 | 243.4661 | 247.5915
| Nebo TS (T3/T4) | 57.487 | 58.2479 | 59.5859 | 60.9157 | 61.9018 | 62.8137 | 64.6575 | 65.515 | 66.4224 | 67.4326 | 68.602 | 69.6997 | 70.815 | 72.0235 | 73.4573 | 74.9399 | 76.4898 | 78.0012 | 79.6187 | 81.2729
| Lake TS (T1/T2) | 60.6005 | 61.3221 | 62.6937 | 64.0423 | 64.992 | 65.8742 | 66.621 | 67.452 | 68.3777 | 69.4378 | 70.6266 | 71.7548 | 72.9596 | 74.1437 | 75.592 | 77.1363 | 78.7098 | 80.2676 | 81.9302 | 83.6348
| Lake TS (T3/T4) | 54.3818 | 55.8604 | 57.0243 | 58.1857 | 58.1124 | 58.9537 | 59.6846 | 60.4797 | 61.3474 | 62.3237 | 63.4087 | 64.4486 | 65.5611 | 66.641 | 67.9501 | 69.3401 | 70.756 | 72.1592 | 73.6544 | 75.1863
| Winona TS (T1/T2) | 52.3544 | 53.3149 | 54.5412 | 55.7568 | 56.6296 | 57.441 | 58.1422 | 58.5739 | 59.2083 | 60.1559 | 61.3405 | 62.4638 | 63.4488 | 64.5019 | 65.7532 | 67.1243 | 68.5911 | 69.9503 | 71.3993 | 72.8837
| Newton TS (T1/T2) | 53.4765 | 54.7235 | 60.5567 | 66.3941 | 70.2867 | 70.8179 | 72.3705 | 73.3844 | 74.4552 | 75.6637 | 77.0273 | 78.3577 | 79.6002 | 80.9732 | 82.536 | 84.2039 | 85.8861 | 87.5893 | 89.4058 | 91.2643
| Stirton TS (T3/T4) | 54.9622 | 54.8569 | 55.4758 | 55.0869 | 55.931 | 56.7137 | 57.3794 | 58.1159 | 58.919 | 59.829 | 60.8477 | 61.8801 | 62.8209 | 63.878 | 65.1004 | 66.4355 | 67.8307 | 69.1724 | 70.6059 | 72.0738
| Birmingham TS (T1/T2) | 11.5757 | 11.7679 | 12.0791 | 12.3961 | 12.6457 | 12.8796 | 13.1027 | 13.3255 | 13.557 | 13.8031 | 14.064 | 14.3135 | 14.5543 | 14.8031 | 15.09 | 15.3966 | 15.7053 | 16.0202 | 16.3523 | 16.6917
| Birmingham TS (T3/T4) | 62.8099 | 63.9424 | 65.6956 | 67.4948 | 68.9541 | 70.3217 | 71.6464 | 72.9524 | 74.2789 | 75.6621 | 77.1169 | 78.5317 | 79.9074 | 81.3078 | 82.8981 | 84.585 | 86.2822 | 88.0158 | 89.8417 | 91.7056
| Gage TS (T11/T12) | 25.4705 | 25.9249 | 29.516 | 33.1224 | 36.6139 | 40.0932 | 43.5499 | 46.951 | 50.4508 | 51.3889 | 52.376 | 53.3333 | 54.2616 | 55.2063 | 56.2837 | 57.4287 | 58.5805 | 59.7573 | 60.9967 | 62.2618
| Gage TS (T8/T9) | 17.0305 | 17.3343 | 18.525 | 19.7294 | 20.8709 | 22.0123 | 23.1471 | 24.2581 | 25.424 | 25.8968 | 26.3943 | 26.8766 | 27.3445 | 27.8206 | 28.3635 | 28.9405 | 29.5209 | 30.1139 | 30.7385 | 31.3761
| Elgin TS (T5/T6) | 81.0469 | 82.4806 | 85.9682 | 90.9584 | 95.2683 | 100.0462 | 101.2599 | 103.1612 | 105.0812 | 107.0759 | 109.1857 | 111.2372 | 113.2399 | 115.2742 | 117.5765 | 120.0094 | 122.4652 | 126.9061 | 129.5396 | 132.2279
| Kenilworth TS (T2/T3) | 43.9645 | 44.7473 | 45.9698 | 47.2261 | 48.2391 | 49.1886 | 50.108 | 51.0127 | 51.9366 | 52.9022 | 53.9182 | 54.903 | 55.8574 | 56.829 | 57.9375 | 59.1161 | 60.3018 | 61.513 | 62.7888 | 64.091
| Beach TS (T3/T4) | 42.985 | 43.4499 | 44.4331 | 45.4018 | 46.3699 | 46.9677 | 47.4824 | 48.0405 | 48.7099 | 49.4978 | 50.3673 | 51.1325 | 51.8552 | 52.6635 | 53.6542 | 54.7416 | 55.8509 | 56.9594 | 58.1367 | 59.3462
| Beach TS (T5/T6) | 29.3294 | 29.6573 | 30.3315 | 30.9963 | 32.6803 | 33.0939 | 33.4363 | 33.8198 | 34.2673 | 34.7934 | 35.3843 | 35.9283 | 36.5108 | 37.1647 | 37.9091 | 38.6893 | 39.5213 | 40.3018 | 41.1355 | 41.9906
| Hamilton Combined CTS | 199.1485 | 199.6485 | 212.6485 | 216.4257 | 456.6314 | 460.6314 | 462.1314 | 465.9809 | 469.9809 | 469.9809 | 469.9809 | 469.9809 | 473.9809 | 473.9809 | 473.9809 | 475.9809 | 475.9809 | 477.9809 | 477.9809 | 477.9809
Total Subregion | Brant | 234.3815 | 243.7721 | 257.3866 | 262.5946 | 262.7764 | 264.299 | 265.2876 | 275.2427 | 291.4838 | 303.4408 | 316.6406 | 330.6014 | 344.786 | 362.5272 | 379.2385 | 396.0809 | 414.2182 | 432.2933 | 438.0277 | 443.783
| Caledonia-Norfolk | 355.9321 | 362.5565 | 385.2523 | 397.9382 | 403.3554 | 453.6184 | 641.6612 | 680.0437 | 685.4541 | 690.2641 | 693.448 | 705.3222 | 708.062 | 700.927 | 707.9434 | 711.1189 | 714.3689 | 718.5034 | 721.7824 | 725.0703
| Hamilton | 1358.6418 | 1377.3753 | 1425.8074 | 1463.4737 | 1730.9188 | 1757.9409 | 1782.8781 | 1807.1152 | 1834.0076 | 1855.7786 | 1879.6245 | 1902.7172 | 1929.6442 | 1953.7597 | 1981.9143 | 2016.3693 | 2046.1836 | 2079.6038 | 2115.8766 | 2147.72
| All Subregion | 1948.9554 | 1983.7038 | 2068.4462 | 2124.0065 | 2397.0505 | 2475.8584 | 2689.8268 | 2762.4016 | 2810.9455 | 2849.4835 | 2889.7131 | 2938.6407 | 2982.4922 | 3017.2139 | 3069.0962 | 3123.5691 | 3174.7708 | 3230.4006 | 3275.6868 | 3316.5733
This document and the information contained herein is provided for informational purposes only. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## DG
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Subregion | Transformer Station | Total Contracted Distributed Generation (DG) Contribution to Peak (MW)
|  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Brant | Brantford TS (T3/T4) | 7.2309 | 7.2309 | 7.2309 | 7.2309 | 7.2309 | 7.2309 | 7.2309 | 7.2309 | 1.9389 | 1.8994 | 1.5507 | 1.1871 | 0.999 | 0.75747 | 0.49885 | 0.47885 | 0 | 0 | 0 | 0
| Brant TS (T1/T2) | 2.951 | 2.951 | 2.951 | 2.951 | 2.951 | 2.951 | 2.951 | 2.951 | 2.9462 | 2.8818 | 2.7635 | 2.6675 | 2.5842 | 0.29187 | 0.21726 | 0.19875 | 0 | 0 | 0 | 0
| Powerline MTS (T1/T2) | 0.69577 | 0.69577 | 0.69577 | 0.69577 | 0.69577 | 0.69577 | 0.69577 | 0.69577 | 0.69577 | 0.65882 | 0.62331 | 0.46551 | 0.46551 | 0.42606 | 0 | 0 | 0 | 0 | 0 | 0
Caledonia-Norfolk | Caledonia TS (T1/T2) | 5.6856 | 5.6856 | 5.6856 | 5.6856 | 5.6856 | 5.6856 | 5.6856 | 5.6856 | 5.6856 | 5.6779 | 5.6626 | 0.31367 | 0.19843 | 0.027497 | 0.023709 | 0.0098494 | 0 | 0 | 0 | 0
| Bloomsburg DS (T1/T2) | 3.4645 | 3.4645 | 3.4645 | 3.4645 | 3.4645 | 3.4645 | 3.4645 | 3.4645 | 3.4645 | 3.4645 | 3.4645 | 0.75557 | 0.75557 | 0.75557 | 0 | 0 | 0 | 0 | 0 | 0
| Norfolk TS (T1/T2) | 9.0538 | 9.0538 | 9.0538 | 9.0538 | 9.0538 | 9.0538 | 7.5094 | 7.5094 | 4.8794 | 2.3998 | 2.027 | 1.9405 | 1.761 | 1.7386 | 0.022296 | 0.016243 | 0 | 0 | 0 | 0
| Jarvis TS (T3/T4) | 1.2504 | 1.2504 | 1.2504 | 1.2504 | 1.2504 | 1.2504 | 1.2504 | 1.2504 | 1.2504 | 1.2327 | 0.99554 | 0.7493 | 0.70842 | 0.69889 | 0.066013 | 0.066013 | 0 | 0 | 0 | 0
| Caledonia-Norfolk Combined CTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hamilton | Dundas TS 1 (T1/T2) | 9.3599 | 9.3599 | 9.3599 | 9.3599 | 9.3599 | 9.3599 | 9.3599 | 9.3599 | 9.3599 | 9.2268 | 9.1829 | 9.0898 | 8.8651 | 8.7623 | 8.394 | 5.1449 | 5.0539 | 5.0539 | 0 | 0
| Dundas TS 2 (T5/T6) | 0.5358 | 0.5358 | 0.5358 | 0.5358 | 0.5358 | 0.5358 | 0.5358 | 0.5358 | 0.5358 | 0.5314 | 0.49809 | 0.41759 | 0.21124 | 0.1962 | 0.024459 | 0.01315 | 0 | 0 | 0 | 0
| Horning TS (T3/T4) | 0.40481 | 0.40481 | 0.40481 | 0.40481 | 0.40481 | 0.40481 | 0.40481 | 0.40481 | 0.40481 | 0.39442 | 0.39245 | 0.37884 | 0.36428 | 0.3064 | 0.13754 | 0.049668 | 0 | 0 | 0 | 0
| Mohawk TS (T1/T2) | 0.32488 | 0.32488 | 0.32488 | 0.32488 | 0.32488 | 0.32488 | 0.32488 | 0.32488 | 0.32488 | 0.31741 | 0.30715 | 0.29732 | 0.28753 | 0.1986 | 0.12159 | 0.041422 | 0 | 0 | 0 | 0
| Nebo TS (T1/T2) | 2.7579 | 2.7579 | 2.7579 | 2.7579 | 2.7579 | 2.7579 | 0.3828 | 0.3828 | 0.3828 | 0.3828 | 0.30512 | 0.30512 | 0.24038 | 0.21797 | 0.12137 | 0.12137 | 0 | 0 | 0 | 0
| Nebo TS (T3/T4) | 1.2396 | 1.2396 | 1.2396 | 1.2396 | 1.2396 | 1.2396 | 0.17206 | 0.17206 | 0.17206 | 0.17206 | 0.13715 | 0.13715 | 0.10805 | 0.097975 | 0.054552 | 0.054552 | 0 | 0 | 0 | 0
| Lake TS (T1/T2) | 0.26613 | 0.26613 | 0.26613 | 0.26613 | 0.26613 | 0.26613 | 0.26613 | 0.26613 | 0.26613 | 0.26613 | 0.2638 | 0.23562 | 0.091443 | 0.088879 | 0.05125 | 0.033088 | 0 | 0 | 0 | 0
| Lake TS (T3/T4) | 0.24148 | 0.24148 | 0.24148 | 0.24148 | 0.24148 | 0.24148 | 0.24148 | 0.24148 | 0.24148 | 0.24148 | 0.23937 | 0.2138 | 0.082973 | 0.080646 | 0.046502 | 0.030023 | 0 | 0 | 0 | 0
| Winona TS (T1/T2) | 0.53413 | 0.53413 | 0.53413 | 0.53413 | 0.53413 | 0.53413 | 0.53413 | 0.53413 | 0.53413 | 0.52733 | 0.38773 | 0.24079 | 0.19797 | 0.18351 | 0.16462 | 0.12437 | 0 | 0 | 0 | 0
| Newton TS (T1/T2) | 0.1866 | 0.1866 | 0.1866 | 0.1866 | 0.1866 | 0.1866 | 0.1866 | 0.1866 | 0.1866 | 0.16018 | 0.1068 | 0.034382 | 0.028094 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Stirton TS (T3/T4) | 0.19124 | 0.19124 | 0.19124 | 0.19124 | 0.19124 | 0.19124 | 0.19124 | 0.19124 | 0.19124 | 0.18977 | 0.18834 | 0.11555 | 0.10935 | 0.088313 | 0.088313 | 0.06838 | 0 | 0 | 0 | 0
| Birmingham TS (T1/T2) | 0.00054147 | 0.00054147 | 0.00054147 | 0.00054147 | 0.00054147 | 0.00054147 | 0.00054147 | 0.00054147 | 0.00054147 | 0.00040927 | 0.00040927 | 0.00040927 | 0.00040927 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Birmingham TS (T3/T4) | 0.002938 | 0.002938 | 0.002938 | 0.002938 | 0.002938 | 0.002938 | 0.002938 | 0.002938 | 0.002938 | 0.0022207 | 0.0022207 | 0.0022207 | 0.0022207 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gage TS (T11/T12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gage TS (T8/T9) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Elgin TS (T5/T6) | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.9718 | 1.9613 | 1.9589 | 1.9558 | 1.9506 | 1.9479 | 1.9479 | 1.9404 | 0 | 0 | 0
| Kenilworth TS (T2/T3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Beach TS (T3/T4) | 0.40621 | 0.40621 | 0.40621 | 0.40621 | 0.07667 | 0.07667 | 0.07667 | 0.07667 | 0.07667 | 0.076408 | 0.076135 | 0.073747 | 0.053483 | 0.032203 | 0.020043 | 0.016016 | 0 | 0 | 0 | 0
| Beach TS (T5/T6) | 1.5266 | 1.5266 | 1.5266 | 1.5266 | 0.28814 | 0.28814 | 0.28814 | 0.28814 | 0.28814 | 0.28715 | 0.28613 | 0.27715 | 0.201 | 0.12102 | 0.075323 | 0.060191 | 0 | 0 | 0 | 0
| Hamilton Combined CTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Subregion | Brant | 10.8776 | 10.8776 | 10.8776 | 10.8776 | 10.8776 | 10.8776 | 10.8776 | 10.8776 | 5.5808 | 5.44 | 4.9375 | 4.3201 | 4.0487 | 1.4754 | 0.71611 | 0.6776 | 0 | 0 | 0 | 0
| Caledonia-Norfolk | 19.4543 | 19.4543 | 19.4543 | 19.4543 | 19.4543 | 19.4543 | 17.9099 | 17.9099 | 15.2799 | 12.7749 | 12.1496 | 3.759 | 3.4235 | 3.2206 | 0.11202 | 0.092105 | 0 | 0 | 0 | 0
| Hamilton | 19.9506 | 19.9506 | 19.9506 | 19.9506 | 18.3826 | 18.3826 | 14.9399 | 14.9399 | 14.9399 | 14.7478 | 14.3351 | 13.7784 | 12.7993 | 12.3245 | 11.2475 | 7.7051 | 6.9943 | 5.0539 | 0 | 0
| All Subregion | 50.2826 | 50.2826 | 50.2826 | 50.2826 | 48.7146 | 48.7146 | 43.7275 | 43.7275 | 35.8007 | 32.9627 | 31.4222 | 21.8575 | 20.2715 | 17.0205 | 12.0756 | 8.4748 | 6.9943 | 5.0539 | 0 | 0
DRAFT

## CDM
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The analyses were conducted under normal weather conditions and can be adjusted to reflect extreme weather conditions. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Subregion | Transformer Station | Total Conservation and Demand Management (CDM) Forecast (MW)
|  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Brant | Brantford TS (T3/T4) | 0 | 1.2785 | 2.461 | 3.6226 | 5.1158 | 6.4188 | 8.0287 | 9.4669 | 10.6852 | 11.7221 | 12.5766 | 13.3437 | 14.0887 | 14.4889 | 14.8285 | 15.0768 | 15.3418 | 15.6454 | 15.8512 | 16.0835
| Brant TS (T1/T2) | 0 | 0.50386 | 0.86147 | 1.1535 | 1.5954 | 2.0142 | 2.4961 | 2.9616 | 3.2901 | 3.5321 | 3.7363 | 3.98 | 4.2671 | 4.4558 | 4.5839 | 4.6491 | 4.7201 | 4.7968 | 4.8531 | 4.9145
| Powerline MTS (T1/T2) | 0 | 0.77592 | 1.5792 | 2.2236 | 3.0108 | 3.7774 | 4.7251 | 5.5717 | 6.2885 | 6.899 | 7.4013 | 7.8533 | 8.2918 | 8.5272 | 8.7274 | 8.8731 | 9.0286 | 9.2078 | 9.3288 | 9.4657
Caledonia-Norfolk | Caledonia TS (T1/T2) | 0 | 0.47967 | 0.899 | 1.2923 | 1.7979 | 2.2946 | 2.8794 | 3.4168 | 3.8475 | 4.1983 | 4.4941 | 4.8044 | 5.1344 | 5.3453 | 5.5099 | 5.6253 | 5.7462 | 5.8796 | 5.9836 | 6.0939
| Bloomsburg DS (T1/T2) | 0 | 0.36334 | 0.67651 | 0.9491 | 1.286 | 1.6152 | 2.0079 | 2.361 | 2.6512 | 2.8997 | 3.1037 | 3.2926 | 3.4797 | 3.5627 | 3.626 | 3.6638 | 3.7049 | 3.7542 | 3.7805 | 3.8121
| Norfolk TS (T1/T2) | 0 | 0.5634 | 1.0796 | 1.4776 | 2.0195 | 2.5347 | 3.1438 | 3.705 | 4.1292 | 4.4585 | 4.7278 | 5.0097 | 5.3156 | 5.494 | 5.6191 | 5.6854 | 5.7577 | 5.8399 | 5.892 | 5.951
| Jarvis TS (T3/T4) | 0 | 0.78973 | 1.4042 | 1.9606 | 2.7416 | 3.4816 | 4.3425 | 5.1316 | 5.7101 | 6.138 | 6.4918 | 6.9294 | 7.4268 | 7.7562 | 7.9796 | 8.1098 | 8.2441 | 8.3925 | 8.5081 | 8.6259
| Caledonia-Norfolk Combined CTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hamilton | Dundas TS 1 (T1/T2) | 0 | 0.805 | 1.4973 | 2.0947 | 2.8485 | 3.5727 | 4.4655 | 5.2756 | 5.9519 | 6.5147 | 6.987 | 7.4479 | 7.9223 | 8.2055 | 8.4375 | 8.602 | 8.7752 | 8.9682 | 9.1126 | 9.2701
| Dundas TS 2 (T5/T6) | 0 | 0.56062 | 1.0506 | 1.4633 | 1.9713 | 2.4498 | 3.0523 | 3.5949 | 4.053 | 4.4325 | 4.752 | 5.0659 | 5.3908 | 5.5853 | 5.7479 | 5.8648 | 5.9883 | 6.1265 | 6.2344 | 6.3525
| Horning TS (T3/T4) | 0 | 0.73194 | 1.2884 | 1.8268 | 2.5847 | 3.3136 | 4.1687 | 4.9669 | 5.5611 | 6.0109 | 6.3972 | 6.877 | 7.4262 | 7.8098 | 8.0984 | 8.2949 | 8.4972 | 8.7178 | 8.9132 | 9.1135
| Mohawk TS (T1/T2) | 0 | 0.92466 | 1.5826 | 2.2412 | 3.2048 | 4.1229 | 5.1796 | 6.169 | 6.87 | 7.3694 | 7.7985 | 8.3973 | 9.1102 | 9.627 | 9.9962 | 10.235 | 10.4788 | 10.7428 | 10.9847 | 11.2266
| Nebo TS (T1/T2) | 0 | 1.3699 | 2.1604 | 2.7927 | 4.0156 | 5.1736 | 6.4308 | 7.7638 | 8.572 | 9.0752 | 9.5394 | 10.3159 | 11.3681 | 12.1923 | 12.7382 | 13.019 | 13.3193 | 13.6216 | 13.9017 | 14.1911
| Nebo TS (T3/T4) | 0 | 0.6376 | 1.0966 | 1.5536 | 2.2177 | 2.8514 | 3.5831 | 4.2676 | 4.7569 | 5.1093 | 5.412 | 5.8259 | 6.3152 | 6.6678 | 6.9218 | 7.0876 | 7.257 | 7.4408 | 7.6082 | 7.7762
| Lake TS (T1/T2) | 0 | 0.72782 | 1.2187 | 1.7221 | 2.4827 | 3.2023 | 4.0185 | 4.7858 | 5.3075 | 5.6597 | 5.9628 | 6.4294 | 7.0018 | 7.4277 | 7.7214 | 7.9037 | 8.0887 | 8.2879 | 8.4752 | 8.6592
| Lake TS (T3/T4) | 0 | 0.61282 | 1.0176 | 1.4248 | 2.0209 | 2.6073 | 3.2694 | 3.8987 | 4.3212 | 4.6035 | 4.8482 | 5.2302 | 5.704 | 6.059 | 6.3031 | 6.4522 | 6.6042 | 6.7668 | 6.9204 | 7.0718
| Winona TS (T1/T2) | 0 | 0.60357 | 1.0047 | 1.4074 | 2.0291 | 2.6174 | 3.2819 | 3.8929 | 4.3012 | 4.5835 | 4.8285 | 5.2089 | 5.6808 | 6.0343 | 6.2779 | 6.4266 | 6.5784 | 6.7408 | 6.8939 | 7.0451
| Newton TS (T1/T2) | 0 | 0.5509 | 1.0045 | 1.5119 | 2.259 | 2.8877 | 3.655 | 4.359 | 4.844 | 5.1799 | 5.4706 | 5.8966 | 6.4156 | 6.7985 | 7.0675 | 7.236 | 7.4083 | 7.5935 | 7.7655 | 7.9369
| Stirton TS (T3/T4) | 0 | 0.62409 | 1.043 | 1.4319 | 2.0566 | 2.6496 | 3.3262 | 3.9625 | 4.4025 | 4.7069 | 4.9689 | 5.3548 | 5.8227 | 6.1673 | 6.4086 | 6.5608 | 6.7158 | 6.883 | 7.0384 | 7.1924
| Birmingham TS (T1/T2) | 0 | 0.083453 | 0.12653 | 0.16168 | 0.23736 | 0.30813 | 0.38227 | 0.4635 | 0.5073 | 0.52996 | 0.5523 | 0.60072 | 0.6706 | 0.72784 | 0.76509 | 0.78342 | 0.80291 | 0.82221 | 0.84193 | 0.86169
| Birmingham TS (T3/T4) | 0 | 0.36337 | 0.53223 | 0.64417 | 0.94984 | 1.2353 | 1.5235 | 1.8669 | 2.0342 | 2.1091 | 2.1915 | 2.3935 | 2.703 | 2.9636 | 3.1321 | 3.2084 | 3.2917 | 3.3712 | 3.4544 | 3.5396
| Gage TS (T11/T12) | 0 | 0.15215 | 0.24698 | 0.32652 | 0.52102 | 0.72764 | 0.95689 | 1.2417 | 1.4279 | 1.4805 | 1.5383 | 1.6801 | 1.8974 | 2.0803 | 2.1986 | 2.2522 | 2.3107 | 2.3665 | 2.4249 | 2.4847
| Gage TS (T8/T9) | 0 | 0.10173 | 0.15501 | 0.19449 | 0.297 | 0.3995 | 0.5086 | 0.64155 | 0.71958 | 0.74608 | 0.77522 | 0.84669 | 0.95618 | 1.0484 | 1.108 | 1.135 | 1.1644 | 1.1926 | 1.222 | 1.2521
| Elgin TS (T5/T6) | 0 | 0.45895 | 0.68123 | 0.84802 | 1.2805 | 1.7129 | 2.0978 | 2.5706 | 2.801 | 2.9041 | 3.0175 | 3.2957 | 3.7219 | 4.0807 | 4.3127 | 4.4178 | 4.5326 | 4.642 | 4.7566 | 4.8739
| Kenilworth TS (T2/T3) | 0 | 0.26422 | 0.387 | 0.4684 | 0.69067 | 0.89822 | 1.1078 | 1.3575 | 1.4791 | 1.5336 | 1.5935 | 1.7404 | 1.9655 | 2.1549 | 2.2775 | 2.333 | 2.3936 | 2.4514 | 2.5119 | 2.5738
| Beach TS (T3/T4) | 0 | 0.56848 | 0.91303 | 1.2646 | 1.8452 | 2.3894 | 2.9889 | 3.5701 | 3.9327 | 4.1518 | 4.3445 | 4.6985 | 5.1602 | 5.5192 | 5.7556 | 5.8902 | 6.0269 | 6.1709 | 6.3125 | 6.4493
| Beach TS (T5/T6) | 0 | 0.4069 | 0.67689 | 0.9509 | 1.3724 | 1.7709 | 2.2208 | 2.6475 | 2.9338 | 3.1247 | 3.2898 | 3.5491 | 3.8705 | 4.1115 | 4.2768 | 4.3779 | 4.4807 | 4.5908 | 4.695 | 4.7974
| Hamilton Combined CTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Subregion | Brant | 0 | 2.5583 | 4.9017 | 6.9997 | 9.7221 | 12.2104 | 15.25 | 18.0002 | 20.2638 | 22.1531 | 23.7141 | 25.1769 | 26.6477 | 27.4719 | 28.1398 | 28.599 | 29.0906 | 29.6499 | 30.0331 | 30.4637
| Caledonia-Norfolk | 0 | 2.1962 | 4.0593 | 5.6796 | 7.845 | 9.9262 | 12.3736 | 14.6144 | 16.3379 | 17.6944 | 18.8173 | 20.0361 | 21.3564 | 22.1582 | 22.7346 | 23.0844 | 23.4529 | 23.8662 | 24.1642 | 24.4828
| Hamilton | 0 | 10.5481 | 17.6832 | 24.3291 | 34.8849 | 44.8903 | 56.2175 | 67.2961 | 74.7769 | 79.8252 | 84.2677 | 90.8547 | 99.1032 | 105.2611 | 109.545 | 112.0803 | 114.7148 | 117.4973 | 120.0673 | 122.668
| All Subregion | 0 | 15.3026 | 26.6442 | 37.0084 | 52.452 | 67.0268 | 83.8411 | 99.9107 | 111.3786 | 119.6728 | 126.7992 | 136.0677 | 147.1073 | 154.8912 | 160.4194 | 163.7637 | 167.2583 | 171.0134 | 174.2647 | 177.6145
DRAFT