## General Instructions
General Instructions:
The workbook covers the project specifications and testing procedures for the DER test cases.
1. The 'Project Specifications' worksheet includes the list of attributes of the DER resources to be completed.
1a. The project specifications are to be completed for each aggregated resources and each individual resource that is not part of an aggregate.
1b. The specifications table has been set up for a default of three aggregated and/or individual resources. If more there are more than three resources, please expand the table as needed by copying and pasting the values columns for each additional resource.
1c. The value for power capacity of the resource that is to be provided is the simultaneous aggregated resource peak value (an example is provided below).
2. The 'Outline' worksheet includes a description of the test and test values that are to be filled out.
2a. The test values (expected and measured) are to be completed for each aggregated resources and each individual resource that is not part of an aggregate.
2b. The tables have been set up for a default of four instances of a test. If more there are more than four instances, please expand the tables as needed by copying and pasting the values columns for each additional test instance
2c. The tables have been set up for a default of three aggregated and/or individual resources. If there are more than three resources, please expand the tables as needed by copying and pasting the table for each additional resource.
3. The 'Procedure' worksheet includes a high level description of the steps involved in the test case.
Notes:
For individual resource or aggregation time series data, including metering data, the data shall be recorded and made available to the IESO for the time and duration indicated in the test plan document.
Any data (before, during, and after testing) that can inhibit a resource’s performance when providing the desired sevices should be captured and disclosed in the test case.
Simultaneous Aggregated Resource Peak Example:
Simultaneous aggregated resource peak = the maximum energy demand or output for an aggregation of DERs as constrained by the lesser of local system or resource limits.
The following example shows the difference between the total peak value and the simultaneous aggregated resource peak (considering resource and/or system limitations), value of the project:
Project Description:
A project consists of 6 six electric vehicles (EVs) on a feeder, with a maximum charging power 10 kW for each EV. The maximum number of EVs that will charge simultaneously is 4, due to a limitation of the distribution station transformer.
The total max capacity (i.e. the total peak value) of the project is 60 kW (6 EVs x 10 kW).
The power capacity of the resource (i.e. Simultaneous aggregated resource peak) of the project is 40 kW (4 EVs x 10 kW).
Note: In some projects, the total max capacity equals the power capacity of the resource.
Project Resources - Relationship Types
The diagram below illustrates the relationship types between the project, the aggregate resources and the individual resources and also provide examples of attributes that are required.

## Project Specifications
Test Case Project Specifications - Target Ramp
Step 1 of 2: For the project, please complete the following table.
Project | Value
Project Name
Business Name and Address of Commercial Participant(s) (Note: names and addresses of residential Participants or residences are excluded)
Project Testing Duration (a date range)
Program Funding Sources
Step 2 of 2: For each aggregated resource or each individual resource not part of an aggregate, please complete the following table.
Specifications | Unit | Resource #1 Value | Resource #2 Value | Resource #3 Value
Description of Resources (if aggregated, include a description of the resources that make up the aggregation). | N/A
Individual Resource (i.e. not part of an aggregation) (Y/N) | Y or N
Aggregated Resource (Y/N) | Y or N
Aggregated Resource - Number of individual resources that make up the aggregation | N/A
Local Distribution Company ("LDC") | N/A
LDC Wholesale Market Delivery Point ID(s) | N/A
Delivery Point ID (deemed commercial point of delivery as determined by the LDC) | N/A
Substation(s) at connection point to IESO-Controlled Grid | N/A
Location (Address in Ontario)1 | N/A
Technology Type(s) | N/A
Power Capacity of a Resource That Cannot Store Energy2 | kW
Maximum Discharging Rate of the Resource* (if applicable) | kW
Maximum Charging Rate of the Resource2 (if applicable) | kW
Energy Storage Capacity of the Resource2 (if applicable) | kWh
Operating (Ambient) Temperature Range Certified by Equipment Manufacturer | deg. C
Resource ID1 | N/A
1Not to be collected from a residential Participant.
2If aggregated, enter the simultaneous aggregated resource peak value of the resources that make up the aggregation (see example in General Instructions).

## Outline
Test Case Outline - Target Ramp
Target Ramp
This test case assesses the ability of the DER to follow a power schedule based on programmed rules or a signal at least several hours in advance, especially during the time of the start or end of day ramp.
The system should automatically respond at the correct time and follow the power schedule by holding a target power input/output level for a sustained period of time.
This includes charge management activities if applicable.
Description
This test will simulate a controlled offset to a drop in solar power output over a specified time range of 1 hour to 6 hours. The test may be repeated more than once.
Each test shall be repeated on schedule agreed with the IESO. The data points must be recorded and time-stamped.
For each test:
- The test will start at a pre-determined time, without prior knowledge of the state of charge (if applicable).
- The test will ramp to a target input/output level and sustain that level of input/output at a constant rate until the earliest of 6 hours or until the facility reaches its safe operating limit to hold that level.
Notes:
1. Project operators are required to manage the state of charge (if applicable).
2. Prior to test case implementation, please consult with the IESO regarding any additional test timing conditions to satisfy contract requirements.
Step 1 of 1: For each aggregated resource or each individual resource not part of an aggregate, please complete the following table.
Notes:
1. All blank cells are to be completed by the participant, including the Test Observation Notes field (as needed).
2. For the Measured Value cells, please enter the data in the cell if the data is a single value. If the data is made up multiple values (e.g. time series data), please enter the reference data file name in the cell and attach the necessary corresponding file when reporting.
3. The sampling period for the Measured Values should be between 4 seconds and 5-minutes. The IESO's preference is for a faster sampling period, if possible.
DER Resource #1
Category | Specifications | Notes | Unit | Test Observation Notes | Test Cycle #1 Expected Value | Test Cycle #1 Measured Value | Test Cycle #2 Expected Value | Test Cycle #2 Measured Value | Test Cycle #3 Expected Value | Test Cycle #3 Measured Value | Test Cycle #4 Expected Value | Test Cycle #4 Measured Value
Resource ID | Resource ID | N/A | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Test Date | Day | The date of the test (may be a range). | Date |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Time | The time of the test (may be a range). | Time |  | N/A |  | N/A |  | N/A |  | N/A
Expected and Measured Values | Target Power output/input (AC) | The target Power output/input (AC) level to be reached at the end of each hour in the test | kW
Expected and Measured Values | Offered Ramp Rate - Ramp down rate | The target/offered Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Offered Ramp Rate - Ramp up rate | The target/offered Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Instantaneous Accuracy | 1 - [[Power output/input (AC) - Target Output/Input (AC) for time interval ] ÷ Target Output/Input (AC) for time interval] | +/- X%
Expected and Measured Values | Minimum Sampling Rate | The minimum sampling rate of active power (minimum of one sample every 5 min) | Hz
Measured Values Only | Measured Power output/input (AC) - delivery point level | Record the AC power entering or exiting each delivery point to the distribution system. | kW |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | System Temperature | Measure the system temperature, monitoring for overheating (if applicable). Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Ambient Temperature | Measure the ambient temperature. Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Grid voltage | Observed grid voltage at or near each tested delivery point. | V |  | N/A |  | N/A |  | N/A |  | N/A
DER Resource #2
Category | Specifications | Notes | Unit | Test Observation Notes | Test Cycle #1 Expected Value | Test Cycle #1 Measured Value | Test Cycle #2 Expected Value | Test Cycle #2 Measured Value | Test Cycle #3 Expected Value | Test Cycle #3 Measured Value | Test Cycle #4 Expected Value | Test Cycle #4 Measured Value
Resource ID | Resource ID | N/A | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Test Date | Day | The date of the test (may be a range). | Date |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Time | The time of the test (may be a range). | Time |  | N/A |  | N/A |  | N/A |  | N/A
Expected and Measured Values | Target Power output/input (AC) | The target Power output/input (AC) level to be reached at the end of each hour in the test | kW
Expected and Measured Values | Offered Ramp Rate - Ramp down rate | The target/offered Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Offered Ramp Rate - Ramp up rate | The target/offered Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Instantaneous Accuracy | 1 - [[Power output/input (AC) - Target Output/Input (AC) for time interval ] ÷ Target Output/Input (AC) for time interval] | +/- X%
Expected and Measured Values | Minimum Sampling Rate | The minimum sampling rate of active power (minimum of one sample every 5 min) | Hz
Measured Values Only | Measured Power output/input (AC) - delivery point level | Record the AC power entering or exiting each delivery point to the distribution system. | kW |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | System Temperature | Measure the system temperature, monitoring for overheating (if applicable). Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Ambient Temperature | Measure the ambient temperature. Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Grid voltage | Observed grid voltage at or near each tested delivery point. | V |  | N/A |  | N/A |  | N/A |  | N/A
DER Resource #3
Category | Specifications | Notes | Unit | Test Observation Notes | Test Cycle #1 Expected Value | Test Cycle #1 Measured Value | Test Cycle #2 Expected Value | Test Cycle #2 Measured Value | Test Cycle #3 Expected Value | Test Cycle #3 Measured Value | Test Cycle #4 Expected Value | Test Cycle #4 Measured Value
Resource ID | Resource ID | N/A | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Test Date | Day | The date of the test (may be a range). | Date |  | N/A |  | N/A |  | N/A |  | N/A
Test Time | Time | The time of the test (may be a range). | Time |  | N/A |  | N/A |  | N/A |  | N/A
Expected and Measured Values | Target Power output/input (AC) | The target Power output/input (AC) level to be reached at the end of each hour in the test | kW
Expected and Measured Values | Offered Ramp Rate - Ramp down rate | The target/offered Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Offered Ramp Rate - Ramp up rate | The target/offered Ramp Rate being tested for this test case | kW/min
Expected and Measured Values | Instantaneous Accuracy | 1 - [[Power output/input (AC) - Target Output/Input (AC) for time interval ] ÷ Target Output/Input (AC) for time interval] | +/- X%
Expected and Measured Values | Minimum Sampling Rate | The minimum sampling rate of active power (minimum of one sample every 5 min) | Hz
Measured Values Only | Measured Power output/input (AC) - delivery point level | Record the AC power entering or exiting each delivery point to the distribution system. | kW |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | System Temperature | Measure the system temperature, monitoring for overheating (if applicable). Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Ambient Temperature | Measure the ambient temperature. Maximum sampling period is 10 minutes. | deg. C |  | N/A |  | N/A |  | N/A |  | N/A
Measured Values Only | Grid voltage | Observed grid voltage at or near each tested delivery point. | V |  | N/A |  | N/A |  | N/A |  | N/A

## Procedure
Test Case Procedure - Target Ramp
Section | Step # | Description
Pretest (in any order) | 1 | Prepare the functionality to schedule end of day ramp a day ahead.
Pretest (in any order) | 2 | Determine the desired shape of the power schedule (e.g., flat so it does not exacerbate the end of day system ramp).
Initialize Test | 3 | Determine the number of eligible DERs along with the power schedule in kW.
Initialize Test | 4 | Set target power input/output level for the end of each hour in the test.
Initialize Test | 5 | Manually add the DR schedule to the appropriate DER.
Initialize Test | 6 | Final review of the system. If there are any errors delay the test appropriately.
Test | 7 | If applicable, the DER should charge to ensure that it's at the appropriate capacity for when it is required to discharge.
Test | 8 | Ramp to the maximum output by the end of the time period.
Test | 9 | Remain at the maximum output for the specified period of time.
Test | 10 | Ramp down using the same method as was used for ramping up.
Ending | 11 | Return the overall system to normal operation.
Ending | 12 | Confirm the appropriate data points were gathered. Note any unexpected behavior in test log.