## Overview
IESO Measures and Assumptions List March 2026
Overview:
The IESO Measures and Assumptions List (“MAL”) is a collection of electricity demand side management (DSM) measures offered in the current Save on Energy programs containing deemed energy and peak demand savings using prescriptive input assumptions (PIAs) for prescriptive measures and deemed algorithms for quasi-prescriptive measures. PIAs and algorithms are based on best current available information and consistent program assumptions used to estimate potential gross energy and peak demand savings. The deemed energy and peak demand savings serve as the basis for the design, implementation, reporting and evaluation of DSM programs.
Purpose and Scope:
Information presented in the MAL is derived and gathered from various sources ranging from previous evaluation studies involving engineering calculations to in-situ (in its original place) metering studies. Data may also be based on studies undertaken in jurisdictions outside Ontario and updated to reflect Ontario conditions. In addition to gross demand and energy savings, the MAL also includes other useful information about each measure, including effective useful life, and estimated incremental life cycle cost.
Updating the Measures and Assumptions List
Measure-level assumptions are reviewed on an annual basis or as new information becomes available. The IESO has adopted an open, transparent, and flexible approach for reviewing and maintaining its Measures and Assumptions List. Stakeholders and other interested parties may submit new measures or measure revisions to the IESO for consideration by sending an email to evaluations@ieso.ca.

## Disclaimer
IESO Measures and Assumptions List Disclaimer
The IESO Measures and Assumptions List (“MAL”) is provided solely for informational purposes and based on information currently available to the Independent Electricity System Operator (“IESO”). The IESO expressly disclaims any responsibility or liability for any other use of the information in the MAL or any methods or equipment described. In particular, the information in the MAL is not meant to be relied on to determine or project actual electricity or cost savings, or to calculate progress towards any demand side management targets. The IESO does not warrant the accuracy, reliability, completeness or timeliness of any of the information contained in the MAL, including any third party information, and undertakes no obligation to revise or update the MAL. Users of the MAL rely on the information contained therein at their own risk and remain responsible for seeking appropriate legal, technical or other professional advice with regard to their particular circumstances. The IESO and its respective officers, directors, employees, consultants, agents and subcontractors assume no liability or responsibility whatsoever to any person for damages of whatever kind and nature, which may occur or be suffered as a result of the use of the MAL or reliance on the information therein.

## Definitions
IESO Measures and Assumptions List March 2026
How to Use this Workbook:
This workbook contains demand side management measures found under six (6) tabs:
Consumer - Energy Affordability Program (EAP), Consumer - Home Renovation Savings Program (HRSP),
Business - Retrofit Prescriptive, Business - Retrofit Quasi-Prescriptive, Business - Small Business Program (SBP), and
Business - Instant Discount Program (IDP).
Below is an explanation of the column headings used in the Worksheet.
Column Heading | Description
END_USE | Shows the general application of the conservation measure (e.g. lighting, space cooling, water heating, etc.).
CONSERVATION_MEASURE_NAME | This is the high efficiency measure that usually involves the installation of equipment or technology that is considered more energy efficient than existing base case installations.
DESCRIPTION | Describes the energy efficient measure by indicating different sizes, capacities, types and efficiency levels available in the market.
BASE_MEASURE | Indicates the equipment or technology to be replaced or describes the baseline scenario.
ASSUMED_ANNUAL_OPERATING_HOURS | Indicates the assumed annual operating hours for the estimation of energy savings.
BASE_CASE_KW | Shows the assumed connected demand wattage of the base case measure.
BASE_CASE_KWH | Indicates the assumed energy consumption of the base case measure. In general, this is estimated from the assumed wattage and annual operating hours.
CONSERVATION_CASE_KW | Shows the assumed connected demand wattage of the energy efficient measure.
CONSERVATION_CASE_KWH | Indicates the assumed energy consumption of the energy efficient measure. In general, this is estimated from the assumed wattage and annual operating hours.
FIRST_YEAR_DEMAND_SAVINGS | Indicates the difference in connected demand wattages of the base and efficient measures over a one year period.
FIRST_YEAR_ENERGY_SAVINGS | Indicates the difference in energy consumption of the base and efficient measures over a one year period.
PEAK_DEMAND_SAVINGS | Indicates the demand savings occurring during summer peak from 3:00 pm to 9:00 pm, Monday to Friday, June to September.
EFFECTIVE_USEFUL_LIFE | Shows the assumed effective useful life of the measure in year(s). For lighting, this is estimated based on the effective useful life of lamps and/or ballasts and the annual operating hours.
END_USE_LOAD_PROFILE | Indicates the time-of-use pattern of equipment energy use over a year (8760 hours).
INCREMENTAL_LIFE_CYCLE_COST | Indicates the price differential between the energy efficient measure and baseline measure over the measure's lifetime.

## Consumer - EAP
END_USE | CONSERVATION_MEASURE_NAME | DESCRIPTION | BASE_MEASURE | ASSUMED_ANNUAL_OPERATING_HOURS | BASE_CASE_KW | BASE_CASE_KWH | CONSERVATION_CASE_KW | CONSERVATION_CASE_KWH | FIRST_YEAR_DEMAND_SAVINGS | FIRST_YEAR_ENERGY_SAVINGS | PEAK_DEMAND_SAVINGS | EFFECTIVE_USEFUL_LIFE | END_USE_LOAD_PROFILE
Appliances | COMPACT CHEST FREEZER | Compact Chest Freezer Replacement (ENERGY STAR Qualified< 7.75 cu ft) | Standard Freezer | 8760 | 0.025645 | 224.6537 | 0.023084 | 202.2158 | 0.0025614 | 22.4379 | 0.0029651 | 10 | PSP-Consumer-Residential-Freezers
Appliances | ENERGY STAR® FREEZER | Chest Freezer Replacement (ENERGY STAR Qualified 12 ≤ and < 14.5 cu ft) | Standard Freezer | 8760 | 0.037452 | 328.0777 | 0.028239 | 247.3716 | 0.009213 | 80.7061 | 0.010661 | 12 | PSP-Consumer-Residential-Freezers
Appliances | ENERGY STAR® FREEZER | Chest Freezer Replacement (ENERGY STAR Qualified 14.5 ≤ and < 16.0 cu ft) | Standard Freezer | 8760 | 0.039368 | 344.8643 | 0.03083 | 270.0692 | 0.0085383 | 74.7951 | 0.0098804 | 12 | PSP-Consumer-Residential-Freezers
Appliances | ENERGY STAR® FREEZER | Chest Freezer Replacement (ENERGY STAR Qualified 7.75 ≤ and < 12.0 cu ft) | Standard Freezer | 8760 | 0.034218 | 299.7504 | 0.023866 | 209.0694 | 0.010352 | 90.681 | 0.011979 | 12 | PSP-Consumer-Residential-Freezers
Appliances | ENERGY STAR® REFRIGERATOR | Refrigerator Replacement (ENERGY STAR Qualified 10.0 ≤ and < 12.5 cu ft) | Standard Refrigerator | 8760 | 0.048697 | 426.583 | 0.03568 | 312.5571 | 0.013017 | 114.0259 | 0.015325 | 12 | PSP-Consumer-Residential-Refrigerators
Appliances | ENERGY STAR® REFRIGERATOR | Refrigerator Replacement (ENERGY STAR Qualified 12.5 ≤ and < 15.5 cu ft) | Standard Refrigerator | 8760 | 0.053634 | 469.8375 | 0.038533 | 337.5533 | 0.015101 | 132.2843 | 0.017779 | 12 | PSP-Consumer-Residential-Refrigerators
Appliances | ENERGY STAR® REFRIGERATOR | Refrigerator Replacement (ENERGY STAR Qualified 15.5 ≤ and < 17.0 cu ft) | Standard Refrigerator | 8760 | 0.057674 | 505.2277 | 0.040868 | 358.0047 | 0.016806 | 147.223 | 0.019787 | 12 | PSP-Consumer-Residential-Refrigerators
Appliances | ENERGY STAR® REFRIGERATOR | Refrigerator Replacement (ENERGY STAR Qualified 17.0 ≤ and < 18.4 cu ft) | Standard Refrigerator | 8760 | 0.060278 | 528.0346 | 0.042373 | 371.1845 | 0.017905 | 156.8501 | 0.021081 | 12 | PSP-Consumer-Residential-Refrigerators
Hot Water | EFFICIENT BATHROOM AERATORS-MULTI-FAMILY | Bathroom - Flow Rate ≤ 3.8 L/min | Aerator with an Average Flow Rate of 5.7 L/min - Multi-Family | - | 4.2003 | 92.5729 | 2.7895 | 61.4781 | 1.4109 | 31.0947 | 0.0032126 | 12 | PSP-Consumer-Residential-Domestic_Hot_Water
Hot Water | EFFICIENT BATHROOM AERATORS-SINGLE FAMILY | Bathroom - Flow Rate ≤ 3.8 L/min | Aerator with an Average Flow Rate of 5.7 L/min - Single Family | - | 4.2003 | 58.8803 | 2.7895 | 39.1027 | 1.4109 | 19.7776 | 0.0020434 | 12 | PSP-Consumer-Residential-Domestic_Hot_Water
Hot Water | EFFICIENT KITCHEN AERATORS-MULTI-FAMILY | Kitchen - Flow Rate ≤ 5.7 L/min | Aerator with an Average Flow Rate of 8.4 L/min- Multi-Family | - | 4.2003 | 585.8201 | 2.8563 | 398.3647 | 1.3441 | 187.4554 | 0.019367 | 12 | PSP-Consumer-Residential-Domestic_Hot_Water
Hot Water | EFFICIENT KITCHEN AERATORS-SINGLE FAMILY | Kitchen - Flow Rate ≤ 5.7 L/min | Aerator with an Average Flow Rate of 8.4 L/min - Single Family | - | 4.2003 | 702.9841 | 2.8563 | 478.0376 | 1.3441 | 224.9465 | 0.023241 | 12 | PSP-Consumer-Residential-Domestic_Hot_Water
Hot Water | EFFICIENT SHOWERHEAD (HANDHELD)-MULTI-FAMILY | Flow Rate < 4.8 L/min | Electric DHW Showerhead for multi-family with Flow Rate = 7.6 L/min | - | 3.4795 | 760.8521 | 2.5996 | 568.4466 | 0.87989 | 192.4055 | 0.019879 | 10 | PSP-Consumer-Residential-Domestic_Hot_Water
Hot Water | EFFICIENT SHOWERHEAD (HANDHELD)-SINGLE FAMILY | Flow Rate < 4.8 L/min | Electric DHW Showerhead for multi-family with Flow Rate = 7.6 L/min | - | 2.527 | 663.089 | 1.888 | 495.406 | 0.63903 | 167.683 | 0.017325 | 10 | PSP-Consumer-Residential-Domestic_Hot_Water
Hot Water | EFFICIENT SHOWERHEAD (STANDARD)-MULTI-FAMILY | Flow Rate < 4.8 L/min | Electric DHW Showerhead for multi-family with Flow Rate = 7.6 L/min | - | 3.4795 | 760.8521 | 2.1663 | 473.7055 | 1.3132 | 287.1466 | 0.029667 | 10 | PSP-Consumer-Residential-Domestic_Hot_Water
Hot Water | EFFICIENT SHOWERHEAD (STANDARD)-SINGLE FAMILY | Flow Rate < 4.8 L/min | Electric DHW Showerhead for multi-family with Flow Rate = 7.6 L/min | - | 2.527 | 663.089 | 1.5733 | 412.8383 | 0.95369 | 250.2507 | 0.025855 | 10 | PSP-Consumer-Residential-Domestic_Hot_Water
Hot Water | HOT WATER PIPE WRAP | Hot Water Tank Pipe Insulation - ½” (per foot) | Electric hot water heater without pipe insulation | 8760 | 0.0020547 | 17.9988 | 0.00051366 | 4.4997 | 0.001541 | 13.4991 | 0.0013947 | 12 | PSP-Consumer-Residential-Domestic_Hot_Water
Hot Water | HOT WATER PIPE WRAP | Hot Water Tank Pipe Insulation - ¾” (per foot) | Electric hot water heater without pipe insulation | 8760 | 0.0030013 | 26.2917 | 0.00075034 | 6.5729 | 0.002251 | 19.7188 | 0.0020373 | 12 | PSP-Consumer-Residential-Domestic_Hot_Water
Hot Water | HOT WATER TANK WRAP | Hot water tank wrap | Electric hot water heater without insulation blanket | 8760 | 0.037368 | 327.3447 | 0.026976 | 236.3064 | 0.010392 | 91.0382 | 0.011252 | 7 | PSP-Consumer-Residential-Water_Heater_Blanket
HVAC | ENERGY STAR® DEHUMIDIFIER | Dehumidifier Replacement (ENERGY STAR Qualified ≤11.83 or less L/day) | Non-Energy Star® Dehumidifier | - | 0.33049 | 727.0859 | 0.27366 | 602.0456 | 0.056836 | 125.0402 | 0.032761 | 12 | PSP-Consumer-Residential-Dehumidifiers
HVAC | ENERGY STAR® DEHUMIDIFIER | Dehumidifier Replacement (ENERGY STAR Qualified >11.83 - <23.65 L/day) | Non-Energy Star® Dehumidifier | - | 0.53089 | 1167.9651 | 0.47191 | 1038.1912 | 0.058988 | 129.7739 | 0.034001 | 12 | PSP-Consumer-Residential-Dehumidifiers
HVAC | ENERGY STAR® DEHUMIDIFIER | Dehumidifier Replacement (ENERGY STAR Qualified ≥23.65 - <35.48 L/day) | Non-Energy Star® Dehumidifier | - | 0.43992 | 967.8199 | 0.37326 | 821.1806 | 0.066654 | 146.6394 | 0.03842 | 12 | PSP-Consumer-Residential-Dehumidifiers
HVAC | ENERGY STAR® ROOM AIR CONDITIONER | Room Air Conditioner Replacement (ENERGY STAR Qualified 10,000 - 12,000 BTU/hr) | Non-Energy Star® Room Air Conditioner | - | 1.0936 | 381.0487 | 0.80961 | 282.1074 | 0.28395 | 98.9414 | 0.045276 | 12 | PSP-Consumer-Residential-AC_Room
HVAC | ENERGY STAR® ROOM AIR CONDITIONER | Room Air Conditioner Replacement (ENERGY STAR Qualified 6,000 - 7,999 BTU/hr) | Non-Energy Star® Room Air Conditioner | - | 0.62758 | 218.6816 | 0.48349 | 168.4729 | 0.14409 | 50.2087 | 0.022975 | 12 | PSP-Consumer-Residential-AC_Room
HVAC | ENERGY STAR® ROOM AIR CONDITIONER | Room Air Conditioner Replacement (ENERGY STAR Qualified 8,000 - 9,999 BTU/hr) | Non-Energy Star® Room Air Conditioner | - | 0.82171 | 286.3241 | 0.60742 | 211.6571 | 0.21428 | 74.6671 | 0.034168 | 12 | PSP-Consumer-Residential-AC_Room
HVAC Control | LINE VOLTAGE SMART THERMOSTATS | Line Voltage Smart Thermostat – Baseboard Heater | Electric baseboard heating with non-programmable or programmable thermostat | - | - | - | - | - | - | 436.9402 | 0.0039325 | 11 | PSP-Consumer-Residential-Forced_Air_Central_Heating
HVAC Control | LOW VOLTAGE SMART THERMOSTATS | Low-voltage Smart Thermostat – Electric Furnace with CAC | Conventional manual and programmable thermostat for Electric Furnace w/ or w/o CAC | - | - | - | - | - | - | 838.0942 | 0.042413 | 11 | PSP-Consumer-Residential-AC_Central
HVAC Control | PROGRAMMABLE THERMOSTAT | Line-voltage Programmable Thermostat - Baseboard Heater | Non-programmable thermostat | - | - | - | - | - | - | 127.3878 | 0.0011465 | 11 | PSP-Consumer-Residential-Forced_Air_Central_Heating
Lighting | ≤11W LED A Shape (60W) (minimum 600 Lumen output) (Formerly: 7W – 11W ENERGY STAR® Qualified LED A Shape) | ≤11W LED A Shape (60W) (minimum 600 Lumen output) (Formerly: 7W – 11W ENERGY STAR® Qualified LED A Shape) | Mixture of incandescent and halogen bulbs based on lumen equivalence. | 1095 | 0.043 | 47.085 | 0.0094 | 10.293 | 0.0336 | 36.792 | 0.0055262 | 14 | EM&V-Residential-Lighting_Interior
Lighting | ≤14W LED A Shape (75W) (minimum 800 Lumen output) (Formerly: 10W – 14W ENERGY STAR® Qualified LED A Shape) | ≤14W LED A Shape (75W) (minimum 800 Lumen output) (Formerly: 10W – 14W ENERGY STAR® Qualified LED A Shape) | Mixture of incandescent and halogen bulbs based on lumen equivalence. | 1095 | 0.043 | 47.085 | 0.00974 | 10.6653 | 0.03326 | 36.4197 | 0.0054702 | 14 | EM&V-Residential-Lighting_Interior
Lighting | ≤16W LED PAR30 & PAR38 (minimum 600 Lumen output) (Formerly: 8W – 12W ENERGY STAR® Qualified LED PAR 30) | ≤16W LED PAR30 & PAR38 (minimum 600 Lumen output) (Formerly: 8W – 12W ENERGY STAR® Qualified LED PAR 30) | Mixture of incandescent and halogen bulbs based on lumen equivalence. | 985.5 | 0.065 | 64.0575 | 0.01351 | 13.3141 | 0.05149 | 50.7434 | 0.0076217 | 14 | EM&V-Residential-Lighting_Interior
Lighting | ≤23W LED A Shape (100W) (minimum 1600 Lumen output) (Formerly: 17W – 23W ENERGY STAR® Qualified LED A Shape) | ≤23W LED A Shape (100W) (minimum 1600 Lumen output) (Formerly: 17W – 23W ENERGY STAR® Qualified LED A Shape) | Mixture of incandescent and halogen bulbs based on lumen equivalence. | 1095 | 0.072 | 78.84 | 0.01601 | 17.531 | 0.05599 | 61.309 | 0.0092086 | 14 | EM&V-Residential-Lighting_Interior
Lighting | ≤6W LED MR 16 / PAR 16 (minimum 250 Lumen output) (Formerly: 7W – 10W ENERGY STAR® Qualified LED MR 16 / PAR 16 - GU 10 Base) | ≤6W LED MR 16 / PAR 16 (minimum 250 Lumen output) (Formerly: 7W – 10W ENERGY STAR® Qualified LED MR 16 / PAR 16 - GU 10 Base) | Mixture of incandescent and halogen bulbs based on lumen equivalence. | 985.5 | 0.04 | 39.42 | 0.00559 | 5.5089 | 0.03441 | 33.9111 | 0.0050934 | 14 | EM&V-Residential-Lighting_Interior
Lighting | LED Wet Location Rated PAR lamp ≤ 23 Watt (minimum 1100 Lumen output) | LED Wet Location Rated PAR lamp ≤ 23 Watt (minimum 1100 Lumen output) | Mixture of incandescent and halogen bulbs based on lumen equivalence. | 985.5 | 0.065 | 64.0575 | 0.01642 | 16.1819 | 0.04858 | 47.8756 | 0.0071909 | 14 | EM&V-Residential-Lighting_Interior
Lighting | LED NIGHTLIGHT | LED Nightlight | Incandescent or halogen nightlight | 4380 | 0.007 | 30.66 | 0.0003 | 1.314 | 0.0067 | 29.346 | 0.0044078 | 8 | EM&V-Residential-Lighting_Interior
Miscellaneous | HEAVY DUTY PLUG-IN TIMERS | Car Block Heater Timer | No timer on the car block heater | - | - | 376.7603 | - | 138.0211 | - | 238.7392 | 0 | 10 | EM&V-Residential-Car_Block_Heater_North_Ontario
Miscellaneous | INDOOR CLOTHES DRYING RACK/OUTDOOR RETRACTABLE CLOTHESLINE KIT | Indoor Clothes Drying Rack/Outdoor Retractable Clothesline Kit | Conventional electric clothes dryer with average 5.4 loads per week | - | - | 525.1217 | - | 431.7667 | - | 93.355 | 0.012771 | 14 | PSP-Consumer-Residential-Clothes_Dryers
Miscellaneous | TIER 2 ADVANCED POWER STRIP | Home entertainment and office equipment controlled with Tier 2 Advance Power Strips (APS) | Home entertainment and office equipment with no power strip (wall socket) or standard power strip | - | - | - | - | - | - | 234 | 0.0025974 | 7 | PSP-Consumer-Residential-Power_Bar

## Consumer - HRSP
END_USE | CONSERVATION_MEASURE_NAME | DESCRIPTION | BASE_MEASURE | ASSUMED_ANNUAL_OPERATING_HOURS | BASE_CASE_KW | BASE_CASE_KWH | CONSERVATION_CASE_KW | CONSERVATION_CASE_KWH | FIRST_YEAR_DEMAND_SAVINGS | FIRST_YEAR_ENERGY_SAVINGS | PEAK_DEMAND_SAVINGS | EFFECTIVE_USEFUL_LIFE | END_USE_LOAD_PROFILE
Appliance | Heat Pump Clothes Dryer - Electric Baseline | Standard or Compact Heat Pump Clothing Dryer that Meets the ENERGY STAR Most Efficient rating | ENERGY STAR Clothes Dryer | - | - | - | - | - | - | 134.9 kWh | 0.019 kW | 16 | PSP-Consumer-Residential-Clothes_Dryers
Appliance | Clothes Washer | A Clothes Washer that Meets the ENERGY STAR Most Efficient Rating | ENERGY STAR Washer | - | - | - | - | - | - | 52.0 kWh | 0.006 kW | 14 | PSP-Consumer-Residential-Clothes_Washers
Appliance | Induction Cooktops and Ranges | An ENERGY STAR Qualified Electric Induction Cooktop or Range | Electric Cooktop or Range | - | - | - | - | - | - | 13.9 kWh | 0.003 kW | 16 | PSP-Consumer-Residential-Cooking
Appliance | Dishwasher | Standard or Compact Residential Dishwasher that Meets the ENERGY STAR Most Efficient Rating | ENERGY STAR Dishwasher | - | - | - | - | - | - | 18.9 kWh | 0.003 kW | 11 | PSP-Consumer-Residential-Dishwashers
Appliance | Refrigerator | Refrigerator that Meets the Residential ENERGY STAR Most Efficient Rating | ENERGY STAR Refrigerator | - | - | - | - | - | - | 46.4 kWh | 0.006 kW | 12 | PSP-Consumer-Residential-Refrigerators
Appliance | Freezer | Freezer that Meets the Residential ENERGY STAR Most Efficient Rating | ENERGY STAR Freezer | - | - | - | - | - | - | 17.1 kWh | 0.004 kW | 12 | PSP-Consumer-Residential-Freezers
Building Envelope | Attic Insulation R-12 or Less (Achieve R-50) - Electric Cooling and Heating | Reach a Minimum Insulate level of R-50 for the Total Area of Your Roof Assembly | Less than or Equal to R-12 | - | - | - | - | - | - | 3562.8 kWh/1000 Sq Ft | 0.049 kW/1000 Sq Ft | 30 | PSP-Consumer-Residential-AC_Central*
Building Envelope | Attic Insulation Greater than R-12 to R-25 (Achieve R-50) - Electric Cooling and Heating | Reach a Minimum Insulate level of R-50 for the Total Area of Your Roof Assembly | Greater than R-12 to R-25 | - | - | - | - | - | - | 827.2 kWh/1000 Sq Ft | 0.011 kW/1000 Sq Ft | 30 | PSP-Consumer-Residential-AC_Central*
Building Envelope | Attic Insulation Greater than R-25 to R-35 (Achieve R-50) - Electric Cooling and Heating | Reach a Minimum Insulate Level of R-50 for the Total Area of Your Roof Assembly | Greater than R-25 to R-35 | - | - | - | - | - | - | 323.9 kWh/1000 Sq Ft | 0.004 kW/1000 Sq Ft | 30 | PSP-Consumer-Residential-AC_Central*
Building Envelope | Cathedral/Flat Roof Insulation R-25 or Less (Achieve R-28) - Electric Cooling and Heating | Reach a Minimum Insulate Level of R-28 for the Total Area of Your Roof Assembly | Less than or Equal to R-25 | - | - | - | - | - | - | 445.5 kWh//1000 Sq Ft | 0.006 kW/1000 Sq Ft | 30 | PSP-Consumer-Residential-AC_Central*
Building Envelope | Cathedral/Flat Roof Insulation R-12 or Less (Achieve R-20) - Electric Cooling and Heating | Reach a Minimum Insulate Level of R-20 for the Total Area of Your Roof Assembly | Less than or Equal to R-12 | - | - | - | - | - | - | 2834.0 kWh/1000 Sq ft | 0.039 kW/1000 Sq Ft | 30 | PSP-Consumer-Residential-AC_Central*
Building Envelope | Attic Insulation R-12 or Less (Achieve R-50) - Electric cooling only | Reach a Minimum Insulate Level of R-50 for the Total Area of Your Roof Assembly | Less than or Equal to R-12 | - | - | - | - | - | - | 107.8 kWh/1000 Sq Ft | 0.049 kW/1000 Sq Ft | 30 | PSP-Consumer-Residential-AC_Central
Building Envelope | Attic Insulation Greater than R-12 to R-25 (Achieve R-50) - Electric cooling only | Reach a Minimum Insulate Level of R-50 for the Total Area of Your Roof Assembly | Greater than R-12 to R-25 | - | - | - | - | - | - | 25.0 kWh/1000 Sq Ft | 0.011 kW/1000 Sq Ft | 30 | PSP-Consumer-Residential-AC_Central
Building Envelope | Attic Insulation Greater than R-25 to R-35 (Achieve R-50) - Electric cooling only | Reach a Minimum Insulate Level of R-50 for the Total Area of Your Roof Assembly | Greater than R-25 to R-35 | - | - | - | - | - | - | 9.8 kWh/1000 Sq Ft | 0.004 kW/1000 Sq Ft | 30 | PSP-Consumer-Residential-AC_Central
Building Envelope | Cathedral/Flat Roof Insulation R-25 or Less (Achieve R-28) - Electric cooling only | Reach a Minimum Insulate Level of R-28 for the Total Area of Your Roof Assembly | Less than or Equal to R-25 | - | - | - | - | - | - | 13.5 kWh/1000 Sq Ft | 0.006 kW/1000 Sq Ft | 30 | PSP-Consumer-Residential-AC_Central
Building Envelope | Cathedral/Flat Roof Insulation R-12 or Less (Achieve R-20) - Electric cooling only | Reach a Minimum Insulate Level of R-20 for the Total Area of Your Roof Assembly | Less than or Equal to R-12 | - | - | - | - | - | - | 85.7 kWh/1000 Sq Ft | 0.039 kW/1000 Sq Ft | 30 | PSP-Consumer-Residential-AC_Central
Solar PV | Solar PV - Electric | A Rebate for the Purchase and Installation of an Eligible Solar PV System | No Solar PV System | - | - | - | - | - | - | 1012.2 kWh | 0.136 kW | 20 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Electric Baseline) | Electric Baseline to ccASHP - Central System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Electric Baseline | - | - | - | - | - | - | 3470.9 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Electric Baseline) | Electric Baseline to ccASHP - Central System with Switchover Temperature -14 or lower, Efficient Case Supplemental Heat - Electric Resistance | Electric Baseline | - | - | - | - | - | - | 4249.9 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Oil Baseline) | Oil Baseline to ccASHP - Central System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Oil Furnace | - | - | - | - | - | - | - 4586.7 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Oil Baseline) | Oil Baseline to ccASHP - Central System with Switchover Temperature -14 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Oil Furnace | - | - | - | - | - | - | - 3807.7 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Wood Baseline) | Wood Baseline to ccASHP - Central System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Wood Furnace | - | - | - | - | - | - | - 4593.9 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Wood Baseline) | Wood Baseline to ccASHP - Central System with Switchover Temperature -14 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Wood Furnace | - | - | - | - | - | - | - 3814.8 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Propane Baseline) | Propane Baseline to ccASHP - Central System with Switchover Temperature -1 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Propane Furnace | - | - | - | - | - | - | - 6412.2 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Propane Baseline) | Propane Baseline to ccASHP - Central System with Switchover Temperature -3 or lower, Efficient Case Supplemental Heat - Electric Resistance | Propane Furnace | - | - | - | - | - | - | - 5826.1 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Propane Baseline) | Propane Baseline to ccASHP - Central System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Propane Furnace | - | - | - | - | - | - | - 4607.5 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Propane Baseline) | Propane Baseline to ccASHP - Central System with Switchover Temperature -14 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Propane Furnace | - | - | - | - | - | - | - 3828.5 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Electric Baseline) | Electric Baseline to ccASHP - Split System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Electric Baseline | - | - | - | - | - | - | 3085.9 kWh/ton | 0.125 kW/tom | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Electric Baseline) | Electric Baseline to ccASHP - Split System with Switchover Temperature -14 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Electric Baseline | - | - | - | - | - | - | 4238.5 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Oil Baseline) | Oil Baseline to ccASHP - Split System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Oil Furnace | - | - | - | - | - | - | - 4971.7 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Oil Baseline) | Oil Baseline to ccASHP - Split System with Switchover Temperature -14 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Oil Furnace | - | - | - | - | - | - | - 3819.0 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Wood Baseline) | Wood Baseline to ccASHP - Split System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Wood Furnace | - | - | - | - | - | - | - 4965.5 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Wood Baseline) | Wood Baseline to ccASHP - Split System with Switchover Temperature -14 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Wood Furnace | - | - | - | - | - | - | - 3812.9 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Propane Baseline) | Propane Baseline to ccASHP - Split System with Switchover Temperature -1 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Propane Furnace | - | - | - | - | - | - | - 7253.6 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Propane Baseline) | Propane Baseline to ccASHP - Split System with Switchover Temperature -3 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Propane Furnace | - | - | - | - | - | - | - 6594.1 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Propane Baseline) | Propane Baseline to ccASHP - Split System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Propane Furnace | - | - | - | - | - | - | - 4992.5 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Propane Baseline) | Propane Baseline to ccASHP - Split System with Switchover temperature -14 or Lower, Efficient Case Supplemental Heat - Electric Resistance | Propane Furnace | - | - | - | - | - | - | - 3839.9 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Propane Baseline) | Propane Baseline to ccASHP - Central System with Switchover Temperature -1 or lower, Efficient Case Supplemental Heat - Hybrid | Propane Furnace | - | - | - | - | - | - | - 1678.1 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Propane Baseline) | Propane Baseline to ccASHP - Central System with Switchover Temperature -3 or Lower, Efficient Case Supplemental Heat - Hybrid | Propane Furnace | - | - | - | - | - | - | - 2034.5 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Propane Baseline) | Propane Baseline to ccASHP - Central System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Hybrid | Propane Furnace | - | - | - | - | - | - | - 2723.1 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Propane Baseline) | Propane Baseline to ccASHP - Central System with Switchover Temperature -14 or Lower, Efficient Case Supplemental Heat - Hybrid | Propane Furnace | - | - | - | - | - | - | - 3156.3 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Wood Baseline) | Wood Baseline to ccASHP - Central System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Hybrid | Wood Furnace | - | - | - | - | - | - | - 2709.4 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Central System - Wood Baseline) | Wood Baseline to ccASHP - Central System with Switchover Temperature -14 or Lower, Efficient Case Supplemental Heat - Hybrid | Wood Furnace | - | - | - | - | - | - | - 3142.6 kWh/ton | 0.091 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Propane Baseline) | Propane Baseline to ccASHP - Split System with Switchover Temperature -1 or Lower, Efficient Case Supplemental Heat - Hybrid | Propane Furnace | - | - | - | - | - | - | -1789.9 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Propane Baseline) | Propane Baseline to ccASHP - Split System with Switchover Temperature -3 or Lower, Efficient Case Supplemental Heat - Hybrid | Propane Furnace | - | - | - | - | - | - | - 2093.6 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Propane Baseline) | Propane Baseline to ccASHP - Split System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Hybrid | Propane Furnace | - | - | - | - | - | - | -2645.3 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Propane Baseline) | Propane Baseline to ccASHP - Split System with Switchover Temperature -14 or Lower, Efficient Case Supplemental Heat - Hybrid | Propane Furnace | - | - | - | - | - | - | - 2960.3 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Wood Baseline) | Wood Baseline to ccASHP - Central System with Switchover Temperature -8 or Lower, Efficient Case Supplemental Heat - Hybrid | Wood Furnace | - | - | - | - | - | - | - 2618.2 kWh/ton | 0.125 kW/ton | 16 | Custom
Heat Pump | Cold Climate Air Source Heat Pump (Split System - Wood Baseline) | Wood Baseline to ccASHP - Central System with Switchover Temperature -14 or Lower, Efficient Case Supplemental Heat - Hybrid | Wood Furnace | - | - | - | - | - | - | - 2933.3 kWh/ton | 0.125 kW/ton | 16 | Custom
GSHP | Ground Source Heat Pump (GSHP) - Electric Baseline | Ground Source Heat Pump (GSHP) - Electric Baseline | Electric Baseline | - | - | - | - | - | - | 4866.7 kWh/ton | 0.150 kW/ton | 25 | Custom
GSHP | Ground Source Heat Pump (GSHP) - Oil Furnace Baseline | Ground Source Heat Pump (GSHP) - Oil Furnace Baseline | Oil Furnace | - | - | - | - | - | - | - 1572.33 kWh/ton | 0.150 kW/ton | 25 | Custom
GSHP | Ground Source Heat Pump (GSHP) - Propane Furnace Baseline | Ground Source Heat Pump (GSHP) - Propane Furnace Baseline | Propane Furnace | - | - | - | - | - | - | - 1589.67 kWh/ton | 0.150 kW/ton | 25 | Custom
GSHP | Ground Source Heat Pump (GSHP) - Wood Furnace Baseline | Ground Source Heat Pump (GSHP) - Wood Furnace Baseline | Wood Furnace | - | - | - | - | - | - | - 1564.0 kWh/ton | 0.150 kW/ton | 25 | Custom
HVAC | Smart Thermostat - Electrically Heated and Cooled Homes | Energy Star Qualified Wi-Fi-Enabled Low-Voltage Smart Thermostat for Electric Furnace or Heat Pump with Central Air-Conditioning (CAC), Featuring Temperature Settings Based on Occupancy Sensing and Remote Access | Electrically Heated and Cooled Homes with Electric Furnace or Heat Pump with Central Air-Conditioning (CAC) - Equipped with Either a Programmable or Non-Programmable Thermostat | - | - | - | - | - | - | 838.1 kWh | 0.042 kW | 11 | PSP-Consumer-Residential-AC_Central*
HVAC | Smart Thermostat - Electrically Heated Homes | Energy Star Qualified Wi-Fi-Enabled Low-Voltage Smart Thermostat for Electric Furnace or Heat Pump without Central Air-Conditioning (CAC), Featuring Temperature Settings Based on Occupancy Sensing and Remote Access | Electrically Heated Homes with no Air-Conditioning (CAC) - Equipped with Either a Programmable or Non-Programmable Thermostat | - | - | - | - | - | - | 745.4 kWh | 0 | 11 | Custom
HVAC | Smart Thermostat - Electrically Cooled Homes | Energy Star Qualified Wi-Fi-Enabled Low-Voltage Smart Thermostat for Central Air-Conditioning (CAC), Featuring Temperature Settings Based on Occupancy Sensing and Remote Access | Electrically Cooled Homes with Air-Conditioning (CAC) - Equipped with Either a Programmable or Non-Programmable Thermostat | - | - | - | - | - | - | 93 kWh | 0.042 kW | 11 | PSP-Consumer-Residential-AC_Central
Note
* used kWh savings for cooling only

## 2021 Load Profiles (hidden)
Look Up Values | Load Profile Source | Sector | Segment | Load Profile Name | Winter Peak | Winter Mid-Peak | Winter Off Peak | Summer Peak | Summer Mid-Peak | Summer Off Peak | Shoulder Mid-Peak | Shoulder Off Peak | Summer Peak Demand | Winter Peak Demand | Alternative Summer Peak Demand | Alternative Winter Peak Demand
PSP-Business-Commercial-Chiller | PSP | Non-Residential | Commercial | Chiller | 0% | 0.3202% | 2.271% | 21.66% | 20.71% | 32.18% | 10.48% | 12.16% | 0.03863% | 0.0005222% | 0.05644% | 0.0005528%
PSP-Business-Commercial-Clip_on_Timer | PSP | Non-Residential | Commercial | Clip_on_Timer | 1.895% | 3.79% | 27.47% | 0% | 5.822% | 27.6% | 5.548% | 27.88% | 0% | 0.02283% | 0% | 0.02283%
PSP-Business-Commercial-Computer_Equipment | PSP | Non-Residential | Commercial | Computer_Equipment | 6.985% | 7.809% | 18.34% | 6.177% | 8.956% | 18.28% | 14.43% | 19.02% | 0.0121% | 0.01181% | 0.01255% | 0.01243%
PSP-Business-Commercial-Cooking | PSP | Non-Residential | Commercial | Cooking | 8.449% | 9.396% | 15.41% | 8.177% | 9.322% | 14.77% | 17.45% | 17.02% | 0.01422% | 0.009593% | 0.02123% | 0.01284%
PSP-Business-Commercial-Cooling_Chillers | PSP | Non-Residential | Commercial | Cooling_Chillers | 0% | 0% | 0% | 25.48% | 30.48% | 39.29% | 2.628% | 2.117% | 0.07492% | 0% | 0.09336% | 0%
PSP-Business-Commercial-Cooling_DX | PSP | Non-Residential | Commercial | Cooling_DX | 0% | 0% | 0% | 25.48% | 30.48% | 39.29% | 2.628% | 2.117% | 0.07492% | 0% | 0.09336% | 0%
PSP-Business-Commercial-Creep_Heat_Controller | PSP | Non-Residential | Commercial | Creep_Heat_Controller | 6.632% | 7.58% | 18.94% | 5.822% | 8.733% | 18.87% | 13.87% | 19.55% | 0.01142% | 0.01142% | 0.01142% | 0.01142%
PSP-Business-Commercial-D&N_Exhaust_Fans_(dairy) | PSP | Non-Residential | Commercial | D&N_Exhaust_Fans_(dairy) | 11.82% | 14.18% | 11.94% | 0.1701% | 0.2552% | 0.08506% | 33.91% | 27.64% | 0.02835% | 0.02835% | 0.008506% | 0.02835%
PSP-Business-Commercial-D&N_Exhaust_Fans_(non-dairy) | PSP | Non-Residential | Commercial | D&N_Exhaust_Fans_(non-dairy) | 6.006% | 7.201% | 6.121% | 7.346% | 11.02% | 23.78% | 17.44% | 21.09% | 0.0144% | 0.0144% | 0.0144% | 0.0144%
PSP-Business-Commercial-Domestic_Hot_Water | PSP | Non-Residential | Commercial | Domestic_Hot_Water | 9.185% | 10.36% | 18.92% | 6.398% | 8.449% | 14.2% | 15.76% | 16.72% | 0.01224% | 0.01513% | 0.01505% | 0.01864%
PSP-Business-Commercial-Double_Creep_Pad | PSP | Non-Residential | Commercial | Double_Creep_Pad | 7.276% | 8.316% | 20.78% | 4.716% | 7.074% | 15.25% | 15.17% | 21.42% | 0.009259% | 0.01252% | 0.0102% | 0.01252%
PSP-Business-Commercial-Electric_Auxiliary | PSP | Non-Residential | Commercial | Electric_Auxiliary | 6.921% | 8.724% | 16.56% | 6.265% | 9.22% | 17.28% | 16.49% | 18.54% | 0.01214% | 0.01205% | 0.01563% | 0.01493%
PSP-Business-Commercial-Elevators | PSP | Non-Residential | Commercial | Elevators | 7.478% | 8.46% | 17.59% | 6.838% | 8.764% | 16.6% | 15.58% | 18.69% | 0.01254% | 0.01084% | 0.01583% | 0.01273%
PSP-Business-Commercial-Exit_Signs | PSP | Non-Residential | Commercial | Exit_Signs | 6.632% | 7.58% | 18.94% | 5.822% | 8.733% | 18.87% | 13.87% | 19.55% | 0.01142% | 0.01142% | 0.01142% | 0.01142%
PSP-Business-Commercial-Forced_Air_Central_Heating | PSP | Non-Residential | Commercial | Forced_Air_Central_Heating | 16.43% | 15.83% | 40.73% | 3.256% | 3.175% | 4.635% | 6.401% | 9.543% | 0.006875% | 0.02438% | 0.01351% | 0.04064%
PSP-Business-Commercial-Ground Source Heat Pump | PSP | Non-Residential | Commercial | Ground Source Heat Pump | 13.69% | 10.83% | 21.99% | 5.058% | 5.105% | 5.204% | 16.74% | 21.38% | 0.009197% | 0.01705% | 0.01245% | 0.02212%
PSP-Business-Commercial-HE_Exhaust_Fans_>24" | PSP | Non-Residential | Commercial | HE_Exhaust_Fans_>24" | 0% | 0.149% | 0% | 37.7% | 18.78% | 24.81% | 12.44% | 6.11% | 0.07452% | 0% | 0.07452% | 0%
PSP-Business-Commercial-HE_Exhaust_Fans_≤24" | PSP | Non-Residential | Commercial | HE_Exhaust_Fans_≤24" | 2.435% | 14.61% | 7.803% | 14.96% | 19.74% | 15.2% | 16.84% | 8.419% | 0.02933% | 0% | 0.02933% | 0%
PSP-Business-Commercial-HT_Cutout_Thermostat | PSP | Non-Residential | Commercial | HT_Cutout_Thermostat | 0% | 0% | 0% | 41.31% | 27.54% | 30.33% | 0.8197% | 0% | 0.08197% | 0% | 0.08197% | 0%
PSP-Business-Commercial-HVAC_Fans_Pumps | PSP | Non-Residential | Commercial | HVAC_Fans_Pumps | 6.454% | 7.376% | 19.33% | 5.65% | 8.475% | 19.28% | 13.46% | 19.97% | 0.01108% | 0.01112% | 0.01142% | 0.01142%
PSP-Business-Commercial-HVLS | PSP | Non-Residential | Commercial | HVLS | 0% | 0% | 0% | 17.21% | 25.82% | 56.15% | 0.5123% | 0.3074% | 0.03415% | 0% | 0.03415% | 0%
PSP-Business-Commercial-Lighting_Exterior | PSP | Non-Residential | Commercial | Lighting_Exterior | 5.323% | 4.129% | 28.36% | 0.5445% | 3.585% | 24.67% | 6.489% | 26.9% | 0.00107% | 0.02063% | 0.0011% | 0.022%
PSP-Business-Commercial-Lighting_Interior_Architectural | PSP | Non-Residential | Commercial | Lighting_Interior_Architectural | 7.641% | 8.73% | 17.09% | 7.012% | 9.003% | 16.18% | 16% | 18.34% | 0.01274% | 0.01069% | 0.01678% | 0.01298%
PSP-Business-Commercial-Lighting_Interior_General | PSP | Non-Residential | Commercial | Lighting_Interior_General | 7.641% | 8.73% | 17.09% | 7.012% | 9.003% | 16.18% | 16% | 18.34% | 0.01274% | 0.01069% | 0.01678% | 0.01298%
PSP-Business-Commercial-Lighting_Interior_High_Bay | PSP | Non-Residential | Commercial | Lighting_Interior_High_Bay | 7.641% | 8.73% | 17.09% | 7.012% | 9.003% | 16.18% | 16% | 18.34% | 0.01274% | 0.01069% | 0.01678% | 0.01298%
PSP-Business-Commercial-Lighting_Interior_Office | PSP | Non-Residential | Commercial | Lighting_Interior_Office | 7.641% | 8.73% | 17.09% | 7.012% | 9.003% | 16.18% | 16% | 18.34% | 0.01274% | 0.01069% | 0.01678% | 0.01298%
PSP-Business-Commercial-Lighting_Small Business | PSP | Non-Residential | Commercial | Lighting_Small Business | 7.817% | 9.182% | 16.02% | 7.917% | 9.383% | 16.15% | 16.41% | 17.13% | 0.01433% | 0.01045% | 0.01904% | 0.01395%
PSP-Business-Commercial-Livestock_Waterer | PSP | Non-Residential | Commercial | Livestock_Waterer | 5.647% | 11.29% | 82.23% | 0% | 0% | 0% | 0.2066% | 0.6198% | 0% | 0% | 0% | 0%
PSP-Business-Commercial-Miscellaneous_Equipment | PSP | Non-Residential | Commercial | Miscellaneous_Equipment | 6.961% | 7.816% | 18.33% | 6.202% | 8.908% | 18.3% | 14.43% | 19.04% | 0.01209% | 0.01165% | 0.01272% | 0.01226%
PSP-Business-Commercial-Non_Ducted_Central_Heating | PSP | Non-Residential | Commercial | Non_Ducted_Central_Heating | 18.38% | 19.67% | 44.28% | 0.02039% | 0.03983% | 0.06979% | 7.661% | 9.875% | 0.0001481% | 0.03086% | 0.0004104% | 0.04859%
PSP-Business-Commercial-Other_Plug_Loads | PSP | Non-Residential | Commercial | Other_Plug_Loads | 6.97% | 7.795% | 18.34% | 6.164% | 8.94% | 18.31% | 14.43% | 19.05% | 0.0121% | 0.01181% | 0.01255% | 0.01243%
PSP-Business-Commercial-Refrigerated_Display_Case_Food Retail | PSP | Non-Residential | Commercial | Refrigerated_Display_Case_Food Retail | 8.331% | 12.18% | 12.48% | 11.38% | 9.592% | 12.57% | 19.88% | 13.58% | 0.01916% | 0.01242% | 0.02406% | 0.01579%
PSP-Business-Commercial-Refrigeration | PSP | Non-Residential | Commercial | Refrigeration | 6.607% | 7.634% | 18.65% | 6.096% | 8.735% | 18.9% | 13.96% | 19.41% | 0.01188% | 0.01121% | 0.01266% | 0.01165%
PSP-Business-Commercial-Single_Creep_Pad | PSP | Non-Residential | Commercial | Single_Creep_Pad | 7.751% | 8.858% | 22.13% | 3.9% | 5.851% | 12.58% | 16.12% | 22.8% | 0.007667% | 0.01334% | 0.009308% | 0.01334%
PSP-Business-Commercial-Space_Cooling_&_Heating | PSP | Non-Residential | Commercial | Space_Cooling_&_Heating | 8.16% | 8.014% | 19.41% | 11.64% | 15.92% | 22.77% | 6.805% | 7.284% | 0.0304% | 0.01507% | 0.05591% | 0.02015%
PSP-Business-Commercial-Timer_Photocell | PSP | Non-Residential | Commercial | Timer_Photocell | 6.193% | 11.08% | 7.88% | 13.82% | 9.567% | 11.26% | 24.99% | 15.21% | 0.02253% | 0% | 0.02955% | 0%
PSP-Business-Food_Retail-Computer_Equipment | PSP | Non-Residential | Food_Retail | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Food_Retail-Cooking | PSP | Non-Residential | Food_Retail | Cooking | 8.443% | 8.591% | 16.2% | 7.108% | 10.34% | 16.06% | 16.46% | 16.81% | 0.01224% | 0.011% | 0.01422% | 0.01122%
PSP-Business-Food_Retail-Cooling_Chillers | PSP | Non-Residential | Food_Retail | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Food_Retail-Cooling_DX | PSP | Non-Residential | Food_Retail | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Food_Retail-Domestic_Hot_Water | PSP | Non-Residential | Food_Retail | Domestic_Hot_Water | 10.96% | 11.38% | 16.48% | 6.846% | 10.05% | 12.15% | 17.98% | 14.16% | 0.01353% | 0.0194% | 0.01426% | 0.02147%
PSP-Business-Food_Retail-Elevators | PSP | Non-Residential | Food_Retail | Elevators | 7.422% | 8.178% | 17.58% | 6.606% | 9.37% | 17.49% | 15.16% | 18.2% | 0.01289% | 0.01234% | 0.01295% | 0.01264%
PSP-Business-Food_Retail-HVAC_Fans_Pumps | PSP | Non-Residential | Food_Retail | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Food_Retail-Lighting_Exterior | PSP | Non-Residential | Food_Retail | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Food_Retail-Lighting_Interior_Architectural | PSP | Non-Residential | Food_Retail | Lighting_Interior_Architectural | 8.366% | 9.388% | 15.46% | 7.289% | 10.89% | 15.31% | 17.18% | 16.11% | 0.01421% | 0.01444% | 0.01447% | 0.01447%
PSP-Business-Food_Retail-Lighting_Interior_General | PSP | Non-Residential | Food_Retail | Lighting_Interior_General | 8.366% | 9.388% | 15.46% | 7.289% | 10.89% | 15.31% | 17.18% | 16.11% | 0.01421% | 0.01444% | 0.01447% | 0.01447%
PSP-Business-Food_Retail-Lighting_Interior_High_Bay | PSP | Non-Residential | Food_Retail | Lighting_Interior_High_Bay | 8.366% | 9.388% | 15.46% | 7.289% | 10.89% | 15.31% | 17.18% | 16.11% | 0.01421% | 0.01444% | 0.01447% | 0.01447%
PSP-Business-Food_Retail-Miscellaneous_Equipment | PSP | Non-Residential | Food_Retail | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Food_Retail-Other_Plug_Loads | PSP | Non-Residential | Food_Retail | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Food_Retail-Refrigeration | PSP | Non-Residential | Food_Retail | Refrigeration | 6.385% | 7.524% | 17.72% | 6.74% | 9.353% | 19.41% | 14.04% | 18.82% | 0.01333% | 0.011% | 0.01387% | 0.01106%
PSP-Business-Hospital-Computer_Equipment | PSP | Non-Residential | Hospital | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Hospital-Cooking | PSP | Non-Residential | Hospital | Cooking | 9.714% | 11.44% | 12.01% | 9.407% | 12.25% | 11.78% | 20.64% | 12.76% | 0.01935% | 0.01926% | 0.02012% | 0.01995%
PSP-Business-Hospital-Cooling_Chillers | PSP | Non-Residential | Hospital | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Hospital-Cooling_DX | PSP | Non-Residential | Hospital | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Hospital-Domestic_Hot_Water | PSP | Non-Residential | Hospital | Domestic_Hot_Water | 9.759% | 10.46% | 18.51% | 6.869% | 8.429% | 13.71% | 16.29% | 15.98% | 0.01219% | 0.01274% | 0.01445% | 0.01416%
PSP-Business-Hospital-Elevators | PSP | Non-Residential | Hospital | Elevators | 7.334% | 8.738% | 17.06% | 7.364% | 9.095% | 17.01% | 15.68% | 17.71% | 0.013% | 0.009856% | 0.01496% | 0.01012%
PSP-Business-Hospital-HVAC_Fans_Pumps | PSP | Non-Residential | Hospital | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Hospital-Lighting_Exterior | PSP | Non-Residential | Hospital | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Hospital-Lighting_Interior_Architectural | PSP | Non-Residential | Hospital | Lighting_Interior_Architectural | 7.591% | 8.671% | 16.87% | 7.26% | 9.394% | 16.83% | 15.87% | 17.52% | 0.01335% | 0.01089% | 0.01445% | 0.0112%
PSP-Business-Hospital-Lighting_Interior_General | PSP | Non-Residential | Hospital | Lighting_Interior_General | 7.591% | 8.671% | 16.87% | 7.26% | 9.394% | 16.83% | 15.87% | 17.52% | 0.01335% | 0.01089% | 0.01445% | 0.0112%
PSP-Business-Hospital-Lighting_Interior_High_Bay | PSP | Non-Residential | Hospital | Lighting_Interior_High_Bay | 7.591% | 8.671% | 16.87% | 7.26% | 9.394% | 16.83% | 15.87% | 17.52% | 0.01335% | 0.01089% | 0.01445% | 0.0112%
PSP-Business-Hospital-Miscellaneous_Equipment | PSP | Non-Residential | Hospital | Miscellaneous_Equipment | 7.334% | 8.738% | 17.06% | 7.364% | 9.095% | 17.01% | 15.68% | 17.71% | 0.013% | 0.009856% | 0.01496% | 0.01012%
PSP-Business-Hospital-Other_Plug_Loads | PSP | Non-Residential | Hospital | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Hospital-Refrigeration | PSP | Non-Residential | Hospital | Refrigeration | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Large_Hotel-Computer_Equipment | PSP | Non-Residential | Large_Hotel | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Large_Hotel-Cooking | PSP | Non-Residential | Large_Hotel | Cooking | 9.067% | 10.18% | 13.91% | 8.166% | 11.55% | 13.73% | 18.78% | 14.62% | 0.01626% | 0.01651% | 0.01753% | 0.01695%
PSP-Business-Large_Hotel-Cooling_Chillers | PSP | Non-Residential | Large_Hotel | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Large_Hotel-Cooling_DX | PSP | Non-Residential | Large_Hotel | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Large_Hotel-Domestic_Hot_Water | PSP | Non-Residential | Large_Hotel | Domestic_Hot_Water | 9.371% | 10.65% | 18.72% | 6.076% | 9.066% | 13.84% | 16.12% | 16.16% | 0.0118% | 0.01659% | 0.01195% | 0.01799%
PSP-Business-Large_Hotel-Elevators | PSP | Non-Residential | Large_Hotel | Elevators | 7.711% | 8.619% | 16.83% | 6.711% | 10.01% | 16.71% | 15.94% | 17.47% | 0.01391% | 0.01495% | 0.01498% | 0.01498%
PSP-Business-Large_Hotel-HVAC_Fans_Pumps | PSP | Non-Residential | Large_Hotel | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Large_Hotel-Lighting_Exterior | PSP | Non-Residential | Large_Hotel | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Large_Hotel-Lighting_Interior_Architectural | PSP | Non-Residential | Large_Hotel | Lighting_Interior_Architectural | 7.85% | 8.187% | 17.12% | 5.784% | 10.64% | 17.02% | 15.65% | 17.75% | 0.01208% | 0.01454% | 0.01402% | 0.01514%
PSP-Business-Large_Hotel-Lighting_Interior_General | PSP | Non-Residential | Large_Hotel | Lighting_Interior_General | 7.85% | 8.187% | 17.12% | 5.784% | 10.64% | 17.02% | 15.65% | 17.75% | 0.01208% | 0.01454% | 0.01402% | 0.01514%
PSP-Business-Large_Hotel-Lighting_Interior_High_Bay | PSP | Non-Residential | Large_Hotel | Lighting_Interior_High_Bay | 7.85% | 8.187% | 17.12% | 5.784% | 10.64% | 17.02% | 15.65% | 17.75% | 0.01208% | 0.01454% | 0.01402% | 0.01514%
PSP-Business-Large_Hotel-Miscellaneous_Equipment | PSP | Non-Residential | Large_Hotel | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Large_Hotel-Other_Plug_Loads | PSP | Non-Residential | Large_Hotel | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Large_Hotel-Refrigeration | PSP | Non-Residential | Large_Hotel | Refrigeration | 7% | 8.041% | 18.12% | 6.274% | 9.129% | 18.03% | 14.68% | 18.73% | 0.01225% | 0.01197% | 0.0123% | 0.01206%
PSP-Business-Large_Non_Food_Retail-Computer_Equipment | PSP | Non-Residential | Large_Non_Food_Retail | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Large_Non_Food_Retail-Cooking | PSP | Non-Residential | Large_Non_Food_Retail | Cooking | 10.08% | 11.53% | 11.65% | 9.357% | 12.77% | 11.41% | 20.83% | 12.39% | 0.01837% | 0.01816% | 0.01887% | 0.01877%
PSP-Business-Large_Non_Food_Retail-Cooling_Chillers | PSP | Non-Residential | Large_Non_Food_Retail | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Large_Non_Food_Retail-Cooling_DX | PSP | Non-Residential | Large_Non_Food_Retail | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Large_Non_Food_Retail-Domestic_Hot_Water | PSP | Non-Residential | Large_Non_Food_Retail | Domestic_Hot_Water | 10.43% | 12.66% | 15.72% | 8.311% | 9.153% | 11.57% | 18.59% | 13.56% | 0.01584% | 0.01992% | 0.01661% | 0.02285%
PSP-Business-Large_Non_Food_Retail-Elevators | PSP | Non-Residential | Large_Non_Food_Retail | Elevators | 8.105% | 9.716% | 15.38% | 7.603% | 10.65% | 15.23% | 17.26% | 16.05% | 0.01491% | 0.01487% | 0.01491% | 0.01491%
PSP-Business-Large_Non_Food_Retail-HVAC_Fans_Pumps | PSP | Non-Residential | Large_Non_Food_Retail | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Large_Non_Food_Retail-Lighting_Exterior | PSP | Non-Residential | Large_Non_Food_Retail | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Large_Non_Food_Retail-Lighting_Interior_Architectural | PSP | Non-Residential | Large_Non_Food_Retail | Lighting_Interior_Architectural | 8.258% | 9.803% | 15.04% | 7.563% | 10.93% | 15.02% | 17.49% | 15.88% | 0.01483% | 0.01483% | 0.01483% | 0.01483%
PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | PSP | Non-Residential | Large_Non_Food_Retail | Lighting_Interior_General | 8.258% | 9.803% | 15.04% | 7.563% | 10.93% | 15.02% | 17.49% | 15.88% | 0.01483% | 0.01483% | 0.01483% | 0.01483%
PSP-Business-Large_Non_Food_Retail-Lighting_Interior_High_Bay | PSP | Non-Residential | Large_Non_Food_Retail | Lighting_Interior_High_Bay | 8.258% | 9.803% | 15.04% | 7.563% | 10.93% | 15.02% | 17.49% | 15.88% | 0.01483% | 0.01483% | 0.01483% | 0.01483%
PSP-Business-Large_Non_Food_Retail-Miscellaneous_Equipment | PSP | Non-Residential | Large_Non_Food_Retail | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Large_Non_Food_Retail-Other_Plug_Loads | PSP | Non-Residential | Large_Non_Food_Retail | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Large_Non_Food_Retail-Refrigeration | PSP | Non-Residential | Large_Non_Food_Retail | Refrigeration | 6.913% | 7.981% | 18.27% | 6.279% | 8.973% | 18.19% | 14.51% | 18.88% | 0.01225% | 0.01191% | 0.01235% | 0.01208%
PSP-Business-Large_Office-Computer_Equipment | PSP | Non-Residential | Large_Office | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Large_Office-Cooking | PSP | Non-Residential | Large_Office | Cooking | 11.86% | 12.64% | 8.224% | 12.57% | 12.26% | 9.3% | 23.63% | 9.509% | 0.01995% | 0.007396% | 0.02674% | 0.01088%
PSP-Business-Large_Office-Cooling_Chillers | PSP | Non-Residential | Large_Office | Cooling_Chillers | 0% | 0% | 0% | 28.47% | 26.31% | 40.47% | 2.577% | 2.168% | 0.08049% | 0% | 0.104% | 0%
PSP-Business-Large_Office-Cooling_DX | PSP | Non-Residential | Large_Office | Cooling_DX | 0% | 0% | 0% | 28.47% | 26.31% | 40.47% | 2.577% | 2.168% | 0.08049% | 0% | 0.104% | 0%
PSP-Business-Large_Office-Domestic_Hot_Water | PSP | Non-Residential | Large_Office | Domestic_Hot_Water | 8.358% | 9.637% | 20.72% | 5.779% | 7.835% | 15.41% | 14.52% | 17.75% | 0.01079% | 0.01238% | 0.01143% | 0.01343%
PSP-Business-Large_Office-Elevators | PSP | Non-Residential | Large_Office | Elevators | 8.822% | 9.779% | 14.37% | 8.758% | 10.17% | 14.79% | 18.03% | 15.28% | 0.01521% | 0.009915% | 0.01818% | 0.01135%
PSP-Business-Large_Office-HVAC_Fans_Pumps | PSP | Non-Residential | Large_Office | HVAC_Fans_Pumps | 7.949% | 9.085% | 16.13% | 6.978% | 10.47% | 16% | 16.62% | 16.76% | 0.01368% | 0.01363% | 0.01368% | 0.01368%
PSP-Business-Large_Office-Lighting_Exterior | PSP | Non-Residential | Large_Office | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Large_Office-Lighting_Interior_Architectural | PSP | Non-Residential | Large_Office | Lighting_Interior_Architectural | 10.21% | 11.46% | 11.23% | 9.314% | 12.69% | 11.84% | 20.95% | 12.3% | 0.01786% | 0.01562% | 0.01864% | 0.01709%
PSP-Business-Large_Office-Lighting_Interior_General | PSP | Non-Residential | Large_Office | Lighting_Interior_General | 10.21% | 11.46% | 11.23% | 9.314% | 12.69% | 11.84% | 20.95% | 12.3% | 0.01786% | 0.01562% | 0.01864% | 0.01709%
PSP-Business-Large_Office-Lighting_Interior_High_Bay | PSP | Non-Residential | Large_Office | Lighting_Interior_High_Bay | 10.21% | 11.46% | 11.23% | 9.314% | 12.69% | 11.84% | 20.95% | 12.3% | 0.01786% | 0.01562% | 0.01864% | 0.01709%
PSP-Business-Large_Office-Miscellaneous_Equipment | PSP | Non-Residential | Large_Office | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Large_Office-Other_Plug_Loads | PSP | Non-Residential | Large_Office | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Large_Office-Refrigeration | PSP | Non-Residential | Large_Office | Refrigeration | 6.889% | 8.046% | 18.2% | 6.377% | 8.902% | 18.19% | 14.56% | 18.84% | 0.01194% | 0.01088% | 0.01275% | 0.0109%
PSP-Business-Nursing_Home-Computer_Equipment | PSP | Non-Residential | Nursing_Home | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Nursing_Home-Cooking | PSP | Non-Residential | Nursing_Home | Cooking | 9.714% | 11.44% | 12.01% | 9.407% | 12.25% | 11.78% | 20.64% | 12.76% | 0.01935% | 0.01926% | 0.02012% | 0.01995%
PSP-Business-Nursing_Home-Cooling_Chillers | PSP | Non-Residential | Nursing_Home | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Nursing_Home-Cooling_DX | PSP | Non-Residential | Nursing_Home | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Nursing_Home-Domestic_Hot_Water | PSP | Non-Residential | Nursing_Home | Domestic_Hot_Water | 10.28% | 10.92% | 17.54% | 6.367% | 9.67% | 12.94% | 17.07% | 15.21% | 0.01239% | 0.01799% | 0.01309% | 0.01965%
PSP-Business-Nursing_Home-Elevators | PSP | Non-Residential | Nursing_Home | Elevators | 7.903% | 9.571% | 15.66% | 7.794% | 10.1% | 15.58% | 17.05% | 16.34% | 0.01471% | 0.01343% | 0.01564% | 0.01372%
PSP-Business-Nursing_Home-HVAC_Fans_Pumps | PSP | Non-Residential | Nursing_Home | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Nursing_Home-Lighting_Exterior | PSP | Non-Residential | Nursing_Home | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Nursing_Home-Lighting_Interior_Architectural | PSP | Non-Residential | Nursing_Home | Lighting_Interior_Architectural | 7.737% | 9.581% | 15.83% | 7.874% | 9.862% | 15.71% | 16.9% | 16.5% | 0.01512% | 0.01409% | 0.01555% | 0.01451%
PSP-Business-Nursing_Home-Lighting_Interior_General | PSP | Non-Residential | Nursing_Home | Lighting_Interior_General | 7.737% | 9.581% | 15.83% | 7.874% | 9.862% | 15.71% | 16.9% | 16.5% | 0.01512% | 0.01409% | 0.01555% | 0.01451%
PSP-Business-Nursing_Home-Lighting_Interior_High_Bay | PSP | Non-Residential | Nursing_Home | Lighting_Interior_High_Bay | 7.737% | 9.581% | 15.83% | 7.874% | 9.862% | 15.71% | 16.9% | 16.5% | 0.01512% | 0.01409% | 0.01555% | 0.01451%
PSP-Business-Nursing_Home-Miscellaneous_Equipment | PSP | Non-Residential | Nursing_Home | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Nursing_Home-Other_Plug_Loads | PSP | Non-Residential | Nursing_Home | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Nursing_Home-Refrigeration | PSP | Non-Residential | Nursing_Home | Refrigeration | 6.997% | 8.042% | 18.12% | 6.275% | 9.127% | 18.03% | 14.68% | 18.73% | 0.01224% | 0.01197% | 0.0123% | 0.01206%
PSP-Business-Other_Commercial_Buildings-Computer_Equipment | PSP | Non-Residential | Other_Commercial_Buildings | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Commercial_Buildings-Cooking | PSP | Non-Residential | Other_Commercial_Buildings | Cooking | 10.58% | 13.65% | 8.905% | 13.92% | 10.9% | 8.976% | 23.36% | 9.713% | 0.01847% | 0.0006521% | 0.03086% | 0.0009808%
PSP-Business-Other_Commercial_Buildings-Cooling_Chillers | PSP | Non-Residential | Other_Commercial_Buildings | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Other_Commercial_Buildings-Cooling_DX | PSP | Non-Residential | Other_Commercial_Buildings | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Other_Commercial_Buildings-Domestic_Hot_Water | PSP | Non-Residential | Other_Commercial_Buildings | Domestic_Hot_Water | 10.63% | 12.16% | 16.04% | 7.361% | 9.882% | 11.77% | 18.36% | 13.8% | 0.01429% | 0.01996% | 0.01448% | 0.0218%
PSP-Business-Other_Commercial_Buildings-Elevators | PSP | Non-Residential | Other_Commercial_Buildings | Elevators | 8.443% | 10.68% | 14.02% | 9.883% | 9.701% | 14.01% | 18.52% | 14.73% | 0.01543% | 0.006462% | 0.02016% | 0.006736%
PSP-Business-Other_Commercial_Buildings-HVAC_Fans_Pumps | PSP | Non-Residential | Other_Commercial_Buildings | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Other_Commercial_Buildings-Lighting_Exterior | PSP | Non-Residential | Other_Commercial_Buildings | Lighting_Exterior | 5.335% | 4.241% | 28.06% | 0.561% | 3.786% | 24.61% | 6.721% | 26.69% | 0.0011% | 0.02119% | 0.0011% | 0.02189%
PSP-Business-Other_Commercial_Buildings-Lighting_Interior_Architectural | PSP | Non-Residential | Other_Commercial_Buildings | Lighting_Interior_Architectural | 8.329% | 11.19% | 13.63% | 10.46% | 9.527% | 13.64% | 18.89% | 14.34% | 0.01578% | 0.005955% | 0.02079% | 0.006051%
PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | PSP | Non-Residential | Other_Commercial_Buildings | Lighting_Interior_General | 8.329% | 11.19% | 13.63% | 10.46% | 9.527% | 13.64% | 18.89% | 14.34% | 0.01578% | 0.005955% | 0.02079% | 0.006051%
PSP-Business-Other_Commercial_Buildings-Lighting_Interior_High_Bay | PSP | Non-Residential | Other_Commercial_Buildings | Lighting_Interior_High_Bay | 8.329% | 11.19% | 13.63% | 10.46% | 9.527% | 13.64% | 18.89% | 14.34% | 0.01578% | 0.005955% | 0.02079% | 0.006051%
PSP-Business-Other_Commercial_Buildings-Miscellaneous_Equipment | PSP | Non-Residential | Other_Commercial_Buildings | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Commercial_Buildings-Other_Plug_Loads | PSP | Non-Residential | Other_Commercial_Buildings | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Commercial_Buildings-Refrigeration | PSP | Non-Residential | Other_Commercial_Buildings | Refrigeration | 6.995% | 8.075% | 18.08% | 6.354% | 9.079% | 18.02% | 14.68% | 18.72% | 0.01239% | 0.01206% | 0.0125% | 0.01222%
PSP-Business-Other_Hotel_Motel-Computer_Equipment | PSP | Non-Residential | Other_Hotel_Motel | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Hotel_Motel-Cooking | PSP | Non-Residential | Other_Hotel_Motel | Cooking | 9.067% | 10.18% | 13.91% | 8.166% | 11.55% | 13.73% | 18.78% | 14.62% | 0.01626% | 0.01651% | 0.01753% | 0.01695%
PSP-Business-Other_Hotel_Motel-Cooling_Chillers | PSP | Non-Residential | Other_Hotel_Motel | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Other_Hotel_Motel-Cooling_DX | PSP | Non-Residential | Other_Hotel_Motel | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Other_Hotel_Motel-Domestic_Hot_Water | PSP | Non-Residential | Other_Hotel_Motel | Domestic_Hot_Water | 9.371% | 10.65% | 18.72% | 6.076% | 9.066% | 13.84% | 16.12% | 16.16% | 0.0118% | 0.01659% | 0.01195% | 0.01799%
PSP-Business-Other_Hotel_Motel-Elevators | PSP | Non-Residential | Other_Hotel_Motel | Elevators | 7.711% | 8.619% | 16.83% | 6.711% | 10.01% | 16.71% | 15.94% | 17.47% | 0.01391% | 0.01495% | 0.01498% | 0.01498%
PSP-Business-Other_Hotel_Motel-HVAC_Fans_Pumps | PSP | Non-Residential | Other_Hotel_Motel | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Other_Hotel_Motel-Lighting_Exterior | PSP | Non-Residential | Other_Hotel_Motel | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Other_Hotel_Motel-Lighting_Interior_Architectural | PSP | Non-Residential | Other_Hotel_Motel | Lighting_Interior_Architectural | 7.85% | 8.187% | 17.12% | 5.784% | 10.64% | 17.02% | 15.65% | 17.75% | 0.01208% | 0.01454% | 0.01402% | 0.01514%
PSP-Business-Other_Hotel_Motel-Lighting_Interior_General | PSP | Non-Residential | Other_Hotel_Motel | Lighting_Interior_General | 7.85% | 8.187% | 17.12% | 5.784% | 10.64% | 17.02% | 15.65% | 17.75% | 0.01208% | 0.01454% | 0.01402% | 0.01514%
PSP-Business-Other_Hotel_Motel-Lighting_Interior_High_Bay | PSP | Non-Residential | Other_Hotel_Motel | Lighting_Interior_High_Bay | 7.85% | 8.187% | 17.12% | 5.784% | 10.64% | 17.02% | 15.65% | 17.75% | 0.01208% | 0.01454% | 0.01402% | 0.01514%
PSP-Business-Other_Hotel_Motel-Miscellaneous_Equipment | PSP | Non-Residential | Other_Hotel_Motel | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Hotel_Motel-Other_Plug_Loads | PSP | Non-Residential | Other_Hotel_Motel | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Hotel_Motel-Refrigeration | PSP | Non-Residential | Other_Hotel_Motel | Refrigeration | 7% | 8.041% | 18.12% | 6.274% | 9.129% | 18.03% | 14.68% | 18.73% | 0.01225% | 0.01197% | 0.0123% | 0.01206%
PSP-Business-Other_Non_Food_Retail-Computer_Equipment | PSP | Non-Residential | Other_Non_Food_Retail | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Non_Food_Retail-Cooking | PSP | Non-Residential | Other_Non_Food_Retail | Cooking | 12.49% | 13.86% | 6.578% | 14.11% | 12.87% | 6.918% | 25.4% | 7.776% | 0.02495% | 0.01001% | 0.02843% | 0.01653%
PSP-Business-Other_Non_Food_Retail-Cooling_Chillers | PSP | Non-Residential | Other_Non_Food_Retail | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Other_Non_Food_Retail-Cooling_DX | PSP | Non-Residential | Other_Non_Food_Retail | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Other_Non_Food_Retail-Domestic_Hot_Water | PSP | Non-Residential | Other_Non_Food_Retail | Domestic_Hot_Water | 10.65% | 12.19% | 15.79% | 7.374% | 9.899% | 11.89% | 18.39% | 13.82% | 0.01432% | 0.01975% | 0.0145% | 0.02086%
PSP-Business-Other_Non_Food_Retail-Elevators | PSP | Non-Residential | Other_Non_Food_Retail | Elevators | 9.544% | 10.67% | 12.83% | 9.888% | 10.81% | 12.96% | 19.57% | 13.72% | 0.01853% | 0.01207% | 0.01939% | 0.01521%
PSP-Business-Other_Non_Food_Retail-HVAC_Fans_Pumps | PSP | Non-Residential | Other_Non_Food_Retail | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Other_Non_Food_Retail-Lighting_Exterior | PSP | Non-Residential | Other_Non_Food_Retail | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Other_Non_Food_Retail-Lighting_Interior_Architectural | PSP | Non-Residential | Other_Non_Food_Retail | Lighting_Interior_Architectural | 9.548% | 10.81% | 12.69% | 9.5% | 11.35% | 12.79% | 19.69% | 13.62% | 0.01844% | 0.01353% | 0.01863% | 0.0175%
PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | PSP | Non-Residential | Other_Non_Food_Retail | Lighting_Interior_General | 9.548% | 10.81% | 12.69% | 9.5% | 11.35% | 12.79% | 19.69% | 13.62% | 0.01844% | 0.01353% | 0.01863% | 0.0175%
PSP-Business-Other_Non_Food_Retail-Lighting_Interior_High_Bay | PSP | Non-Residential | Other_Non_Food_Retail | Lighting_Interior_High_Bay | 9.548% | 10.81% | 12.69% | 9.5% | 11.35% | 12.79% | 19.69% | 13.62% | 0.01844% | 0.01353% | 0.01863% | 0.0175%
PSP-Business-Other_Non_Food_Retail-Miscellaneous_Equipment | PSP | Non-Residential | Other_Non_Food_Retail | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Non_Food_Retail-Other_Plug_Loads | PSP | Non-Residential | Other_Non_Food_Retail | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Non_Food_Retail-Refrigeration | PSP | Non-Residential | Other_Non_Food_Retail | Refrigeration | 6.996% | 8.077% | 18.07% | 6.355% | 9.081% | 18.03% | 14.69% | 18.71% | 0.01239% | 0.01201% | 0.0125% | 0.01222%
PSP-Business-Other_Office-Computer_Equipment | PSP | Non-Residential | Other_Office | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Office-Cooking | PSP | Non-Residential | Other_Office | Cooking | 11.86% | 12.64% | 8.224% | 12.57% | 12.26% | 9.3% | 23.63% | 9.509% | 0.01995% | 0.007396% | 0.02674% | 0.01088%
PSP-Business-Other_Office-Cooling_Chillers | PSP | Non-Residential | Other_Office | Cooling_Chillers | 0% | 0% | 0% | 28.47% | 26.31% | 40.47% | 2.577% | 2.168% | 0.08049% | 0% | 0.104% | 0%
PSP-Business-Other_Office-Cooling_DX | PSP | Non-Residential | Other_Office | Cooling_DX | 0% | 0% | 0% | 28.47% | 26.31% | 40.47% | 2.577% | 2.168% | 0.08049% | 0% | 0.104% | 0%
PSP-Business-Other_Office-Domestic_Hot_Water | PSP | Non-Residential | Other_Office | Domestic_Hot_Water | 8.358% | 9.637% | 20.72% | 5.779% | 7.835% | 15.41% | 14.52% | 17.75% | 0.01079% | 0.01238% | 0.01143% | 0.01343%
PSP-Business-Other_Office-Elevators | PSP | Non-Residential | Other_Office | Elevators | 8.822% | 9.779% | 14.37% | 8.758% | 10.17% | 14.79% | 18.03% | 15.28% | 0.01521% | 0.009915% | 0.01818% | 0.01135%
PSP-Business-Other_Office-HVAC_Fans_Pumps | PSP | Non-Residential | Other_Office | HVAC_Fans_Pumps | 7.949% | 9.085% | 16.13% | 6.978% | 10.47% | 16% | 16.62% | 16.76% | 0.01368% | 0.01363% | 0.01368% | 0.01368%
PSP-Business-Other_Office-Lighting_Exterior | PSP | Non-Residential | Other_Office | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Other_Office-Lighting_Interior_Architectural | PSP | Non-Residential | Other_Office | Lighting_Interior_Architectural | 10.21% | 11.46% | 11.23% | 9.314% | 12.69% | 11.84% | 20.95% | 12.3% | 0.01786% | 0.01562% | 0.01864% | 0.01709%
PSP-Business-Other_Office-Lighting_Interior_General | PSP | Non-Residential | Other_Office | Lighting_Interior_General | 10.21% | 11.46% | 11.23% | 9.314% | 12.69% | 11.84% | 20.95% | 12.3% | 0.01786% | 0.01562% | 0.01864% | 0.01709%
PSP-Business-Other_Office-Lighting_Interior_High_Bay | PSP | Non-Residential | Other_Office | Lighting_Interior_High_Bay | 10.21% | 11.46% | 11.23% | 9.314% | 12.69% | 11.84% | 20.95% | 12.3% | 0.01786% | 0.01562% | 0.01864% | 0.01709%
PSP-Business-Other_Office-Miscellaneous_Equipment | PSP | Non-Residential | Other_Office | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Office-Other_Plug_Loads | PSP | Non-Residential | Other_Office | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Other_Office-Refrigeration | PSP | Non-Residential | Other_Office | Refrigeration | 6.889% | 8.046% | 18.2% | 6.377% | 8.902% | 18.19% | 14.56% | 18.84% | 0.01194% | 0.01088% | 0.01275% | 0.0109%
PSP-Business-Restaurant-Computer_Equipment | PSP | Non-Residential | Restaurant | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Restaurant-Cooking | PSP | Non-Residential | Restaurant | Cooking | 9.06% | 11.02% | 13.16% | 9.046% | 11.52% | 12.95% | 19.37% | 13.86% | 0.01922% | 0.01893% | 0.0205% | 0.0198%
PSP-Business-Restaurant-Cooling_Chillers | PSP | Non-Residential | Restaurant | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Restaurant-Cooling_DX | PSP | Non-Residential | Restaurant | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Restaurant-Domestic_Hot_Water | PSP | Non-Residential | Restaurant | Domestic_Hot_Water | 10.23% | 12.85% | 15.73% | 7.657% | 9.805% | 11.59% | 18.59% | 13.54% | 0.0168% | 0.0247% | 0.01823% | 0.0271%
PSP-Business-Restaurant-Elevators | PSP | Non-Residential | Restaurant | Elevators | 7.768% | 9.511% | 15.92% | 7.647% | 10.05% | 15.78% | 16.75% | 16.57% | 0.0156% | 0.01513% | 0.01572% | 0.01552%
PSP-Business-Restaurant-HVAC_Fans_Pumps | PSP | Non-Residential | Restaurant | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Restaurant-Lighting_Exterior | PSP | Non-Residential | Restaurant | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Restaurant-Lighting_Interior_Architectural | PSP | Non-Residential | Restaurant | Lighting_Interior_Architectural | 7.985% | 10.09% | 15.14% | 7.984% | 10.53% | 14.98% | 17.49% | 15.8% | 0.01639% | 0.0163% | 0.01643% | 0.0164%
PSP-Business-Restaurant-Lighting_Interior_General | PSP | Non-Residential | Restaurant | Lighting_Interior_General | 7.985% | 10.09% | 15.14% | 7.984% | 10.53% | 14.98% | 17.49% | 15.8% | 0.01639% | 0.0163% | 0.01643% | 0.0164%
PSP-Business-Restaurant-Lighting_Interior_High_Bay | PSP | Non-Residential | Restaurant | Lighting_Interior_High_Bay | 7.985% | 10.09% | 15.14% | 7.984% | 10.53% | 14.98% | 17.49% | 15.8% | 0.01639% | 0.0163% | 0.01643% | 0.0164%
PSP-Business-Restaurant-Miscellaneous_Equipment | PSP | Non-Residential | Restaurant | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Restaurant-Other_Plug_Loads | PSP | Non-Residential | Restaurant | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Restaurant-Refrigeration | PSP | Non-Residential | Restaurant | Refrigeration | 6.844% | 8.043% | 18.28% | 6.26% | 8.986% | 18.2% | 14.5% | 18.89% | 0.01243% | 0.01215% | 0.01254% | 0.0123%
PSP-Business-Schools-Computer_Equipment | PSP | Non-Residential | Schools | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Schools-Cooking | PSP | Non-Residential | Schools | Cooking | 14.79% | 13.09% | 9.634% | 7.134% | 8.292% | 6.341% | 29.25% | 11.47% | 0.004962% | 0.001652% | 0.0245% | 0.002118%
PSP-Business-Schools-Cooling_Chillers | PSP | Non-Residential | Schools | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Schools-Cooling_DX | PSP | Non-Residential | Schools | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Schools-Domestic_Hot_Water | PSP | Non-Residential | Schools | Domestic_Hot_Water | 12.97% | 15.31% | 8.724% | 12.15% | 11.19% | 7.122% | 24.79% | 7.753% | 0.01752% | 0.00717% | 0.0267% | 0.01032%
PSP-Business-Schools-Elevators | PSP | Non-Residential | Schools | Elevators | 12.15% | 10.45% | 15.45% | 4.695% | 6.894% | 10.71% | 23.05% | 16.61% | 0.003389% | 0.007873% | 0.01648% | 0.007892%
PSP-Business-Schools-HVAC_Fans_Pumps | PSP | Non-Residential | Schools | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Schools-Lighting_Exterior | PSP | Non-Residential | Schools | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Schools-Lighting_Interior_Architectural | PSP | Non-Residential | Schools | Lighting_Interior_Architectural | 12.29% | 12.93% | 12.51% | 6.641% | 6.942% | 8.536% | 26.14% | 14.01% | 0.00503% | 0.004676% | 0.0222% | 0.004883%
PSP-Business-Schools-Lighting_Interior_General | PSP | Non-Residential | Schools | Lighting_Interior_General | 12.29% | 12.93% | 12.51% | 6.641% | 6.942% | 8.536% | 26.14% | 14.01% | 0.00503% | 0.004676% | 0.0222% | 0.004883%
PSP-Business-Schools-Lighting_Interior_High_Bay | PSP | Non-Residential | Schools | Lighting_Interior_High_Bay | 12.29% | 12.93% | 12.51% | 6.641% | 6.942% | 8.536% | 26.14% | 14.01% | 0.00503% | 0.004676% | 0.0222% | 0.004883%
PSP-Business-Schools-Miscellaneous_Equipment | PSP | Non-Residential | Schools | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Schools-Other_Plug_Loads | PSP | Non-Residential | Schools | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Schools-Refrigeration | PSP | Non-Residential | Schools | Refrigeration | 6.892% | 8.05% | 18.19% | 6.38% | 8.906% | 18.18% | 14.56% | 18.83% | 0.01194% | 0.01088% | 0.01276% | 0.01091%
PSP-Business-University_Colleges-Computer_Equipment | PSP | Non-Residential | University_Colleges | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-University_Colleges-Cooking | PSP | Non-Residential | University_Colleges | Cooking | 11.73% | 12.09% | 9.63% | 10.37% | 10.8% | 9.227% | 24.93% | 11.22% | 0.01803% | 0.01403% | 0.02772% | 0.0198%
PSP-Business-University_Colleges-Cooling_Chillers | PSP | Non-Residential | University_Colleges | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-University_Colleges-Cooling_DX | PSP | Non-Residential | University_Colleges | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-University_Colleges-Domestic_Hot_Water | PSP | Non-Residential | University_Colleges | Domestic_Hot_Water | 13.33% | 14.04% | 9.831% | 9.237% | 13.23% | 7.827% | 23.86% | 8.648% | 0.01729% | 0.02003% | 0.01842% | 0.02433%
PSP-Business-University_Colleges-Elevators | PSP | Non-Residential | University_Colleges | Elevators | 9.951% | 10.38% | 14.88% | 7.652% | 8.98% | 11.62% | 20.66% | 15.87% | 0.01198% | 0.01274% | 0.01761% | 0.01555%
PSP-Business-University_Colleges-HVAC_Fans_Pumps | PSP | Non-Residential | University_Colleges | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-University_Colleges-Lighting_Exterior | PSP | Non-Residential | University_Colleges | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-University_Colleges-Lighting_Interior_Architectural | PSP | Non-Residential | University_Colleges | Lighting_Interior_Architectural | 9.744% | 11% | 14.38% | 8.403% | 8.806% | 11.2% | 21.11% | 15.37% | 0.01317% | 0.01175% | 0.01826% | 0.0137%
PSP-Business-University_Colleges-Lighting_Interior_General | PSP | Non-Residential | University_Colleges | Lighting_Interior_General | 9.744% | 11% | 14.38% | 8.403% | 8.806% | 11.2% | 21.11% | 15.37% | 0.01317% | 0.01175% | 0.01826% | 0.0137%
PSP-Business-University_Colleges-Lighting_Interior_High_Bay | PSP | Non-Residential | University_Colleges | Lighting_Interior_High_Bay | 9.744% | 11% | 14.38% | 8.403% | 8.806% | 11.2% | 21.11% | 15.37% | 0.01317% | 0.01175% | 0.01826% | 0.0137%
PSP-Business-University_Colleges-Miscellaneous_Equipment | PSP | Non-Residential | University_Colleges | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-University_Colleges-Other_Plug_Loads | PSP | Non-Residential | University_Colleges | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-University_Colleges-Refrigeration | PSP | Non-Residential | University_Colleges | Refrigeration | 6.892% | 8.05% | 18.19% | 6.38% | 8.906% | 18.18% | 14.56% | 18.83% | 0.01194% | 0.01088% | 0.01276% | 0.01091%
PSP-Business-Warehouse_Wholesale-Computer_Equipment | PSP | Non-Residential | Warehouse_Wholesale | Computer_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Warehouse_Wholesale-Cooking | PSP | Non-Residential | Warehouse_Wholesale | Cooking | 12.04% | 14.95% | 5.963% | 14.98% | 12.67% | 6.333% | 26.04% | 7.029% | 0.0223% | 0.005256% | 0.03186% | 0.006827%
PSP-Business-Warehouse_Wholesale-Cooling_Chillers | PSP | Non-Residential | Warehouse_Wholesale | Cooling_Chillers | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Warehouse_Wholesale-Cooling_DX | PSP | Non-Residential | Warehouse_Wholesale | Cooling_DX | 0% | 0% | 0% | 24.01% | 32.37% | 38.88% | 2.648% | 2.097% | 0.07059% | 0% | 0.08797% | 0%
PSP-Business-Warehouse_Wholesale-Domestic_Hot_Water | PSP | Non-Residential | Warehouse_Wholesale | Domestic_Hot_Water | 12.47% | 13.37% | 12.83% | 9.251% | 10.29% | 9.703% | 20.81% | 11.27% | 0.01701% | 0.01411% | 0.01877% | 0.01921%
PSP-Business-Warehouse_Wholesale-Elevators | PSP | Non-Residential | Warehouse_Wholesale | Elevators | 10.46% | 11.78% | 10.8% | 11.01% | 11.76% | 11.01% | 21.5% | 11.68% | 0.01967% | 0.01113% | 0.02158% | 0.01328%
PSP-Business-Warehouse_Wholesale-HVAC_Fans_Pumps | PSP | Non-Residential | Warehouse_Wholesale | HVAC_Fans_Pumps | 7.263% | 9.192% | 14.73% | 8.369% | 11.21% | 15.81% | 17.34% | 16.08% | 0.01643% | 0.01219% | 0.01643% | 0.01244%
PSP-Business-Warehouse_Wholesale-Lighting_Exterior | PSP | Non-Residential | Warehouse_Wholesale | Lighting_Exterior | 5.335% | 4.241% | 27.98% | 0.561% | 3.786% | 24.69% | 6.721% | 26.68% | 0.0011% | 0.02114% | 0.0011% | 0.02189%
PSP-Business-Warehouse_Wholesale-Lighting_Interior_Architectural | PSP | Non-Residential | Warehouse_Wholesale | Lighting_Interior_Architectural | 10.44% | 12.48% | 10.09% | 11.92% | 11.56% | 10.33% | 22.16% | 11.02% | 0.01965% | 0.008512% | 0.02402% | 0.0102%
PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | PSP | Non-Residential | Warehouse_Wholesale | Lighting_Interior_General | 10.44% | 12.48% | 10.09% | 11.92% | 11.56% | 10.33% | 22.16% | 11.02% | 0.01965% | 0.008512% | 0.02402% | 0.0102%
PSP-Business-Warehouse_Wholesale-Lighting_Interior_High_Bay | PSP | Non-Residential | Warehouse_Wholesale | Lighting_Interior_High_Bay | 10.44% | 12.48% | 10.09% | 11.92% | 11.56% | 10.33% | 22.16% | 11.02% | 0.01965% | 0.008512% | 0.02402% | 0.0102%
PSP-Business-Warehouse_Wholesale-Miscellaneous_Equipment | PSP | Non-Residential | Warehouse_Wholesale | Miscellaneous_Equipment | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Warehouse_Wholesale-Other_Plug_Loads | PSP | Non-Residential | Warehouse_Wholesale | Other_Plug_Loads | 7.216% | 8.031% | 17.89% | 6.401% | 9.213% | 17.83% | 14.88% | 18.54% | 0.01253% | 0.01216% | 0.01255% | 0.01243%
PSP-Business-Warehouse_Wholesale-Refrigeration | PSP | Non-Residential | Warehouse_Wholesale | Refrigeration | 6.359% | 7.49% | 17.65% | 6.779% | 9.41% | 19.53% | 14% | 18.78% | 0.01343% | 0.01095% | 0.01397% | 0.01102%
PSP-Consumer-Residential-AC_Central | PSP | Residential | Residential | AC_Central | 0% | 0% | 0% | 20.65% | 27.89% | 49.26% | 0.7877% | 1.413% | 0.05635% | 0% | 0.123% | 0%
PSP-Consumer-Residential-AC_Room | PSP | Residential | Residential | AC_Room | 0% | 0% | 0% | 20.65% | 27.89% | 49.26% | 0.7877% | 1.413% | 0.05635% | 0% | 0.123% | 0%
PSP-Consumer-Residential-Attic Insulation - Electric Fired | PSP | Residential | Residential | Attic Insulation - Electric Fired | 14.02% | 13.01% | 41.08% | 0.8835% | 1.45% | 2.606% | 11.13% | 15.81% | 0.001331% | 0.0274% | 0.002576% | 0.03463%
PSP-Consumer-Residential-Attic Insulation - Gas Fired | PSP | Residential | Residential | Attic Insulation - Gas Fired | 3.489% | 3.987% | 9.962% | 12.85% | 17.81% | 33.27% | 7.669% | 10.96% | 0.03272% | 0.006005% | 0.06429% | 0.006005%
PSP-Consumer-Residential-Car_Block_Heater | PSP | Residential | Residential | Car_Block_Heater | 2.443% | 9.772% | 80.66% | 0.03267% | 0.1307% | 1.018% | 0.8451% | 5.1% | 0.00142% | 0% | 0.0004403% | 0%
PSP-Consumer-Residential-Clothes_Dryers | PSP | Residential | Residential | Clothes_Dryers | 9.705% | 11.21% | 15.73% | 7.47% | 9.947% | 12.43% | 18.52% | 14.99% | 0.01353% | 0.01631% | 0.02016% | 0.01851%
PSP-Consumer-Residential-Clothes_Washers | PSP | Residential | Residential | Clothes_Washers | 10.25% | 8.417% | 17.35% | 5.806% | 9.725% | 13.7% | 17.48% | 17.27% | 0.01117% | 0.01335% | 0.01552% | 0.01581%
PSP-Consumer-Residential-Clothesline | PSP | Residential | Residential | Clothesline | 0% | 0% | 0% | 34.43% | 34.43% | 30.33% | 0.8197% | 0% | 0.06831% | 0% | 0.06831% | 0%
PSP-Consumer-Residential-Computers | PSP | Residential | Residential | Computers | 6.982% | 8.384% | 17.79% | 5.67% | 10.09% | 17.6% | 15.02% | 18.46% | 0.01436% | 0.01849% | 0.01846% | 0.01854%
PSP-Consumer-Residential-Cooking | PSP | Residential | Residential | Cooking | 11.07% | 9.279% | 16.21% | 6.694% | 9.963% | 12.56% | 18.49% | 15.74% | 0.01933% | 0.024% | 0.03268% | 0.03402%
PSP-Consumer-Residential-Dehumidifiers | PSP | Residential | Residential | Dehumidifiers | 4.48% | 6.141% | 9.432% | 12.1% | 16.64% | 30.52% | 10.32% | 10.36% | 0.03055% | 0.01034% | 0.06121% | 0.0108%
PSP-Consumer-Residential-Dishwashers | PSP | Residential | Residential | Dishwashers | 10.67% | 9.096% | 15.98% | 5.103% | 12.11% | 13.3% | 18.08% | 15.66% | 0.01177% | 0.02615% | 0.02109% | 0.02765%
PSP-Consumer-Residential-Domestic_Hot_Water | PSP | Residential | Residential | Domestic_Hot_Water | 10.44% | 7.981% | 20.4% | 4.238% | 9.24% | 14.3% | 15.38% | 18.03% | 0.009069% | 0.01642% | 0.01187% | 0.01693%
PSP-Consumer-Residential-Duct Sealing - Electric Fired | PSP | Residential | Residential | Duct Sealing - Electric Fired | 13.41% | 12.49% | 39.28% | 1.584% | 2.407% | 4.393% | 10.92% | 15.52% | 0.003173% | 0.02616% | 0.00622% | 0.03297%
PSP-Consumer-Residential-Duct Sealing - Gas Fired, ECM | PSP | Residential | Residential | Duct Sealing - Gas Fired, ECM | 3.962% | 4.529% | 11.31% | 11.79% | 16.44% | 31.1% | 8.604% | 12.25% | 0.02951% | 0.00682% | 0.05632% | 0.00682%
PSP-Consumer-Residential-Duct Sealing - Gas Fired, PSC | PSP | Residential | Residential | Duct Sealing - Gas Fired, PSC | 2.751% | 3.144% | 7.855% | 14.5% | 19.94% | 36.66% | 6.214% | 8.938% | 0.03771% | 0.004735% | 0.0767% | 0.004735%
PSP-Consumer-Residential-Elevators | PSP | Residential | Residential | Elevators | 9.705% | 11.21% | 15.73% | 7.47% | 9.947% | 12.43% | 18.52% | 14.99% | 0.01353% | 0.01631% | 0.02016% | 0.01851%
PSP-Consumer-Residential-Energy Star Windows - Electric Fired | PSP | Residential | Residential | Energy Star Windows - Electric Fired | 13.66% | 12.7% | 39.99% | 1.285% | 2.002% | 3.652% | 11.04% | 15.68% | 0.002371% | 0.02664% | 0.004569% | 0.03361%
PSP-Consumer-Residential-Energy Star Windows - Gas Fired, ECM | PSP | Residential | Residential | Energy Star Windows - Gas Fired, ECM | 4.232% | 4.837% | 12.08% | 11.19% | 15.67% | 29.87% | 9.136% | 12.99% | 0.02768% | 0.007284% | 0.05178% | 0.007284%
PSP-Consumer-Residential-Energy Star Windows - Gas Fired, PSC | PSP | Residential | Residential | Energy Star Windows - Gas Fired, PSC | 2.84% | 3.246% | 8.111% | 14.3% | 19.69% | 36.24% | 6.39% | 9.183% | 0.03711% | 0.004889% | 0.07519% | 0.004889%
PSP-Consumer-Residential-Forced_Air_Central_Heating | PSP | Residential | Residential | Forced_Air_Central_Heating | 14.46% | 13.39% | 42.38% | 0.3842% | 0.7676% | 1.326% | 11.28% | 16.02% | 0.0002306% | 0.02829% | 0.0002056% | 0.03582%
PSP-Consumer-Residential-Freezers | PSP | Residential | Residential | Freezers | 6.296% | 7.551% | 17.4% | 6.72% | 9.543% | 19.94% | 13.95% | 18.59% | 0.01357% | 0.01126% | 0.01414% | 0.01135%
PSP-Consumer-Residential-Furnace_ECM_1 | PSP | Residential | Residential | Furnace_ECM_1 | 10.55% | 10.48% | 30.66% | 3.103% | 4.75% | 10.1% | 12.57% | 17.79% | 0.005718% | 0.01985% | 0.005811% | 0.02362%
PSP-Consumer-Residential-Furnace_ECM_2 | PSP | Residential | Residential | Furnace_ECM_2 | 14.46% | 13.39% | 42.38% | 0.3842% | 0.7676% | 1.326% | 11.28% | 16.02% | 0.0002306% | 0.02829% | 0.0002056% | 0.03582%
PSP-Consumer-Residential-Furnace_ECM_3 | PSP | Residential | Residential | Furnace_ECM_3 | 7.232% | 6.695% | 21.19% | 10.52% | 14.33% | 25.29% | 6.032% | 8.715% | 0.02819% | 0.01414% | 0.06148% | 0.01791%
PSP-Consumer-Residential-Holiday_Lighting_Timer | PSP | Residential | Residential | Holiday_Lighting_Timer | 29.31% | 0% | 43.44% | 0% | 0% | 0% | 11.12% | 16.12% | 0% | 0.2413% | 0% | 0.1582%
PSP-Consumer-Residential-Lighting | PSP | Residential | Residential | Lighting | 9.307% | 8.837% | 19.59% | 2.403% | 10.45% | 15.56% | 15.19% | 18.66% | 0.006444% | 0.02893% | 0.01801% | 0.03109%
PSP-Consumer-Residential-Lighting_Common_Area | PSP | Residential | Residential | Lighting_Common_Area | 9.376% | 8.893% | 19.48% | 2.207% | 9.577% | 16.57% | 15.42% | 18.48% | 0.004777% | 0.02894% | 0.008945% | 0.03109%
PSP-Consumer-Residential-Miscellaneous | PSP | Residential | Residential | Miscellaneous | 6.632% | 7.58% | 18.94% | 5.822% | 8.733% | 18.87% | 13.87% | 19.55% | 0.01142% | 0.01142% | 0.01142% | 0.01142%
PSP-Consumer-Residential-Non_Ducted_Central_Heating | PSP | Residential | Residential | Non_Ducted_Central_Heating | 14.46% | 13.39% | 42.38% | 0.3842% | 0.7676% | 1.326% | 11.28% | 16.02% | 0.0002306% | 0.02829% | 0.0002056% | 0.03582%
PSP-Consumer-Residential-On_Site_Generation | PSP | Residential | Residential | On_Site_Generation | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
PSP-Consumer-Residential-Other_Consumer_Electronics | PSP | Residential | Residential | Other_Consumer_Electronics | 6.632% | 7.58% | 18.94% | 5.822% | 8.733% | 18.87% | 13.87% | 19.55% | 0.01142% | 0.01142% | 0.01142% | 0.01142%
PSP-Consumer-Residential-Outdoor Solar Lighting | PSP | Residential | Residential | Outdoor Solar Lighting | 0% | 0.1192% | 0.2385% | 0% | 12.49% | 64.77% | 4.799% | 17.59% | 0% | 0% | 0% | 0%
PSP-Consumer-Residential-Power_Bar | PSP | Residential | Residential | Power_Bar | 7.39% | 2.603% | 23.13% | 2.502% | 7.729% | 23.17% | 9.774% | 23.7% | 0.002877% | 6.594e-05% | 0.006737% | 9.111e-05%
PSP-Consumer-Residential-Refrigerators | PSP | Residential | Residential | Refrigerators | 6.353% | 6.976% | 17.52% | 6.1% | 9.791% | 20.32% | 13.75% | 19.19% | 0.01291% | 0.0124% | 0.01445% | 0.01284%
PSP-Consumer-Residential-Set_Top_Boxes | PSP | Residential | Residential | Set_Top_Boxes | 6.982% | 8.384% | 17.79% | 5.67% | 10.09% | 17.6% | 15.02% | 18.46% | 0.01436% | 0.01849% | 0.01846% | 0.01854%
PSP-Consumer-Residential-Space_Heating_Room | PSP | Residential | Residential | Space_Heating_Room | 14.46% | 13.39% | 42.38% | 0.3842% | 0.7676% | 1.326% | 11.28% | 16.02% | 0.0002306% | 0.02829% | 0.0002056% | 0.03582%
PSP-Consumer-Residential-Swimming_Pool_And_Spa_Heaters | PSP | Residential | Residential | Swimming_Pool_And_Spa_Heaters | 8.591% | 8.18% | 16.39% | 5.763% | 11.45% | 16.13% | 16.41% | 17.09% | 0.01821% | 0.02576% | 0.02683% | 0.02688%
PSP-Consumer-Residential-Swimming_Pool_Pumps | PSP | Residential | Residential | Swimming_Pool_Pumps | 8.591% | 8.18% | 16.39% | 5.763% | 11.45% | 16.13% | 16.41% | 17.09% | 0.01821% | 0.02576% | 0.02683% | 0.02688%
PSP-Consumer-Residential-Televisions | PSP | Residential | Residential | Televisions | 6.982% | 8.384% | 17.79% | 5.67% | 10.09% | 17.6% | 15.02% | 18.46% | 0.01436% | 0.01849% | 0.01846% | 0.01854%
PSP-Consumer-Residential-Ventilation_And_Circulation | PSP | Residential | Residential | Ventilation_And_Circulation | 6.632% | 7.58% | 18.94% | 5.822% | 8.733% | 18.87% | 13.87% | 19.55% | 0.01142% | 0.01142% | 0.01142% | 0.01142%
PSP-Consumer-Residential-Water_Heater_Blanket | PSP | Residential | Residential | Water_Heater_Blanket | 9.923% | 9.998% | 15.68% | 5.173% | 10.66% | 13.15% | 19.19% | 16.22% | 0.01034% | 0.01837% | 0.01664% | 0.02175%
PSP-Consumer-Residential-Weatherstripping | PSP | Residential | Residential | Weatherstripping | 14.17% | 13.12% | 41.51% | 0.7984% | 1.322% | 2.306% | 11.06% | 15.72% | 0.001172% | 0.02771% | 0.002513% | 0.03509%
PSP-Consumer-Residential-Window Solar Film - Electric Fired | PSP | Residential | Residential | Window Solar Film - Electric Fired | 13.67% | 12.72% | 40.04% | 1.265% | 1.975% | 3.602% | 11.04% | 15.69% | 0.002318% | 0.02668% | 0.004464% | 0.03366%
PSP-Consumer-Residential-Window Solar Film - Gas Fired | PSP | Residential | Residential | Window Solar Film - Gas Fired | 3.61% | 4.126% | 10.31% | 12.58% | 17.46% | 32.72% | 7.909% | 11.29% | 0.03189% | 0.006214% | 0.06224% | 0.006214%
PSP-Consumer-Residential-Forced_Air_Central_Heating | PSP | Consumer | Residential | Forced_Air_Central_Heating | 14.01% | 13% | 41.44% | 0.4082% | 0.8252% | 1.51% | 12.02% | 16.78% | 0.001178% | 0.0277% | 0.002007% | 0.03582%
PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | PSP | Industrial | Miscellaneous_Industrial | Compressed_Air | 6.817% | 7.778% | 18.49% | 6.141% | 8.746% | 18.49% | 14.25% | 19.29% | 0.01142% | 0.01062% | 0.0145% | 0.01131%
PSP-Industrial-Miscellaneous_Industrial-Motors_Pumps | PSP | Industrial | Miscellaneous_Industrial | Motors_Pumps | 6.817% | 7.778% | 18.49% | 6.141% | 8.746% | 18.49% | 14.25% | 19.29% | 0.01142% | 0.01062% | 0.0145% | 0.01131%
PSP-Industrial-Miscellaneous_Industrial-Other | PSP | Industrial | Miscellaneous_Industrial | Other | 6.632% | 7.58% | 18.94% | 5.822% | 8.733% | 18.87% | 13.87% | 19.55% | 0.01142% | 0.01142% | 0.01142% | 0.01142%
PSP-Industrial-Miscellaneous_Industrial-Process_Specific | PSP | Industrial | Miscellaneous_Industrial | Process_Specific | 6.817% | 7.778% | 18.49% | 6.141% | 8.746% | 18.49% | 14.25% | 19.29% | 0.01142% | 0.01062% | 0.0145% | 0.01131%
PSP-Industrial-Agriculture-Process_Specific | PSP | Industrial | Agriculture | Process_Specific | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
PSP-Industrial-Agriculture-Process_Heating | PSP | Industrial | Agriculture | Process_Heating | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
PSP-Industrial-Agriculture-Other | PSP | Industrial | Agriculture | Other | 6.632% | 7.58% | 18.94% | 5.822% | 8.733% | 18.87% | 13.87% | 19.55% | 0.01142% | 0.01142% | 0.01142% | 0.01142%
PSP-Industrial-Agriculture-Process_Cooling | PSP | Industrial | Agriculture | Process_Cooling | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
PSP-Business-Food_Retail-CE_Space_Heating | PSP | Non-Residential | Food_Retail | CE_Space_Heating | 21.34% | 18.32% | 44.03% | 0.001363% | 0.04808% | 0.103% | 6.435% | 9.721% | 0% | 0.03291% | 0% | 0.04947%
PSP-Business-Hospital-CE_Space_Heating | PSP | Non-Residential | Hospital | CE_Space_Heating | 14.86% | 15.07% | 50.13% | 0.1415% | 0.4444% | 1.255% | 4.624% | 13.48% | 0.001437% | 0.02934% | 0.003921% | 0.04717%
PSP-Business-Large_Hotel-CE_Space_Heating | PSP | Non-Residential | Large_Hotel | CE_Space_Heating | 16.67% | 14.48% | 57.41% | -0.00018% | 0.00625% | 0.101% | 2.703% | 8.631% | 0% | 0.02807% | 0% | 0.0519%
PSP-Business-Large_Non_Food_Retail-CE_Space_Heating | PSP | Non-Residential | Large_Non_Food_Retail | CE_Space_Heating | 21.34% | 18.32% | 44.03% | 0.001363% | 0.04808% | 0.103% | 6.435% | 9.721% | 0% | 0.03291% | 0% | 0.04947%
PSP-Business-Large_Office-CE_Space_Heating | PSP | Non-Residential | Large_Office | CE_Space_Heating | 21.34% | 18.32% | 44.03% | 0.001363% | 0.04808% | 0.103% | 6.435% | 9.721% | 0% | 0.03291% | 0% | 0.04947%
PSP-Business-Nursing_Home-CE_Space_Heating | PSP | Non-Residential | Nursing_Home | CE_Space_Heating | 17.12% | 17.37% | 44.06% | 0.08654% | 0.2297% | 0.3096% | 7.898% | 12.92% | 0% | 0.02855% | 0% | 0.04216%
PSP-Business-Other_Commercial_Buildings-CE_Space_Heating | PSP | Non-Residential | Other_Commercial_Buildings | CE_Space_Heating | 16.53% | 18.89% | 47.84% | 0.0149% | 0.04677% | 0% | 7.897% | 8.782% | 0% | 0.01613% | 0% | 0.02626%
PSP-Business-Other_Hotel_Motel-CE_Space_Heating | PSP | Non-Residential | Other_Hotel_Motel | CE_Space_Heating | 15.79% | 16.48% | 52.44% | 0.01818% | 0.06444% | 0.2541% | 4.102% | 10.86% | 0% | 0.02808% | 0% | 0.04434%
PSP-Business-Other_Non_Food_Retail-CE_Space_Heating | PSP | Non-Residential | Other_Non_Food_Retail | CE_Space_Heating | 21.34% | 18.32% | 44.03% | 0.001363% | 0.04808% | 0.103% | 6.435% | 9.721% | 0% | 0.03291% | 0% | 0.04947%
PSP-Business-Other_Office-CE_Space_Heating | PSP | Non-Residential | Other_Office | CE_Space_Heating | 21.34% | 18.32% | 44.03% | 0.001363% | 0.04808% | 0.103% | 6.435% | 9.721% | 0% | 0.03291% | 0% | 0.04947%
PSP-Business-Restaurant-CE_Space_Heating | PSP | Non-Residential | Restaurant | CE_Space_Heating | 21.34% | 18.32% | 44.03% | 0.001363% | 0.04808% | 0.103% | 6.435% | 9.721% | 0% | 0.03291% | 0% | 0.04947%
PSP-Business-Schools-CE_Space_Heating | PSP | Non-Residential | Schools | CE_Space_Heating | 21.34% | 18.32% | 44.03% | 0.001363% | 0.04808% | 0.103% | 6.435% | 9.721% | 0% | 0.03291% | 0% | 0.04947%
PSP-Business-University_Colleges-CE_Space_Heating | PSP | Non-Residential | University_Colleges | CE_Space_Heating | 21.34% | 18.32% | 44.03% | 0.001363% | 0.04808% | 0.103% | 6.435% | 9.721% | 0% | 0.03291% | 0% | 0.04947%
PSP-Business-Warehouse_Wholesale-CE_Space_Heating | PSP | Non-Residential | Warehouse_Wholesale | CE_Space_Heating | 14.32% | 15.44% | 47.23% | 0.05249% | 0.1406% | 0.1979% | 7.005% | 15.61% | 0% | 0.02672% | 0% | 0.03598%
EM&V-Residential-Car_Block_Heater_North_Ontario | EM&V | Residential | Residential | Car_Block_Heater_North_Ontario | 0.12249 | 0.18373 | 0.67613 | 0 | 0 | 0 | 0.0069213 | 0.01072 | 0 | 0.00041693 | 0 | 0.0011702
EM&V-Residential-Car_Block_Heater_South_Ontario | EM&V | Residential | Residential | Car_Block_Heater_South_Ontario | 0.13388 | 0.20082 | 0.6653 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0024172 | 0 | 0.006734
EM&V-Residential-Clothesline_Outdoor | EM&V | Residential | Residential | Clothesline_Outdoor | 0 | 0 | 0 | 0.28561 | 0.32231 | 0.3524 | 0.020872 | 0.018803 | 0.00052732 | #DIV/0! | 0.00076147 | 0
EM&V-Residential-AC_Cooling | EM&V | Residential | Residential | AC_Cooling | 0 | 0 | 0 | 0.22401 | 0.30319 | 0.43819 | 0.018585 | 0.016028 | 0.00061714 | #DIV/0! | 0.0012005 | 0
EM&V-Residential-Cooling_and_Gas_Heating | EM&V | Residential | Residential | Cooling_and_Gas_Heating | 0.052201 | 0.057325 | 0.15736 | 0.13441 | 0.1845 | 0.29141 | 0.053257 | 0.069548 | 0.00035257 | 9.3051e-05 | 0.00062907 | 0.00014605
EM&V-Residential-Electric_Heating_and_Cooling | EM&V | Residential | Residential | Electric_Heating_and_Cooling | 0.078907 | 0.077434 | 0.18594 | 0.11416 | 0.15582 | 0.22643 | 0.07758 | 0.083725 | 0.00030888 | 0.00014911 | 0.00060023 | 0.00020152
EM&V-Residential-Electric_Heating_and_Ventilation | EM&V | Residential | Residential | Electric_Heating_and_Ventilation | 0.11207 | 0.11533 | 0.28063 | 0.031265 | 0.047891 | 0.10169 | 0.13764 | 0.17348 | 5.7384e-05 | 0.00020619 | 6.1513e-05 | 0.0002586
EM&V-Residential-Electric_Heating | EM&V | Residential | Residential | Electric_Heating | 0.15781 | 0.15487 | 0.37188 | 0.0043109 | 0.0084529 | 0.014675 | 0.13657 | 0.15142 | 5.0608e-06 | 0.00029823 | 8.8699e-06 | 0.00040304
EM&V-Residential-Lighting_Interior | EM&V | Residential | Residential | Lighting_Interior | 0.10452 | 0.089761 | 0.17925 | 0.027723 | 0.11058 | 0.15012 | 0.1631 | 0.17494 | 7.0266e-05 | 0.0002936 | 0.00018008 | 0.00031139
EM&V-Residential-Consumer_Electronics | EM&V | Residential | Residential | Consumer_Electronics | 0.073393 | 0.088453 | 0.17003 | 0.061527 | 0.10474 | 0.16795 | 0.15815 | 0.17576 | 0.00014734 | 0.00018483 | 0.00018457 | 0.00018536
EM&V-Commercial-HE_Ventilation_Exhaust_Fans | EM&V | Non-Residential | Commercial | HE_Ventilation_Exhaust_Fans | 0.024347 | 0.14608 | 0.078029 | 0.1496 | 0.19331 | 0.15195 | 0.16838 | 0.088296 | 0.00029334 | #DIV/0! | 0.00029334 | 0
EM&V-Commercial-Agricultural_Ground_Source_Heat_Pump | EM&V | Non-Residential | Commercial | Agricultural_Ground_Source_Heat_Pump | 0.12136 | 0.10834 | 0.23339 | 0.040552 | 0.038701 | 0.076865 | 0.16151 | 0.21929 | 6.705e-05 | 0.00013244 | 0.00010623 | 0.0002212
EM&V-Commercial-Cooling | EM&V | Non-Residential | Commercial | Cooling | 0 | 0 | 0 | 0.29796 | 0.31808 | 0.32873 | 0.038778 | 0.016454 | 0.00073323 | #DIV/0! | 0.00093499 | 0
EM&V-Commercial-Creep_Heat_Pad | EM&V | Non-Residential | Commercial | Creep_Heat_Pad | 0 | 0.10134 | 0.25321 | 0.019231 | 0.028846 | 0.061813 | 0.18544 | 0.26145 | 0 | 0.00015263 | 0 | 0.00015263
EM&V-Commercial-Dual_&_Natural_Ventilation_Fans_All_year | EM&V | Non-Residential | Commercial | Dual_&_Natural_Ventilation_Fans_All_year | 0.060637 | 0.072591 | 0.063229 | 0.073455 | 0.11018 | 0.23722 | 0.17384 | 0.20884 | 0.00014403 | 0.00014403 | 0.00014403 | 0.00014403
EM&V-Commercial-Dual_&_Natural_Ventilation_Fans_Winter_Only | EM&V | Non-Residential | Commercial | Dual_&_Natural_Ventilation_Fans_Winter_Only | 0.11936 | 0.1429 | 0.12107 | 0.0051035 | 0.0076552 | 0.0025517 | 0.33796 | 0.2634 | 0 | 0.00028353 | 0 | 0.00028353
EM&V-Commercial-Agricultural_Ground_Source_Heat_Pump | EM&V | Non-Residential | Commercial | Heating | 0.1648 | 0.15851 | 0.40119 | 0.035325 | 0.033403 | 0.042674 | 0.063849 | 0.10025 | 7.4487e-05 | 0.00024301 | 0.00013084 | 0.00041916
EM&V-Commercial-HT_Cut-Off_Thermostat | EM&V | Non-Residential | Commercial | HT_Cut-Off_Thermostat | 0 | 0 | 0 | 0.3595 | 0.30508 | 0.30508 | 0.012489 | 0.017841 | 0.00089206 | #DIV/0! | 0.00089206 | 0
EM&V-Commercial-HVAC_Fans_Pumps | EM&V | Non-Residential | Commercial | HVAC_Fans_Pumps | 0.064543 | 0.073764 | 0.19326 | 0.056597 | 0.084896 | 0.19284 | 0.13464 | 0.19945 | 0.00011102 | 0.00011093 | 0.00011416 | 0.00011416
EM&V-Commercial-HVLS_No_Summer_Operation | EM&V | Non-Residential | Commercial | HVLS_No_Summer_Operation | 0 | 0 | 0 | 0.16803 | 0.25205 | 0.55533 | 0.005123 | 0.019467 | 0.00034153 | #DIV/0! | 0.00034153 | 0
EM&V-Commercial-Low_Energy_Livestock_Waterers | EM&V | Non-Residential | Commercial | Low_Energy_Livestock_Waterers | 0.055096 | 0.11019 | 0.80992 | 0 | 0 | 0 | 0.0041322 | 0.020661 | 0 | #DIV/0! | 0 | 0
EM&V-Commercial-Space_Cooling_&_Heating | EM&V | Non-Residential | Commercial | Space_Cooling_&_Heating | 0.074431 | 0.070824 | 0.20369 | 0.10668 | 0.14535 | 0.24888 | 0.067245 | 0.082892 | 0.0002795 | 0.00014401 | 0.00059845 | 0.00019787
CUSTOM-Residential-Residential-Nightlight | CUSTOM | Residential | Residential | Nightlight | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0.125 | 0 | 0 | 0 | 0
CUSTOM-Business-Other_Commercial_Buildings-CUSTOM-Industrial-Agriculture-Horticultural Lighting - Veg | CUSTOM | Business | Other_Commercial_Buildings | CUSTOM-Industrial-Agriculture-Horticultural Lighting - Veg | 0.12546 | 0.10099 | 0.41528 | 0.010395 | 0.014352 | 0.035977 | 0.10776 | 0.18979 | 3.547e-06 | 1.1312e-05 | 1.2734e-05 | 6.0937e-05
CUSTOM-Business-Other_Commercial_Buildings-CUSTOM-Industrial-Agriculture-Horticultural Lighting - Cannabis | CUSTOM | Business | Other_Commercial_Buildings | CUSTOM-Industrial-Agriculture-Horticultural Lighting - Cannabis | 0.17793 | 0.22404 | 0.32257 | 0.011776 | 0.013235 | 0.019033 | 0.11853 | 0.11289 | 4.2498e-06 | 0.00017338 | 8.913e-06 | 0.00026569
Custom-Business-Cold Water_Booster_Pumps | Custom | Business | Cold Water | Booster Pumps | 0.090333 | 0.114 | 0.12233 | 0.099 | 0.13033 | 0.11367 | 0.20667 | 0.12367 | 6e-05 | 6.3333e-05 | 6e-05 | 6.3333e-05

## Revision History (hidden)
IESO Prescriptive Measures and Assumptions List January 2024
Version | Date Released | Sector | Major Changes/Revisions | Measures Revised/Added
2014 Measures and Assumptions List | January 2014 | Consumer | Updated input assumptions based on 2012 Evaluation Report | All measures
|  | Business | Aligned with program assumptions | All measures
Measures and Assumptions List - January 1, 2015 | January 2015 | Consumer | Updated kW and kWh savings for key province-wide measures based on 2013 Evaluation Report | All measures except Residential New Construction measures
|  | Consumer | Adjusted incremental life cycle cost to incorporate a discount rate. The discount rate is the rate at which future costs are discounted to establish their present value. | All lighting measures with base cases having effective useful life (EUL) less than the EUL of the conservation measure (e.g. incandescent lamps retrofitted with LED)
|  | Consumer | Updated net to gross ratios based on 2013 Consumer Program evaluation | All measures
|  | Business | Removed compact fluorescent lamps (CFL) measures since they are now the new base lighting measure | All CFL measures
|  | Business | Removed standard T8s since they are now the new base measure for linear fluorescents | All standard T8s linear fluorescent measures
|  | Business | Revised certain base measures from incandescent to CFL | All measures except base measures for LED light bulbs (e.g. MR, PAR)
|  | Business | Updated certain base measures from T12s to standard T8s | All high efficiency linear fluorescents (e.g. T8s, T5s)
|  | Business | Updated assumed annual operating hours and savings assumptions for unitary A/C measures based on 2013 business program evaluation | All unitary A/C measures
|  | Business | Adjusted incremental life cycle cost to incorporate a discount rate. The discount rate is the rate at which future costs are discounted to establish their present value. | All lighting measures with base cases having effective useful life (EUL) less than the EUL of the conservation measure (e.g. std T8s retrofitted with LED troffers)
|  | Business | Updated effective useful life (EUL) of lighting fixtures to consider ballast life (50,000 hours) | All linear fluorescent lighting fixtures
|  | Business | Updated assumed annual operating hours for Small Business Lighting measures | All lighting measures
|  | Business | Added new building types for the lighting measures to take into consideration their different operating hours. | All lighting measures. Building types include food retail, non-food retail, hospital, hotel, office, nursing home, restaurant, schools, universities, warehouses
|  | Business | Added new lighting prescriptive measures | LED troffers, exterior lighting, vapour/dust free fixtures, omni-directional A lamps
|  | Business | Added new non-lighting prescriptive measures | Building plug load, HVAC controls, refrigeration
|  | Business | Revised HVLS fans assumptions from a per 1000 cfm basis to a per unit (fan) basis | High volume low speed agribusiness fans
|  | Business | Updated net to gross ratios based on 2013 Business Program evaluation | All measures
Measures and Assumptions List - October 2015 |  | Consumer |  | Added "Attic Ventilation - Passive Mechanical" to list.
Measures and Assumptions List - May 2017 |  | Consumer | Updated Residential Measures with 2015 Verified Results
|  | Business | Major revisions and updates include: a) updating baseline and energy efficient case assumptions for all lighting measures; b) removed all prescriptive HPNC measures except for Agribusiness measures; and c) removed all Small Business Lighting measures.
Measures and Assumptions List - March 2018 |  | Consumer | ` Removed the Net-to-Gross Ratio tab. | Removed CFL measures not to be offered in future programs
|  | Consumer |  | Removed permutations of heating and cooling measures not relevant to the data tracking
|  | Consumer |  | Added various new LED lighting measures
|  | Consumer |  | Add Efficient Showerhead and Aerator measures
|  | Consumer |  | Add Smart Burner measure
|  | Consumer |  | Add Tier 1 and Tier 2 Smart Power Bar measures
|  | Consumer |  | Add Hot Water Pipe Wrap measure
|  | Consumer |  | Add Window Film measure
|  | Consumer |  | Add Energy Star Most Efficient TV measure
|  | Consumer |  | Add Energy Star Clothes Washer and Dryer measure
|  | Consumer |  | Delete CAC SEER 15 and add SEER 18 measure
|  | Consumer |  | Add Air Source Heat Pump measures
Measures and Assumptions List - February 2019 |  | Consumer | Updated Instant Discount measure input assumptions based on 2017 Consumer Program Evaluation, changes to programs and additional IESO research. | a) increased LED unit savings; b) reduced Lighting Control unit savings; c) added Pipe wrap measure; d) re-grouped Heavy Duty Plug-in Timers; and e) increased Outdoor Clothesline unit savings
|  | Consumer | Updated Heating and Cooling measure input assumptions based on 2017 Consumer Program Evaluation, changes to programs and additional IESO research. | a) removed Furnace ECM savings attributable to fuel switching; and b) added varies permutations of ASHP measures to include Ductless, Ducted and Cold-climate ASHP replacing baselines with or without cooling
|  | Consumer | Updated HAP measure input assumptions based on 2017 Consumer Program Evaluation, changes to programs and additional IESO research. | a) adjusted LED unit savings; b) removed CFL lighting measures; c) adjusted Appliance unit savings; d) adjusted miscellaneous measure unit savings; and e) increased Programmable Thermostat and Pipe Wrap unit savings
|  | Consumer | Removed measures from programs and pilots that are no longer being offered. | Removed all measures from the following programs/pilots: Appliance Exchange, Appliance Retirement, Direct Install Pilot, Direct Mail Pilot, Electronic Exchange Pilot, Enersource Truckload Event, Home Depot Home Appliance Market Uplift, HONI HP Pilot, Solar Powered Attic Ventilation
|  | Business | Updated all measure input assumptions that were impacted by the prescriptive lighting quick fix Sept 2018 update. | Occupancy sensor, LED Tube, LED Troffers & Linear Ambient Fixture, LED Troffers & Linear Ambient Retrofit Kit, LED High Bay.
Measures and Assumptions List - January 2020 | January 2020 | Consumer | Removed measures from programs and pilots that are no longer being offered. | Removed all measures from the following programs/pilots: Instant Discount, Residential New Construction
|  | Consumer | Added new measures for 2020 | Added measures for smart thermostats, chest freezer and tier 2 power bar
|  | Consumer | Recalculate Summer Peak Demand Savings (kW) | Update for calendar year 2020.
|  | Business | Removed measures from programs and pilots that are no longer being offered. | Removed all measures from the following programs/pilots: High-Performance New Construction (HPNC) and HVAC Program
|  | Business | Updated new measures from late 2019 for lighting | T5 tubes, T5HO tubes, T8 tubes, filament lamps, globe lamps, and plug-in CFL LED replacements
|  | Business | Added DCKV measure input assumptions | All DCKV cooking measures
|  | Business | Added Energy Star Ice Machines measures | All Building Plug Load measures
|  | Business | Added compressed air measures | All measures
|  | Business | Updated refrigeration measures | Horizontal doors measures added
|  | Business | Recalculate Summer Peak Demand Savings (kW) | Update for calendar year 2020.
Measures and Assumptions List - March 2020 | February 2020 | Consumer | Maintain Summer Peak Demand Savings (kW) to 2019 values for consumer measures. | Maintain Summer Peak Demand Savings (kW) to unadjusted values for consumer measures. (HAP)
Update for calendar year 2019.
Fixed VSD and VD demand and energy savings formula
Measures and Assumptions List - 2021 | March 2021 | Consumer | Removed measures no longer being offered | Removed Programmable Thermostat
|  |  | Updated with new measure offerings | Added: General Purpose Timer, Weather-stripping, LED Nightlight
Updated Savings Assumptions, Incremental Costs and Load Shapes
|  | Business | Removed measures no longer being offered
Updated with new measure offerings
Updated Savings Assumptions, Incremental Costs and Load Shapes
Measures and Assumptions List - 2022 | May 2022 | Consumer | Removed measures no longer being offered | Removed LED Lighting measures not offered
|  |  | Updated with new measure offerings | Updated Line Voltage Programmable Thermostat Incremental Cost
|  |  | Updated appliance and weatherization measure incremental costs | Added Low Voltage Smart Thermostat with C-Wire Kit Measure
|  |  | Updated Weatherization measure (Draftproofing, Attic Insulation, Basement Insulation & Wall Insulation) incremental costs | Revised Compact Chest Freezer size category and updated the measure Incremental Cost
|  |  | Changed Draftproofing Incremental Cost based on sq.ft of total home floor areas used calculating the volume of the home for blower door tests | Added Chest Freezer (7.75 ≤ and < 12.0 cu ft) measure Added Refrigerator (12.5 ≤ and < 15.5 cu ft) measure
|  | Business | Extracted business prescriptive measures from CDMIS | Added cold domestic water booster pump measure
Included quasi prescriptive measures
Measures and Assumptions List - 2024 | February 2024 | Consumer | Corrected miscalculations in energy and demand savings from previous versions | Updated calculations for hot water measures, medium sized dehumidifier. Corrected handheld and shower head savings that were switched around
|  |  | Added new measures to support savings accuracy | Added multi-unit home option for hot water measures that were intially built only around single-family
|  |  | Updated accuracy of demand savings load profile | Weatherization measures based on alternative summer peak demand instead of summer peak demand. Also applied a demand factor of electric heating and cooling for smart thermostats instead of forced air central heating
|  | Business | Added Small Business Program and Instant Discounts Program measures list
Separated Quasi-Prescriptive measures from the Prescriptive measures
|  |  | Changes to Annual Operating Hours for Lighting - Food Retail and Lighting - Warehouse | Lighting - Food Retail (from 6074 to 3121) and Lighting - Warehouse (from 3759 to 4408)
|  |  | Corrected calculation errors | Creep heat controller, LED grow lights - Cannabis Greenhouse, Unitary ASHP and PTHP

## Business-Retrofit Prescriptive
END_USE | CONSERVATION_MEASURE_NAME | DESCRIPTION | BASE_MEASURE | ASSUMED_ANNUAL_OPERATING_HOURS | BASE_CASE_KW | BASE_CASE_KWH | CONSERVATION_CASE_KW | CONSERVATION_CASE_KWH | FIRST_YEAR_DEMAND_SAVINGS | FIRST_YEAR_ENERGY_SAVINGS | PEAK_DEMAND_SAVINGS | EFFECTIVE_USEFUL_LIFE | END_USE_LOAD_PROFILE | INCREMENTAL_LIFE_CYCLE_COST
Agribusiness | CREEP HEAT CONTROLLER | NEMA 4 or 4X. Must meet all applicable Code, standard, safety and regulatory requirements including CSA/UL/CUL | Poorly Controlled Creep Heat Lamps | 6900 | 1.75 | 12075 | 1.4 | 9660 | 0.35 | 2415 | 0.27568 | 15 | PSP-Business-Commercial-Creep_Heat_Controller | 666
Agribusiness | DAIRY ENERGY STAR WATER HEATER | Energy Star Electric Hot Water Tank >= 60 gal | Standard electric hot water heater | 8760 | 1.7222 | 15086.4099 | 0.77499 | 6788.8844 | 0.94721 | 8297.5254 | 0.94721 | 15 | PSP-Industrial-Agriculture-Other | 853
Agribusiness | DAIRY PLATE COOLER | Plate cooler to pre-cool milk prior to refrigeration | No pre-cooling | 2920 | - | - | - | - | 2.57 | 7503 | 0 | 15 | PSP-Industrial-Agriculture-Process_Cooling | 3098
Agribusiness | DOUBLE CREEP HEAT PAD | Up to 200W maximum | 2 x 175W Heat Lamps | 6900 | 0.35 | 2415 | 0.169 | 1166.1 | 0.181 | 1248.9 | 0.046545 | 10 | EM&V-Commercial-Creep_Heat_Pad | 95
Agribusiness | DUAL AND NATURAL EXHAUST VENTILATION SYSTEM | Chicken broilers | Fans: 340W/1000 birds | - | 0.34 | 1020 | 0.152 | 203.8052 | 0.188 | 816.1948 | 0.11756 | 15 | EM&V-Commercial-Dual_&_Natural_Ventilation_Fans_All_Year | 27000
Agribusiness | DUAL AND NATURAL EXHAUST VENTILATION SYSTEM | Dairy-tie stall, outside in summer | 50% in barn; 50% on pasture | - | 0.035 | 176.52 | 0.016 | 35.2703 | 0.019 | 141.2497 | 0.00046568 | 15 | EM&V-Commercial-Dual_&_Natural_Ventilation_Fans_Winter_Only | 12000
Agribusiness | DUAL AND NATURAL EXHAUST VENTILATION SYSTEM | Dairy-tie stall, year-round housing | Fans: 35W/cow | - | 0.035 | 229.1835 | 0.016 | 45.7929 | 0.019 | 183.3906 | 0.00060461 | 15 | EM&V-Commercial-Dual_&_Natural_Ventilation_Fans_Winter_Only | 12000
Agribusiness | DUAL AND NATURAL EXHAUST VENTILATION SYSTEM | Egg layers | Fans: 400W/1000 birds | - | 0.4 | 2190 | 0.179 | 437.5817 | 0.221 | 1752.4183 | 0.2524 | 15 | EM&V-Commercial-Dual_&_Natural_Ventilation_Fans_All_Year | 18000
Agribusiness | DUAL AND NATURAL EXHAUST VENTILATION SYSTEM | Greenhouse - Flowers | Fans: 1260W/1000 sq. meters | - | 1.26 | 11037.6 | 0.563 | 2205.4118 | 0.697 | 8832.1882 | 1.2721 | 15 | EM&V-Commercial-Dual_&_Natural_Ventilation_Fans_All_Year | 10250
Agribusiness | DUAL AND NATURAL EXHAUST VENTILATION SYSTEM | Swine - Breeding & Gestation | Fans: 17W/sow | - | 0.017 | 99.688 | 0.008 | 19.9186 | 0.009 | 79.7694 | 0.011489 | 15 | EM&V-Commercial-Dual_&_Natural_Ventilation_Fans_All_Year | 5500
Agribusiness | DUAL AND NATURAL EXHAUST VENTILATION SYSTEM | Swine - Growing & Finishing | Fans: 5W/market-weight hog | - | 0.005 | 43.8 | 0.002 | 8.7516 | 0.003 | 35.0484 | 0.005048 | 15 | EM&V-Commercial-Dual_&_Natural_Ventilation_Fans_All_Year | 15000
Agribusiness | DUAL AND NATURAL EXHAUST VENTILATION SYSTEM | Turkeys | Fans: 1130W/1000 birds | - | 1.13 | 7876.7647 | 0.505 | 1573.8485 | 0.625 | 6302.9162 | 0.90781 | 15 | EM&V-Commercial-Dual_&_Natural_Ventilation_Fans_All_Year | 15000
Agribusiness | ENGINE BLOCK HEATER TIMER | Plug-in timer that operates the heater only when outdoor temp drops below -3.8C | Manual plug-in block heater | - | - | - |  |  | 0 | 632.4 | 0 | 3 | EM&V-Residential-Car_Block_Heater_South_Ontario | 13.76
Agribusiness | HIGH EFFICIENCY VENTILATION EXHAUST FANS | >= 18 to < 24" Fan | Minimum fan grouping in category from BESS Laboratory ratings | 4313 | 0.3913 | 1687.6956 | 0.29032 | 1252.1613 | 0.10098 | 435.5344 | 0.12677 | 15 | EM&V-Commercial-HE_Ventilation_Exhaust_Fans | 202
Agribusiness | HIGH EFFICIENCY VENTILATION EXHAUST FANS | >= 24" to < 36" Fans | Minimum fan grouping in category from BESS Laboratory ratings | 4313 | 0.56018 | 2416.0502 | 0.41007 | 1768.6119 | 0.15011 | 647.4383 | 0.18845 | 15 | EM&V-Commercial-HE_Ventilation_Exhaust_Fans | 202
Agribusiness | HIGH EFFICIENCY VENTILATION EXHAUST FANS | >= 36" to < 48" Fans | Minimum fan grouping in category from BESS Laboratory ratings | 4313 | 0.72247 | 3115.9987 | 0.56443 | 2434.374 | 0.15804 | 681.6247 | 0.1984 | 15 | EM&V-Commercial-HE_Ventilation_Exhaust_Fans | 202
Agribusiness | HIGH EFFICIENCY VENTILATION EXHAUST FANS | >= 48" Fans | Minimum fan grouping in category from BESS Laboratory ratings | 4313 | 1.2711 | 5482.3561 | 0.99674 | 4298.94 | 0.27438 | 1183.4161 | 0.34445 | 15 | EM&V-Commercial-HE_Ventilation_Exhaust_Fans | 202
Agribusiness | HIGH TEMPERATURE CUTOUT THERMOSTAT | Operating range 24 to 40 Celsius | Poorly Controlled Creep Heat Lamps | 6900 |  | 10867.5 |  | 9872.1 |  | 995.4 | 0.54393 | 10 | PSP-Business-Commercial-HT_Cutout_Thermostat | 124
Agribusiness | HIGH VOLUME LOW SPEED FAN | >= 10 ft to <11 ft, 1 HP | 2 units Box fan, 1 HP | 2124 | 2.506 | 5322.744 | 0.424 | 900.576 | 2.082 | 4422.168 | 1.4927 | 15 | EM&V-Commercial-HVLS_No_Summer_Operation | 1293
Agribusiness | HIGH VOLUME LOW SPEED FAN | >= 11 ft to <19 ft, 1.5 HP | 4 units Box fan, 1 HP | 2124 | 3.898 | 8279.352 | 0.659 | 1399.716 | 3.239 | 6879.636 | 2.3223 | 15 | EM&V-Commercial-HVLS_No_Summer_Operation | 2962
Agribusiness | HIGH VOLUME LOW SPEED FAN | >= 19 ft to <=24 ft, 2 HP | 4 units Box fan, 1 HP | 2124 | 5.555 | 11798.82 | 0.94 | 1996.56 | 4.615 | 9802.26 | 3.3088 | 15 | EM&V-Commercial-HVLS_No_Summer_Operation | 5558
Agribusiness | LOW ENERGY LIVESTOCK WATERERS | 300W maximum | 1500W (Max) electric heated Waterers | 2804 | - | - | - | - | 0.85 | 2383 | 0 | 10 | PSP-Business-Commercial-Livestock_Waterer | 920
Agribusiness | MILK SCROLL COMPRESSOR | New scroll compressor for milk cooling with minimum EER of 12 | Old Reciprocating Compressor | 2920 | - | - | - | - | 2.314 | 6759 | 0.77158 | 15 | PSP-Industrial-Agriculture-Other | 540
Agribusiness | PHOTOCELL AND TIMER FOR LIGHTING CONTROL | Timer to regulate on-off lighting schedule | 250W Metal Halide (Assume 4 Lamps per Photocell) | 6205 | 1.152 | 7148.16 | 1.152 | 2852.352 | 0 | 4295.808 | 0.47689 | 8 | EM&V-Commercial-HVAC_Fans_Pumps | 78
Agribusiness | SINGLE CREEP HEAT PAD | Up to 100W maximum | 175W Heat Lamp | 6900 | 0.175 | 1207.5 | 0.085 | 586.5 | 0.09 | 621 | 0.023144 | 10 | EM&V-Commercial-Creep_Heat_Pad | 70
Agribusiness | SOLAR HOT WATER COLLECTOR FOR DAIRY FARMS | Solar hot water collector to be used with electric hot water heater | Standard electric hot water heater | 8760 | - | - | - | - | - | 9948 | 1.1043 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 9880
Building Plug Load | BEVERAGE VENDING MACHINE CONTROLS | Power Sensor and/or Occupancy Control for Refrigerated Vending Machine | Standard beverage vending machines | 8760 | - | - | - | - | - | 1612.944 | 0.19672 | 5 | PSP-Business-Commercial-Other_Plug_Loads | 290
Commercial Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | <100 W (<0.134HP) | Circulator pump with PSC motor | 2190 | 0.28 | 613.2 | 0.05 | 109.5 | 0.23 | 503.7 | 0.06161 | 15 | PSP-Business-Commercial-Domestic_Hot_Water | 1225
Commercial Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=100<500 W (>=0.134<0.67HP) | Circulator pump with PSC motor | 2190 | 1.39 | 3044.1 | 0.25 | 547.5 | 1.14 | 2496.6 | 0.30537 | 15 | PSP-Business-Commercial-Domestic_Hot_Water | 1536
Commercial Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=1490<2237 W (>=2<3HP) | Circulator pump with PSC motor | 2190 | 9.75 | 21352.5 | 1.76 | 3854.4 | 7.99 | 17498.1 | 2.1403 | 15 | PSP-Business-Commercial-Domestic_Hot_Water | 1896
Commercial Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=500<750 W (>=0.67<1HP) | Circulator pump with PSC motor | 2190 | 3.89 | 8519.1 | 0.7 | 1533 | 3.19 | 6986.1 | 0.8545 | 15 | PSP-Business-Commercial-Domestic_Hot_Water | 1599
Commercial Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=750<1490 W (>=1<2HP) | Circulator pump with PSC motor | 2190 | 4.88 | 10687.2 | 0.88 | 1927.2 | 4 | 8760 | 1.0715 | 15 | PSP-Business-Commercial-Domestic_Hot_Water | 1800
Commercial Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | 2237 W (3HP) | Circulator pump with PSC motor | 2190 | 14.63 | 32039.7 | 2.63 | 5759.7 | 12 | 26280 | 3.2144 | 15 | PSP-Business-Commercial-Domestic_Hot_Water | 2592
Compressed Air | COMPRESSED AIR LOW PRESSURE DROP FILTER | >=30 to <50 HP | Standard coalescing filter | 5700 | - | - | - | - | 0 | 3543.5 | 0.38354 | 7 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 515
Compressed Air | COMPRESSED AIR LOW PRESSURE DROP FILTER | >=50 to <70 HP | Standard coalescing filter | 5700 | - | - | - | - | 0 | 5315.25 | 0.57532 | 7 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 626
Compressed Air | COMPRESSED AIR LOW PRESSURE DROP FILTER | >=70 to <90 HP | Standard coalescing filter | 5700 | - | - | - | - | 0 | 7087 | 0.76709 | 7 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 709
Compressed Air | COMPRESSED AIR LOW PRESSURE DROP FILTER | >=90 to <110 HP | Standard coalescing filter | 5700 | - | - | - | - | 0 | 8858.75 | 0.95886 | 7 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 1069
Compressed Air | COMPRESSED AIR LOW PRESSURE DROP FILTER | 0 to <30 HP | Standard coalescing filter | 5700 | - | - | - | - | 0 | 1771.75 | 0.19177 | 7 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 270
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 10 HP | Fixed Speed Compressor >= 10 HP | 5702 | - | - | - | - | 1.332 | 7595.06 | 0.82208 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 2095
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 100 HP | Fixed Speed Compressor >= 100 HP | 5702 | - | - | - | - | 16.704 | 95246.21 | 10.3093 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 13888
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 125 HP | Fixed Speed Compressor >= 125 HP | 5702 | - | - | - | - | 20.88 | 119057.76 | 12.8867 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 18628
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 15 HP | Fixed Speed Compressor >= 15 HP | 5702 | - | - | - | - | 1.998 | 11392.6 | 1.2331 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 2470
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 150 HP | Fixed Speed Compressor >= 150 HP | 5702 | - | - | - | - | 25.056 | 142869.31 | 15.464 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 23167
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 20 HP | Fixed Speed Compressor >= 20 HP | 5702 | - | - | - | - | 2.664 | 15190.13 | 1.6442 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 2980
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 200 HP | Fixed Speed Compressor >= 200 HP | 5702 | - | - | - | - | 33.408 | 190492.42 | 20.6187 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 24092
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 25 HP | Fixed Speed Compressor >= 25 HP | 5702 | - | - | - | - | 3.33 | 18987.66 | 2.0552 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 3289
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 30 HP | Fixed Speed Compressor >= 30 HP | 5702 | - | - | - | - | 3.996 | 22785.19 | 2.4662 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 3514
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 40 HP | Fixed Speed Compressor >= 40 HP | 5702 | - | - | - | - | 5.328 | 30380.26 | 3.2883 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 4929
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 50 HP | Fixed Speed Compressor >= 50 HP | 5702 | - | - | - | - | 8.352 | 47623.1 | 5.1547 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 5430
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 60 HP | Fixed Speed Compressor >= 60 HP | 5702 | - | - | - | - | 10.0224 | 57147.72 | 6.1856 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 9323
Compressed Air | COMPRESSED AIR VD | Variable Displacement Compressor >= 75 HP | Fixed Speed Compressor >= 75 HP | 5702 | - | - | - | - | 12.528 | 71434.66 | 7.732 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 13118
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 10 HP | Fixed Speed Compressor >= 10 HP | 5702 | - | - | - | - | 1.665 | 9493.83 | 1.0276 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 2893
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 100 HP | Fixed Speed Compressor >= 100 HP | 5702 | - | - | - | - | 20.88 | 119057.76 | 12.8867 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 22128
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 125 HP | Fixed Speed Compressor >= 125 HP | 5702 | - | - | - | - | 26.1 | 148822.2 | 16.1083 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 28888
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 15 HP | Fixed Speed Compressor >= 15 HP | 5702 | - | - | - | - | 2.4975 | 14240.75 | 1.5414 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 3441
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 150 HP | Fixed Speed Compressor >= 150 HP | 5702 | - | - | - | - | 31.32 | 178586.64 | 19.33 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 32717
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 20 HP | Fixed Speed Compressor >= 20 HP | 5702 | - | - | - | - | 3.33 | 18987.66 | 2.0552 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 5336
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 200 HP | Fixed Speed Compressor >= 200 HP | 5702 | - | - | - | - | 41.76 | 238115.52 | 25.7734 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 54642
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 25 HP | Fixed Speed Compressor >= 25 HP | 5702 | - | - | - | - | 4.1625 | 23734.58 | 2.569 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 5580
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 30 HP | Fixed Speed Compressor >= 30 HP | 5702 | - | - | - | - | 4.995 | 28481.49 | 3.0828 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 6113
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 40 HP | Fixed Speed Compressor >= 40 HP | 5702 | - | - | - | - | 6.66 | 37975.32 | 4.1104 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 6643
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 50 HP | Fixed Speed Compressor >= 50 HP | 5702 | - | - | - | - | 10.44 | 59528.88 | 6.4433 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 8993
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 60 HP | Fixed Speed Compressor >= 60 HP | 5702 | - | - | - | - | 12.528 | 71434.66 | 7.732 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 15578
Compressed Air | COMPRESSED AIR VSD | Variable Speed Drive Compressor >= 75 HP | Fixed Speed Compressor >= 75 HP | 5702 | - | - | - | - | 15.66 | 89293.32 | 9.665 | 13 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 15868
Compressed Air | CYCLING OR THERMAL MASS REFRIGERATED DRYER | >=200 to <400 CFM | Non-Cycling Refrigerated Dryer | 3920 | - | - | - | - | 0 | 2487.1 | 0.2692 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 1839
Compressed Air | CYCLING OR THERMAL MASS REFRIGERATED DRYER | >=400 to <750 CFM | Non-Cycling Refrigerated Dryer | 3920 | - | - | - | - | 0 | 4974.2 | 0.5384 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 2709
Compressed Air | CYCLING OR THERMAL MASS REFRIGERATED DRYER | 0 to <200 CFM | Non-Cycling Refrigerated Dryer | 3920 | - | - | - | - | 0 | 994.84 | 0.10768 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 703
Compressed Air | ENGINEERED NOZZLE | 1/16" Engineered Nozzle | Crimped Pipe or locally made nozzle | 3920 | - | - | - | - | 0.0279 | 109.368 | 0.011838 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 112
Compressed Air | ENGINEERED NOZZLE | 1/4" Engineered Nozzle | Crimped Pipe or locally made nozzle | 3920 | - | - | - | - | 0.44 | 1724.8 | 0.18669 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 142
Compressed Air | ENGINEERED NOZZLE | 1/8" Engineered Nozzle | Crimped Pipe or locally made nozzle | 3920 | - | - | - | - | 0.11 | 431.2 | 0.046673 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 98
Compressed Air | ENGINEERED NOZZLE | 3/8" Engineered Nozzle | Crimped Pipe or locally made nozzle | 3920 | - | - | - | - | 0.99 | 3880.8 | 0.42005 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 121
Compressed Air | PRIMARY AIR RECEIVER TANK | >=125 to <175 HP (>=2200 to <3150 USG) | Primary storage ratio of 1 USG/CFM of oil-flooded load/no load air compressor | 5700 | - | - | - | - | 0 | 55800 | 6.0397 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 29673
Compressed Air | PRIMARY AIR RECEIVER TANK | >=15 to <25 HP (>=240 to <400 USG) | Primary storage ratio of 1 USG/CFM of oil-flooded load/no load air compressor | 5700 | - | - | - | - | 0 | 9513.3333 | 1.0297 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 4147
Compressed Air | PRIMARY AIR RECEIVER TANK | >=175 to <225 HP (>=3150 to <4050 USG) | Primary storage ratio of 1 USG/CFM of oil-flooded load/no load air compressor | 5700 | - | - | - | - | 0 | 74400 | 8.053 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 40007
Compressed Air | PRIMARY AIR RECEIVER TANK | >=25 to <35 HP (>=400 to <660 USG) | Primary storage ratio of 1 USG/CFM of oil-flooded load/no load air compressor | 5700 | - | - | - | - | 0 | 14270 | 1.5446 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 5846
Compressed Air | PRIMARY AIR RECEIVER TANK | >=35 to <45 HP (>=660 to <1060 USG) | Primary storage ratio of 1 USG/CFM of oil-flooded load/no load air compressor | 5700 | - | - | - | - | 0 | 19026.6667 | 2.0594 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 11363
Compressed Air | PRIMARY AIR RECEIVER TANK | >=45 to <55 HP (>=800 to <1060 USG) | Primary storage ratio of 1 USG/CFM of oil-flooded load/no load air compressor | 5700 | - | - | - | - | 0 | 18600 | 2.0132 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 13707
Compressed Air | PRIMARY AIR RECEIVER TANK | >=55 to <125 HP (>=1060 to <2220 USG) | Primary storage ratio of 1 USG/CFM of oil-flooded load/no load air compressor | 5700 | - | - | - | - | 0 | 37200 | 4.0265 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 16050
Compressed Air | PRIMARY AIR RECEIVER TANK | 0 to <15 HP (0 to <240 USG) | Primary storage ratio of 1 USG/CFM of oil-flooded load/no load air compressor | 5700 | - | - | - | - | 0 | 4756.6667 | 0.51486 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 2908
Compressed Air | REGENERATIVE DRYER WITH DEWPOINT CONTROL | >=200 to <400 CFM | Regenerative Dryer with Timer Controlled Regeneration | 3920 | - | - | - | - | 0 | 16587 | 1.7954 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 4538
Compressed Air | REGENERATIVE DRYER WITH DEWPOINT CONTROL | >=400 to <750 CFM | Regenerative Dryer with Timer Controlled Regeneration | 3920 | - | - | - | - | 0 | 33174 | 3.5907 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 4538
Compressed Air | REGENERATIVE DRYER WITH DEWPOINT CONTROL | 0 to <200 CFM | Regenerative Dryer with Timer Controlled Regeneration | 3920 | - | - | - | - | 0 | 6634.8 | 0.71814 | 15 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 4538
Compressed Air | ZERO LOSS DRAIN | Zero Loss Drain | Time controlled moisture drain | 3920 | - | - | - | - | 0.308 | 1206 | 0.13054 | 10 | PSP-Industrial-Miscellaneous_Industrial-Compressed_Air | 380
Demand Control Ventilation | DEMAND CONTROL KITCHEN VENTILATION | 10001 - 15000 CFM exhaust fan capacity | Constant volume exhaust fan | 5840 | - | 48705.6 |  | 20465.5938 |  | 28240.0062 | 3.5202 | 15 | PSP-Business-Commercial-Cooking | 42101
Demand Control Ventilation | DEMAND CONTROL KITCHEN VENTILATION | 5001 - 10000 CFM exhaust fan capacity | Constant volume exhaust fan | 5840 | - | 27389.6 |  | 11508.8291 |  | 15880.7709 | 1.9796 | 15 | PSP-Business-Commercial-Cooking | 25261
Demand Control Ventilation | DEMAND CONTROL KITCHEN VENTILATION | Up to 5000 CFM exhaust fan capacity | Constant volume exhaust fan | 5840 | - | 8234.4 |  | 3460.0105 |  | 4774.3895 | 0.59515 | 15 | PSP-Business-Commercial-Cooking | 8420
Demand Control Ventilation | DEMAND CONTROL VENTILATION - ENCLOSED PARKING GARAGES | >=2 to <= 5 HP | Garage ventilation fans running continuously | 8760 | - | - | - | - | 0 | 8294.3723 | 0.94685 | 10 | PSP-Consumer-Residential-Ventilation_And_Circulation | 2100
Demand Control Ventilation | DEMAND CONTROL VENTILATION - ENCLOSED PARKING GARAGES | >10 to <= 25 HP | Garage ventilation fans running continuously | 8760 | - | - | - | - | 0 | 41471.8615 | 4.7342 | 10 | PSP-Consumer-Residential-Ventilation_And_Circulation | 4200
Demand Control Ventilation | DEMAND CONTROL VENTILATION - ENCLOSED PARKING GARAGES | >25 to <= 50 HP | Garage ventilation fans running continuously | 8760 | - | - | - | - | 0 | 82943.7231 | 9.4685 | 10 | PSP-Consumer-Residential-Ventilation_And_Circulation | 4200
Demand Control Ventilation | DEMAND CONTROL VENTILATION - ENCLOSED PARKING GARAGES | >5 to <= 10 HP | Garage ventilation fans running continuously | 8760 | - | - | - | - | 0 | 16588.7446 | 1.8937 | 10 | PSP-Consumer-Residential-Ventilation_And_Circulation | 2100
Demand Control Ventilation | DEMAND CONTROL VENTILATION - ENCLOSED PARKING GARAGES | >50 to <= 75 HP | Garage ventilation fans running continuously | 8760 | - | - | - | - | 0 | 124415.5846 | 14.2027 | 10 | PSP-Consumer-Residential-Ventilation_And_Circulation | 8400
Demand Control Ventilation | DEMAND CONTROL VENTILATION - ENCLOSED PARKING GARAGES | >75 to <= 100 HP | Garage ventilation fans running continuously | 8760 | - | - | - | - | 0 | 165887.4462 | 18.9369 | 10 | PSP-Consumer-Residential-Ventilation_And_Circulation | 8400
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 1 HP, 1200 RPM, 83.5% | ODP Motor, 1 HP, 1200 RPM, 82.5% | 4000 | 0.67818 | 2712.7273 | 0.67006 | 2680.2395 | 0.00812 | 32.4877 | 0.0036065 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 66.79
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 1 HP, 1800 RPM, 86.5% | ODP Motor, 1 HP, 1800 RPM, 85.5% | 4000 | 0.65439 | 2617.5439 | 0.64682 | 2587.2832 | 0.00757 | 30.2606 | 0.0033593 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 66.79
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 1 HP, 3600 RPM, 78% | ODP Motor, 1 HP, 3600 RPM, 77% | 4000 | 0.72662 | 2906.4935 | 0.71731 | 2869.2308 | 0.00932 | 37.2627 | 0.0041366 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 66.79
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 1.5 HP, 1200 RPM, 87.5% | ODP Motor, 1.5 HP, 1200 RPM, 86.5% | 4000 | 0.97023 | 3880.9249 | 0.95914 | 3836.5714 | 0.01109 | 44.3534 | 0.0049238 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 97.73
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 1.5 HP, 1800 RPM, 87.5% | ODP Motor, 1.5 HP, 1800 RPM, 86.5% | 4000 | 0.97023 | 3880.9249 | 0.95914 | 3836.5714 | 0.01109 | 44.3534 | 0.0049238 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 97.73
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 1.5 HP, 3600 RPM, 85% | ODP Motor, 1.5 HP, 3600 RPM, 84% | 4000 | 0.99911 | 3996.4286 | 0.98735 | 3949.4118 | 0.01175 | 47.0168 | 0.0052194 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 97.73
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 10 HP, 1200 RPM, 92.7% | ODP Motor, 10 HP, 1200 RPM, 91.7% | 4000 | 6.1014 | 24405.6707 | 6.0356 | 24142.3948 | 0.06582 | 263.2758 | 0.029227 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 269.08
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 10 HP, 1800 RPM, 92.7% | ODP Motor, 10 HP, 1800 RPM, 91.7% | 4000 | 6.1014 | 24405.6707 | 6.0356 | 24142.3948 | 0.06582 | 263.2758 | 0.029227 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 269.08
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 10 HP, 3600 RPM, 90.5% | ODP Motor, 10 HP, 3600 RPM, 89.5% | 4000 | 6.2514 | 25005.5866 | 6.1823 | 24729.2818 | 0.06908 | 276.3048 | 0.030673 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 269.08
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 100 HP, 1200 RPM, 96% | ODP Motor, 100 HP, 1200 RPM, 95% | 4000 | 58.8947 | 235578.9474 | 58.2812 | 233125 | 0.61349 | 2453.9474 | 0.27242 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 1132.7
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 100 HP, 1800 RPM, 96.4% | ODP Motor, 100 HP, 1800 RPM, 95.4% | 4000 | 58.6478 | 234591.195 | 58.0394 | 232157.6763 | 0.60838 | 2433.5186 | 0.27015 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 1132.7
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 100 HP, 3600 RPM, 94.6% | ODP Motor, 100 HP, 3600 RPM, 93.6% | 4000 | 59.7756 | 239102.5641 | 59.1438 | 236575.0529 | 0.63188 | 2527.5113 | 0.28058 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 1132.7
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 125 HP, 1200 RPM, 96% | ODP Motor, 125 HP, 1200 RPM, 95% | 4000 | 73.6184 | 294473.6842 | 72.8516 | 291406.25 | 0.76686 | 3067.4342 | 0.34052 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 4360.9067
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 125 HP, 1800 RPM, 96.4% | ODP Motor, 125 HP, 1800 RPM, 95.4% | 4000 | 73.3097 | 293238.9937 | 72.5493 | 290197.0954 | 0.76047 | 3041.8983 | 0.33769 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 4360.9067
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 125 HP, 3600 RPM, 95.1% | ODP Motor, 125 HP, 3600 RPM, 94.1% | 4000 | 74.3225 | 297290.1169 | 73.541 | 294164.0379 | 0.78152 | 3126.079 | 0.34703 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 4360.9067
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 15 HP, 1200 RPM, 92.7% | ODP Motor, 15 HP, 1200 RPM, 91.7% | 4000 | 9.1521 | 36608.506 | 9.0534 | 36213.5922 | 0.09873 | 394.9138 | 0.04384 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 234.99
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 15 HP, 1800 RPM, 94% | ODP Motor, 15 HP, 1800 RPM, 93% | 4000 | 9.0242 | 36096.7742 | 8.9282 | 35712.766 | 0.096 | 384.0082 | 0.04263 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 234.99
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 15 HP, 3600 RPM, 91.2% | ODP Motor, 15 HP, 3600 RPM, 90.2% | 4000 | 9.3043 | 37217.2949 | 9.2023 | 36809.2105 | 0.10202 | 408.0844 | 0.045302 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 234.99
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 150 HP, 1200 RPM, 96.4% | ODP Motor, 150 HP, 1200 RPM, 95.4% | 4000 | 87.9717 | 351886.7925 | 87.0591 | 348236.5145 | 0.91257 | 3650.2779 | 0.40523 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 5318.51
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 150 HP, 1800 RPM, 96.8% | ODP Motor, 150 HP, 1800 RPM, 95.8% | 4000 | 87.6044 | 350417.5365 | 86.6994 | 346797.5207 | 0.905 | 3620.0159 | 0.40187 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 5318.51
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 150 HP, 3600 RPM, 95.1% | ODP Motor, 150 HP, 3600 RPM, 94.1% | 4000 | 89.187 | 356748.1403 | 88.2492 | 352996.8454 | 0.93782 | 3751.2949 | 0.41644 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 5318.51
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 2 HP, 1200 RPM, 88.5% | ODP Motor, 2 HP, 1200 RPM, 87.5% | 4000 | 1.2789 | 5115.4286 | 1.2644 | 5057.6271 | 0.01445 | 57.8015 | 0.0064167 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 105.01
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 2 HP, 1800 RPM, 87.5% | ODP Motor, 2 HP, 1800 RPM, 86.5% | 4000 | 1.2936 | 5174.5665 | 1.2789 | 5115.4286 | 0.01478 | 59.1379 | 0.006565 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 105.01
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 2 HP, 3600 RPM, 86.5% | ODP Motor, 2 HP, 3600 RPM, 85.5% | 4000 | 1.3088 | 5235.0877 | 1.2936 | 5174.5665 | 0.01513 | 60.5213 | 0.0067186 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 105.01
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 20 HP, 1200 RPM, 93.4% | ODP Motor, 20 HP, 1200 RPM, 92.4% | 4000 | 12.1104 | 48441.5584 | 11.9807 | 47922.9122 | 0.12966 | 518.6462 | 0.057576 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 263.31
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 20 HP, 1800 RPM, 94% | ODP Motor, 20 HP, 1800 RPM, 93% | 4000 | 12.0323 | 48129.0323 | 11.9043 | 47617.0213 | 0.128 | 512.011 | 0.056839 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 263.31
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 20 HP, 3600 RPM, 92% | ODP Motor, 20 HP, 3600 RPM, 91% | 4000 | 12.2967 | 49186.8132 | 12.163 | 48652.1739 | 0.13366 | 534.6393 | 0.059351 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 263.31
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 200 HP, 1200 RPM, 96.4% | ODP Motor, 200 HP, 1200 RPM, 95.4% | 4000 | 117.2956 | 469182.3899 | 116.0788 | 464315.3527 | 1.2168 | 4867.0372 | 0.5403 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 6123.7737
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 200 HP, 1800 RPM, 96.8% | ODP Motor, 200 HP, 1800 RPM, 95.8% | 4000 | 116.8059 | 467223.3821 | 115.5992 | 462396.6942 | 1.2067 | 4826.6878 | 0.53582 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 6123.7737
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 200 HP, 3600 RPM, 96% | ODP Motor, 200 HP, 3600 RPM, 95% | 4000 | 117.7895 | 471157.8947 | 116.5625 | 466250 | 1.227 | 4907.8947 | 0.54484 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 6123.7737
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 25 HP, 1200 RPM, 94% | ODP Motor, 25 HP, 1200 RPM, 93% | 4000 | 15.0403 | 60161.2903 | 14.8803 | 59521.2766 | 0.16 | 640.0137 | 0.071049 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 322.7969
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 25 HP, 1800 RPM, 94.6% | ODP Motor, 25 HP, 1800 RPM, 93.6% | 4000 | 14.9439 | 59775.641 | 14.7859 | 59143.7632 | 0.15797 | 631.8778 | 0.070146 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 322.7969
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 25 HP, 3600 RPM, 92.7% | ODP Motor, 25 HP, 3600 RPM, 91.7% | 4000 | 15.2535 | 61014.1767 | 15.089 | 60355.9871 | 0.16455 | 658.1896 | 0.073067 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 322.7969
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 250 HP, 1200 RPM, 96.4% | ODP Motor, 250 HP, 1200 RPM, 95.4% | 4000 | 148.5744 | 594297.6939 | 147.0332 | 588132.7801 | 1.5412 | 6165 | 0.68439 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 7258.34
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 250 HP, 1800 RPM, 96.8% | ODP Motor, 250 HP, 1800 RPM, 95.8% | 4000 | 147.9541 | 591816.2839 | 146.4256 | 585702.4793 | 1.5285 | 6114 | 0.67873 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 7258.34
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 250 HP, 3600 RPM, 96% | ODP Motor, 250 HP, 3600 RPM, 95% | 4000 | 149.2 | 596800 | 147.6458 | 590583.3333 | 1.5442 | 6218 | 0.69027 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 7258.34
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 3 HP, 1200 RPM, 89.5% | ODP Motor, 3 HP, 1200 RPM, 88.5% | 4000 | 1.8966 | 7586.4407 | 1.8754 | 7501.676 | 0.02119 | 84.7647 | 0.0094099 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 120.89
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 3 HP, 1800 RPM, 90.5% | ODP Motor, 3 HP, 1800 RPM, 89.5% | 4000 | 1.8754 | 7501.676 | 1.8547 | 7418.7845 | 0.02072 | 82.8915 | 0.009202 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 120.89
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 3 HP, 3600 RPM, 86.5% | ODP Motor, 3 HP, 3600 RPM, 85.5% | 4000 | 1.9632 | 7852.6316 | 1.9405 | 7761.8497 | 0.0227 | 90.7819 | 0.010078 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 120.89
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 30 HP, 1200 RPM, 94.6% | ODP Motor, 30 HP, 1200 RPM, 93.6% | 4000 | 17.9327 | 71730.7692 | 17.7431 | 70972.5159 | 0.18956 | 758.2534 | 0.084175 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 385.46
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 30 HP, 1800 RPM, 95.1% | ODP Motor, 30 HP, 1800 RPM, 94.1% | 4000 | 17.8374 | 71349.6281 | 17.6498 | 70599.3691 | 0.18756 | 750.259 | 0.083288 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 385.46
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 30 HP, 3600 RPM, 92.7% | ODP Motor, 30 HP, 3600 RPM, 91.7% | 4000 | 18.3042 | 73217.012 | 18.1068 | 72427.1845 | 0.19746 | 789.8275 | 0.08768 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 385.46
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 300 HP, 1200 RPM, 96.4% | ODP Motor, 300 HP, 1200 RPM, 95.4% | 4000 | 178.2893 | 713157.2327 | 176.4398 | 705759.3361 | 1.8495 | 7398 | 0.82127 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 8739.5567
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 300 HP, 1800 RPM, 96.8% | ODP Motor, 300 HP, 1800 RPM, 95.8% | 4000 | 177.5449 | 710179.5407 | 175.7107 | 702842.9752 | 1.8341 | 7337 | 0.8145 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 8739.5567
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 300 HP, 3600 RPM, 96.4% | ODP Motor, 300 HP, 3600 RPM, 95.4% | 4000 | 178.2893 | 713157.2327 | 176.4398 | 705759.3361 | 1.8495 | 7398 | 0.82127 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 8739.5567
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 40 HP, 1200 RPM, 95.1% | ODP Motor, 40 HP, 1200 RPM, 94.1% | 4000 | 23.7832 | 95132.8374 | 23.5331 | 94132.4921 | 0.25009 | 1000.3453 | 0.11105 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 459
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 40 HP, 1800 RPM, 95.1% | ODP Motor, 40 HP, 1800 RPM, 94.1% | 4000 | 23.7832 | 95132.8374 | 23.5331 | 94132.4921 | 0.25009 | 1000.3453 | 0.11105 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 459
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 40 HP, 3600 RPM, 93.4% | ODP Motor, 40 HP, 3600 RPM, 92.4% | 4000 | 24.2208 | 96883.1169 | 23.9615 | 95845.8244 | 0.25932 | 1037.2925 | 0.11515 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 459
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 5 HP, 1200 RPM, 90.5% | ODP Motor, 5 HP, 1200 RPM, 89.5% | 4000 | 3.1257 | 12502.7933 | 3.0912 | 12364.6409 | 0.03454 | 138.1524 | 0.015337 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 166.98
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 5 HP, 1800 RPM, 90.5% | ODP Motor, 5 HP, 1800 RPM, 89.5% | 4000 | 3.1257 | 12502.7933 | 3.0912 | 12364.6409 | 0.03454 | 138.1524 | 0.015337 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 166.98
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 5 HP, 3600 RPM, 87.5% | ODP Motor, 5 HP, 3600 RPM, 86.5% | 4000 | 3.2341 | 12936.4162 | 3.1971 | 12788.5714 | 0.03696 | 147.8448 | 0.016413 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 166.98
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 50 HP, 1200 RPM, 95.1% | ODP Motor, 50 HP, 1200 RPM, 94.1% | 4000 | 29.729 | 118916.0468 | 29.4164 | 117665.6151 | 0.31261 | 1250.4316 | 0.13881 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 553.23
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 50 HP, 1800 RPM, 95.5% | ODP Motor, 50 HP, 1800 RPM, 94.5% | 4000 | 29.6032 | 118412.6984 | 29.2932 | 117172.7749 | 0.30998 | 1239.9235 | 0.13765 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 553.23
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 50 HP, 3600 RPM, 94% | ODP Motor, 50 HP, 3600 RPM, 93% | 4000 | 30.0806 | 120322.5807 | 29.7606 | 119042.5532 | 0.32001 | 1280.0275 | 0.1421 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 553.23
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 60 HP, 1200 RPM, 95.5% | ODP Motor, 60 HP, 1200 RPM, 94.5% | 4000 | 35.5238 | 142095.2381 | 35.1518 | 140607.3298 | 0.37198 | 1487.9082 | 0.16518 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 690.7
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 60 HP, 1800 RPM, 96% | ODP Motor, 60 HP, 1800 RPM, 95% | 4000 | 35.3368 | 141347.3684 | 34.9688 | 139875 | 0.36809 | 1472.3684 | 0.16345 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 690.7
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 60 HP, 3600 RPM, 94.6% | ODP Motor, 60 HP, 3600 RPM, 93.6% | 4000 | 35.8654 | 143461.5385 | 35.4863 | 141945.0317 | 0.37913 | 1516.5068 | 0.16835 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 690.7
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 7.5 HP, 1200 RPM, 91.2% | ODP Motor, 7.5 HP, 1200 RPM, 90.2% | 4000 | 4.6522 | 18608.6475 | 4.6011 | 18404.6053 | 0.05101 | 204.0422 | 0.022651 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 210.9519
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 7.5 HP, 1800 RPM, 92% | ODP Motor, 7.5 HP, 1800 RPM, 91% | 4000 | 4.6113 | 18445.055 | 4.5611 | 18244.5652 | 0.05012 | 200.4897 | 0.022257 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 210.9519
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 7.5 HP, 3600 RPM, 89.5% | ODP Motor, 7.5 HP, 3600 RPM, 88.5% | 4000 | 4.7415 | 18966.1017 | 4.6886 | 18754.1899 | 0.05298 | 211.9118 | 0.023525 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 210.9519
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 75 HP, 1200 RPM, 95.5% | ODP Motor, 75 HP, 1200 RPM, 94.5% | 4000 | 44.4048 | 177619.0476 | 43.9398 | 175759.1623 | 0.46497 | 1859.8853 | 0.20647 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 867.08
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 75 HP, 1800 RPM, 96% | ODP Motor, 75 HP, 1800 RPM, 95% | 4000 | 44.1711 | 176684.2105 | 43.7109 | 174843.75 | 0.46012 | 1840.4605 | 0.20431 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 867.08
Electric Auxiliary | OPEN DRIP-PROOF (ODP) MOTORS | ODP Motor, 75 HP, 3600 RPM, 94.6% | ODP Motor, 75 HP, 3600 RPM, 93.6% | 4000 | 44.8317 | 179326.9231 | 44.3578 | 177431.2896 | 0.47391 | 1895.6334 | 0.21044 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 867.08
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 1 HP, 1200 RPM, 83.5% | TEFC Motor, 1 HP, 1200 RPM, 82.5% | 4942 | 0.67818 | 3351.5745 | 0.67006 | 3311.4359 | 0.00812 | 40.1386 | 0.0044559 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 66.79
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 1 HP, 1800 RPM, 86.5% | TEFC Motor, 1 HP, 1800 RPM, 85.5% | 4942 | 0.65439 | 3233.9754 | 0.64682 | 3196.5884 | 0.00757 | 37.387 | 0.0041504 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 66.79
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 1 HP, 3600 RPM, 78% | TEFC Motor, 1 HP, 3600 RPM, 77% | 4942 | 0.72662 | 3590.9727 | 0.71731 | 3544.9346 | 0.00932 | 46.0381 | 0.0051108 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 66.79
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 1.5 HP, 1200 RPM, 88.5% | TEFC Motor, 1.5 HP, 1200 RPM, 87.5% | 4942 | 0.97023 | 4794.8827 | 0.95914 | 4740.084 | 0.01109 | 54.7987 | 0.0060833 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 97.73
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 1.5 HP, 1800 RPM, 87.5% | TEFC Motor, 1.5 HP, 1800 RPM, 86.5% | 4942 | 0.97023 | 4794.8827 | 0.95914 | 4740.084 | 0.01109 | 54.7987 | 0.0060833 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 97.73
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 1.5 HP, 3600 RPM, 85% | TEFC Motor, 1.5 HP, 3600 RPM, 84% | 4942 | 0.99911 | 4937.5875 | 0.98735 | 4879.4982 | 0.01175 | 58.0893 | 0.0064486 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 97.73
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 10 HP, 1200 RPM, 92.0% | TEFC Motor, 10 HP, 1200 RPM, 91% | 4942 | 6.1014 | 30153.2061 | 6.0356 | 29827.9288 | 0.06582 | 325.2773 | 0.03611 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 269.08
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 10 HP, 1800 RPM, 92.7% | TEFC Motor, 10 HP, 1800 RPM, 91.7% | 4942 | 6.1014 | 30153.2061 | 6.0356 | 29827.9288 | 0.06582 | 325.2773 | 0.03611 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 269.08
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 10 HP, 3600 RPM, 91.2% | TEFC Motor, 10 HP, 3600 RPM, 90.2% | 4942 | 6.2514 | 30894.4022 | 6.1823 | 30553.0276 | 0.06908 | 341.3746 | 0.037897 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 269.08
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 100 HP, 1200 RPM, 96% | TEFC Motor, 100 HP, 1200 RPM, 95% | 4942 | 58.8947 | 291057.7895 | 58.2812 | 288025.9375 | 0.61349 | 3031.852 | 0.33657 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 1132.7
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 100 HP, 1800 RPM, 96.4% | TEFC Motor, 100 HP, 1800 RPM, 95.4% | 4942 | 58.6478 | 289837.4214 | 58.0394 | 286830.8091 | 0.60838 | 3006.6123 | 0.33377 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 1132.7
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 100 HP, 3600 RPM, 95.1% | TEFC Motor, 100 HP, 3600 RPM, 94.1% | 4942 | 59.7756 | 295411.218 | 59.1438 | 292288.4778 | 0.63188 | 3122.7402 | 0.34666 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 1132.7
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 125 HP, 1200 RPM, 96% | TEFC Motor, 125 HP, 1200 RPM, 95% | 4942 | 73.6184 | 363822.2368 | 72.8516 | 360032.4219 | 0.76686 | 3789.815 | 0.42072 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 4360.9067
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 125 HP, 1800 RPM, 96.4% | TEFC Motor, 125 HP, 1800 RPM, 95.4% | 4942 | 73.3097 | 362296.7767 | 72.5493 | 358538.5114 | 0.76047 | 3758.2653 | 0.41721 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 4360.9067
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 125 HP, 3600 RPM, 96% | TEFC Motor, 125 HP, 3600 RPM, 95% | 4942 | 74.3225 | 367301.9394 | 73.541 | 363439.6688 | 0.78152 | 3862.2707 | 0.42876 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 4360.9067
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 15 HP, 1200 RPM, 92.7% | TEFC Motor, 15 HP, 1200 RPM, 91.7% | 4942 | 9.1521 | 45229.8092 | 9.0534 | 44741.8932 | 0.09873 | 487.916 | 0.054165 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 234.99
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 15 HP, 1800 RPM, 93.4% | TEFC Motor, 15 HP, 1800 RPM, 92.4% | 4942 | 9.0242 | 44597.5645 | 8.9282 | 44123.1223 | 0.096 | 474.4422 | 0.052669 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 234.99
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 15 HP, 3600 RPM, 92.0% | TEFC Motor, 15 HP, 3600 RPM, 91% | 4942 | 9.3043 | 45981.9679 | 9.2023 | 45477.7796 | 0.10202 | 504.1882 | 0.055971 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 234.99
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 150 HP, 1200 RPM, 96.8% | TEFC Motor, 150 HP, 1200 RPM, 95.8% | 4942 | 87.9717 | 434756.1321 | 87.0591 | 430246.2137 | 0.91257 | 4509.9184 | 0.50066 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 5318.51
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 150 HP, 1800 RPM, 96.8% | TEFC Motor, 150 HP, 1800 RPM, 95.8% | 4942 | 87.6044 | 432940.8664 | 86.6994 | 428468.3368 | 0.905 | 4472.5296 | 0.49651 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 5318.51
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 150 HP, 3600 RPM, 96% | TEFC Motor, 150 HP, 3600 RPM, 95% | 4942 | 89.187 | 440762.3273 | 88.2492 | 436127.6025 | 0.93782 | 4634.7248 | 0.51451 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 5318.51
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 2 HP, 1200 RPM, 89.5% | TEFC Motor, 2 HP, 1200 RPM, 88.5% | 4942 | 1.2789 | 6320.112 | 1.2644 | 6248.6983 | 0.01445 | 71.4137 | 0.0079278 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 105.01
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 2 HP, 1800 RPM, 87.5% | TEFC Motor, 2 HP, 1800 RPM, 86.5% | 4942 | 1.2936 | 6393.1769 | 1.2789 | 6320.112 | 0.01478 | 73.0649 | 0.0081111 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 105.01
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 2 HP, 3600 RPM, 86.5% | TEFC Motor, 2 HP, 3600 RPM, 85.5% | 4942 | 1.3088 | 6467.9509 | 1.2936 | 6393.1769 | 0.01513 | 74.774 | 0.0083008 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 105.01
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 20 HP, 1200 RPM, 92.7% | TEFC Motor, 20 HP, 1200 RPM, 91.7% | 4942 | 12.1104 | 59849.5454 | 11.9807 | 59208.758 | 0.12966 | 640.7874 | 0.071135 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 263.31
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 20 HP, 1800 RPM, 94% | TEFC Motor, 20 HP, 1800 RPM, 93% | 4942 | 12.0323 | 59463.4193 | 11.9043 | 58830.8298 | 0.128 | 632.5896 | 0.070225 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 263.31
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 20 HP, 3600 RPM, 92% | TEFC Motor, 20 HP, 3600 RPM, 91% | 4942 | 12.2967 | 60770.3077 | 12.163 | 60109.7609 | 0.13366 | 660.5468 | 0.073329 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 263.31
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 200 HP, 1200 RPM, 96.8% | TEFC Motor, 200 HP, 1200 RPM, 95.8% | 4942 | 117.2956 | 579674.8428 | 116.0788 | 573661.6183 | 1.2168 | 6013.2245 | 0.66754 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 6123.7737
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 200 HP, 1800 RPM, 97.2% | TEFC Motor, 200 HP, 1800 RPM, 96.2% | 4942 | 116.8059 | 577254.4885 | 115.5992 | 571291.1157 | 1.2067 | 5963.3728 | 0.66201 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 6123.7737
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 200 HP, 3600 RPM, 96.4% | TEFC Motor, 200 HP, 3600 RPM, 95.4% | 4942 | 117.7895 | 582115.5789 | 116.5625 | 576051.875 | 1.227 | 6063.704 | 0.67315 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 6123.7737
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 25 HP, 1200 RPM, 94% | TEFC Motor, 25 HP, 1200 RPM, 93% | 4942 | 15.0403 | 74329.2742 | 14.8803 | 73538.5372 | 0.16 | 790.737 | 0.087781 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 322.7969
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 25 HP, 1800 RPM, 94.6% | TEFC Motor, 25 HP, 1800 RPM, 93.6% | 4942 | 14.9439 | 73852.8045 | 14.7859 | 73072.1194 | 0.15797 | 780.685 | 0.086666 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 322.7969
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 25 HP, 3600 RPM, 92.7% | TEFC Motor, 25 HP, 3600 RPM, 91.7% | 4942 | 15.2535 | 75383.0153 | 15.089 | 74569.822 | 0.16455 | 813.1933 | 0.090274 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 322.7969
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 250 HP, 1200 RPM, 96.8% | TEFC Motor, 250 HP, 1200 RPM, 95.8% | 4000 | 147.9541 | 591816.2839 | 146.4256 | 585702.4793 | 1.5285 | 6114 | 0.67873 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 7258.34
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 250 HP, 1800 RPM, 97.2% | TEFC Motor, 250 HP, 1800 RPM, 96.2% | 4000 | 147.3389 | 589355.5094 | 145.823 | 583292.1811 | 1.5158 | 6063 | 0.67307 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 7258.34
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 250 HP, 3600 RPM, 96.8% | TEFC Motor, 250 HP, 3600 RPM, 95.8% | 4000 | 147.9541 | 591816.2839 | 146.4256 | 585702.4793 | 1.5285 | 6114 | 0.67873 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 7258.34
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 3 HP, 1200 RPM, 90.5% | TEFC Motor, 3 HP, 1200 RPM, 89.5% | 4942 | 1.8966 | 9373.0475 | 1.8754 | 9268.3207 | 0.02119 | 104.7268 | 0.011626 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 120.89
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 3 HP, 1800 RPM, 90.5% | TEFC Motor, 3 HP, 1800 RPM, 89.5% | 4942 | 1.8754 | 9268.3207 | 1.8547 | 9165.9083 | 0.02072 | 102.4124 | 0.011369 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 120.89
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 3 HP, 3600 RPM, 87.5% | TEFC Motor, 3 HP, 3600 RPM, 86.5% | 4942 | 1.9632 | 9701.9263 | 1.9405 | 9589.7653 | 0.0227 | 112.161 | 0.012451 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 120.89
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 30 HP, 1200 RPM, 94% | TEFC Motor, 30 HP, 1200 RPM, 93% | 4942 | 17.9327 | 88623.3654 | 17.7431 | 87686.5433 | 0.18956 | 936.822 | 0.104 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 385.46
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 30 HP, 1800 RPM, 94.6% | TEFC Motor, 30 HP, 1800 RPM, 93.6% | 4942 | 17.8374 | 88152.4655 | 17.6498 | 87225.5205 | 0.18756 | 926.945 | 0.1029 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 385.46
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 30 HP, 3600 RPM, 92.7% | TEFC Motor, 30 HP, 3600 RPM, 91.7% | 4942 | 18.3042 | 90459.6183 | 18.1068 | 89483.7864 | 0.19746 | 975.8319 | 0.10833 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 385.46
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 300 HP, 1200 RPM, 96.8% | TEFC Motor, 300 HP, 1200 RPM, 95.8% | 4000 | 177.5449 | 710179.5407 | 175.7107 | 702842.9752 | 1.8341 | 7337 | 0.8145 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 8739.5567
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 300 HP, 1800 RPM, 97.2% | TEFC Motor, 300 HP, 1800 RPM, 96.2% | 4000 | 176.8067 | 707226.6112 | 174.9877 | 699950.6173 | 1.819 | 7276 | 0.80772 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 8739.5567
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 300 HP, 3600 RPM, 96.8% | TEFC Motor, 300 HP, 3600 RPM, 95.8% | 4000 | 177.5449 | 710179.5407 | 175.7107 | 702842.9752 | 1.8341 | 7337 | 0.8145 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 8739.5567
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 40 HP, 1200 RPM, 95.1% | TEFC Motor, 40 HP, 1200 RPM, 94.1% | 4942 | 23.7832 | 117536.6206 | 23.5331 | 116300.694 | 0.25009 | 1235.9266 | 0.1372 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 459
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 40 HP, 1800 RPM, 95.1% | TEFC Motor, 40 HP, 1800 RPM, 94.1% | 4942 | 23.7832 | 117536.6206 | 23.5331 | 116300.694 | 0.25009 | 1235.9266 | 0.1372 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 459
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 40 HP, 3600 RPM, 93.4% | TEFC Motor, 40 HP, 3600 RPM, 92.4% | 4942 | 24.2208 | 119699.0909 | 23.9615 | 118417.5161 | 0.25932 | 1281.5748 | 0.14227 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 459
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 5 HP, 1200 RPM, 90.5% | TEFC Motor, 5 HP, 1200 RPM, 89.5% | 4942 | 3.1257 | 15447.2011 | 3.0912 | 15276.5138 | 0.03454 | 170.6873 | 0.018948 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 166.98
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 5 HP, 1800 RPM, 90.5% | TEFC Motor, 5 HP, 1800 RPM, 89.5% | 4942 | 3.1257 | 15447.2011 | 3.0912 | 15276.5138 | 0.03454 | 170.6873 | 0.018948 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 166.98
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 5 HP, 3600 RPM, 89.5% | TEFC Motor, 5 HP, 3600 RPM, 88.5% | 4942 | 3.2341 | 15982.9422 | 3.1971 | 15800.28 | 0.03696 | 182.6622 | 0.020278 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 166.98
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 50 HP, 1200 RPM, 95.1% | TEFC Motor, 50 HP, 1200 RPM, 94.1% | 4942 | 29.729 | 146920.7758 | 29.4164 | 145375.8675 | 0.31261 | 1544.9083 | 0.1715 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 553.23
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 50 HP, 1800 RPM, 95.5% | TEFC Motor, 50 HP, 1800 RPM, 94.5% | 4942 | 29.6032 | 146298.8889 | 29.2932 | 144766.9634 | 0.30998 | 1531.9255 | 0.17006 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 553.23
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 50 HP, 3600 RPM, 94% | TEFC Motor, 50 HP, 3600 RPM, 93% | 4942 | 30.0806 | 148658.5484 | 29.7606 | 147077.0745 | 0.32001 | 1581.4739 | 0.17556 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 553.23
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 60 HP, 1200 RPM, 95.5% | TEFC Motor, 60 HP, 1200 RPM, 94.5% | 4942 | 35.5238 | 175558.6667 | 35.1518 | 173720.356 | 0.37198 | 1838.3106 | 0.20407 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 690.7
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 60 HP, 1800 RPM, 96% | TEFC Motor, 60 HP, 1800 RPM, 95% | 4942 | 35.3368 | 174634.6737 | 34.9688 | 172815.5625 | 0.36809 | 1819.1112 | 0.20194 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 690.7
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 60 HP, 3600 RPM, 94.6% | TEFC Motor, 60 HP, 3600 RPM, 93.6% | 4942 | 35.8654 | 177246.7308 | 35.4863 | 175373.0867 | 0.37913 | 1873.6441 | 0.208 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 690.7
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 7.5 HP, 1200 RPM, 92.0% | TEFC Motor, 7.5 HP, 1200 RPM, 91% | 4942 | 4.6522 | 22990.9839 | 4.6011 | 22738.8898 | 0.05101 | 252.0941 | 0.027986 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 210.9519
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 7.5 HP, 1800 RPM, 92.7% | TEFC Motor, 7.5 HP, 1800 RPM, 91.7% | 4942 | 4.6113 | 22788.8654 | 4.5611 | 22541.1603 | 0.05012 | 247.7051 | 0.027498 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 210.9519
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 7.5 HP, 3600 RPM, 90.5% | TEFC Motor, 7.5 HP, 3600 RPM, 89.5% | 4942 | 4.7415 | 23432.6186 | 4.6886 | 23170.8017 | 0.05298 | 261.817 | 0.029065 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 210.9519
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 75 HP, 1200 RPM, 95.5% | TEFC Motor, 75 HP, 1200 RPM, 94.5% | 4942 | 44.4048 | 219448.3333 | 43.9398 | 217150.445 | 0.46497 | 2297.8883 | 0.25509 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 867.08
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 75 HP, 1800 RPM, 96.4% | TEFC Motor, 75 HP, 1800 RPM, 95% | 4942 | 44.1711 | 218293.3421 | 43.7109 | 216019.4531 | 0.46012 | 2273.889 | 0.25243 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 867.08
Electric Auxiliary | TOTALLY ENCLOSED FAN-COOLED (TEFC) MOTORS | TEFC Motor, 75 HP, 3600 RPM, 94.6% | TEFC Motor, 75 HP, 3600 RPM, 93.6% | 4942 | 44.8317 | 221558.4135 | 44.3578 | 219216.3583 | 0.47391 | 2342.0551 | 0.26 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 867.08
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 1 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 0.25 | 1007 | 0.11179 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 1818.17
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 1.5 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 0.37 | 1493 | 0.16574 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 1870.71
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 10 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 2.35 | 9391 | 1.0425 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 3673.04
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 100 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 22.57 | 90271 | 10.0212 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 23935.39
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 125 HP, 66% Load Factor | No VFD Installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 28.21 | 112840 | 12.5266 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 27073.45
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 15 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 3.47 | 13890 | 1.542 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 4199.66
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 150 HP, 66% Load Factor | No VFD Installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 33.71 | 134840 | 14.9689 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 30024.42
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 2 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 0.5 | 1991 | 0.22103 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 2650.17
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 20 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 4.63 | 18520 | 2.0559 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 4527.3
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 200 HP, 66% Load Factor | No VFD Installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 44.95 | 179790 | 19.9589 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 38276.96
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 25 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 5.75 | 23002 | 2.5535 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 5762.33
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 250 HP, 66% Load Factor | No VFD Installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 56.2 | 225250 | 25.0055 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 39124.45
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 3 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 0.72 | 2887 | 0.32049 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 2779.8
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 30 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 6.86 | 27455 | 3.0478 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 7612.12
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 300 HP, 66% Load Factor | No VFD Installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 67.42 | 270300 | 30.0066 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 42837.87
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 40 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 9.15 | 36607 | 4.0638 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 8178.7
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 5 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 1.2 | 4811 | 0.53408 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 2969.31
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 50 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 11.39 | 45565 | 5.0583 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 12510.36
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 60 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 13.6 | 54390 | 6.038 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 13294.42
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 7.5 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 1.77 | 7098 | 0.78796 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 3333.91
Electric Auxiliary | VARIABLE FREQUENCY DRIVE (VFD) | Motor Size: 75 HP, 66% Load Factor | No VFD installed, Motor is at 75% Load Factor | 4000 | - | - | - | - | 17 | 67988 | 7.5475 | 15 | EM&V-Commercial-HVAC_Fans_Pumps | 21024.32
Multi-Residential In Suite Appliance | ENERGY STAR® REFRIGERATOR | Energy Star® Refrigerator | Standard Refrigerator | 3000 | - | - | - | - | 0.21 | 350 | 0.041692 | 17 | PSP-Business-Restaurant-Refrigeration | 35
Multi-Residential In Suite Appliance | IN-SUITE TEMPERATURE CONTROLS FOR ELECTRIC SPACE HEATING & COOLING | In-suite temperature controls for electric space heating & cooling | No In-suite temperature controls for electric space heating & cooling |  | - | - | - | - | 0 | 1155 | 0.29593 | 11 | EM&V-Commercial-Space_Cooling_&_Heating | 370
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (FREEZER WALK-IN) | Motor Size >= 1/20 hp to < 1/10 hp | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | 8273 | - | - | - | - | 0.07891 | 652.8603 | 0.076309 | 15 | PSP-Business-Commercial-Refrigeration | 300
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (REFRIGERATOR WALK-IN) | Motor Size >= 1/20 hp to < 1/10 hp | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | 8273 | - | - | - | - | 0.0619 | 542.244 | 0.063379 | 15 | PSP-Business-Commercial-Refrigeration | 300
Residential Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | <100 W (<0.134HP) | Circulator pump with PSC motor | 2190 | 0.28 | 613.2 | 0.05 | 109.5 | 0.23 | 503.7 | 0.052041 | 15 | PSP-Consumer-Residential-Domestic_Hot_Water | 1225
Residential Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=100<500 W (>=0.134<0.67HP) | Circulator pump with PSC motor | 2190 | 1.39 | 3044.1 | 0.25 | 547.5 | 1.14 | 2496.6 | 0.25794 | 15 | PSP-Consumer-Residential-Domestic_Hot_Water | 1536
Residential Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=1490<2237 W (>=2<3HP) | Circulator pump with PSC motor | 2190 | 9.75 | 21352.5 | 1.76 | 3854.4 | 7.99 | 17498.1 | 1.8079 | 15 | PSP-Consumer-Residential-Domestic_Hot_Water | 1896
Residential Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=500<750 W (>=0.67<1HP) | Circulator pump with PSC motor | 2190 | 3.89 | 8519.1 | 0.7 | 1533 | 3.19 | 6986.1 | 0.72179 | 15 | PSP-Consumer-Residential-Domestic_Hot_Water | 1599
Residential Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=750<1490 W (>=1<2HP) | Circulator pump with PSC motor | 2190 | 4.88 | 10687.2 | 0.88 | 1927.2 | 4 | 8760 | 0.90506 | 15 | PSP-Consumer-Residential-Domestic_Hot_Water | 1800
Residential Domestic Hot Water | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | 2237 W (3HP) | Circulator pump with PSC motor | 2190 | 14.63 | 32039.7 | 2.63 | 5759.7 | 12 | 26280 | 2.7152 | 15 | PSP-Consumer-Residential-Domestic_Hot_Water | 2592
Space Cooling | ADVANCED ROOFTOP UNIT CONTROLS | Single-zone packaged RTU with single-speed supply fan retrofitted with advanced controls (>=11.4 ton to <19.9 tons) | Single-zone packaged rooftop unit with single-speed supply fan | - | - | - | - | - | 0 | 9691 | 4.9542 | 12 | EM&V-Commercial-Cooling | 9390
Space Cooling | ADVANCED ROOFTOP UNIT CONTROLS | Single-zone packaged RTU with single-speed supply fan retrofitted with advanced controls (>=19.9 ton to <63.4 tons) | Single-zone packaged rooftop unit with single-speed supply fan | - | - | - | - | - | 0 | 25759 | 13.1685 | 12 | EM&V-Commercial-Cooling | 24990
Space Cooling | ADVANCED ROOFTOP UNIT CONTROLS | Single-zone packaged RTU with single-speed supply fan retrofitted with advanced controls (>=3.0 ton to <5.4 tons) | Single-zone packaged rooftop unit with single-speed supply fan | - | - | - | - | - | 0 | 1672 | 0.85476 | 12 | EM&V-Commercial-Cooling | 2520
Space Cooling | ADVANCED ROOFTOP UNIT CONTROLS | Single-zone packaged RTU with single-speed supply fan retrofitted with advanced controls (>=5.4 ton to <11.4 tons) | Single-zone packaged rooftop unit with single-speed supply fan | - | - | - | - | - | 0 | 5201 | 2.6589 | 12 | EM&V-Commercial-Cooling | 5040
Space Cooling | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | <100 W (<0.134HP) | Circulator pump with PSC motor | 1191 | 0.28 | 333.48 | 0.05 | 59.55 | 0.23 | 273.93 | 0.14008 | 15 | PSP-Business-Commercial-Cooling_Chillers | 1225
Space Cooling | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=100<500 W (>=0.134<0.67HP) | Circulator pump with PSC motor | 1191 | 1.39 | 1655.49 | 0.25 | 297.75 | 1.14 | 1357.74 | 0.69429 | 15 | PSP-Business-Commercial-Cooling_Chillers | 1536
Space Cooling | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=1490<2237 W (>=2<3HP) | Circulator pump with PSC motor | 1191 | 9.75 | 11612.25 | 1.76 | 2096.16 | 7.99 | 9516.09 | 4.8661 | 15 | PSP-Business-Commercial-Cooling_Chillers | 1896
Space Cooling | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=500<750 W (>=0.67<1HP) | Circulator pump with PSC motor | 1191 | 3.89 | 4632.99 | 0.7 | 833.7 | 3.19 | 3799.29 | 1.9428 | 15 | PSP-Business-Commercial-Cooling_Chillers | 1599
Space Cooling | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=750<1490 W (>=1<2HP) | Circulator pump with PSC motor | 1191 | 4.88 | 5812.08 | 0.88 | 1048.08 | 4 | 4764 | 2.4361 | 15 | PSP-Business-Commercial-Cooling_Chillers | 1800
Space Cooling | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | 2237 W (3HP) | Circulator pump with PSC motor | 1191 | 14.63 | 17424.33 | 2.63 | 3132.33 | 12 | 14292 | 7.3083 | 15 | PSP-Business-Commercial-Cooling_Chillers | 2592
Space Cooling | ECM MOTORS FOR HVAC APPLICATION (FAN MOTOR REPLACEMENT) | Motor < 1 hp | VAV Box with PSC motors | 3000 | - | - | - | - | 0.3837 | 1205 | 0.61619 | 15 | PSP-Business-Other_Commercial_Buildings-Cooling_DX | 524
Space Cooling | ECM MOTORS FOR HVAC APPLICATION (FAN-POWERED VAV BOX) | VAV Units < 1000 CFM | VAV Box with PSC motors | 3000 | - | - | - | - | 0.18 | 500 | 0.25568 | 15 | PSP-Business-Other_Commercial_Buildings-Cooling_DX | 380
Space Cooling | ECM MOTORS FOR HVAC APPLICATION (FAN-POWERED VAV BOX) | VAV Units > 1000 CFM | VAV Box with PSC motors | 3000 | - | - | - | - | 0.32 | 350 | 0.17897 | 15 | PSP-Business-Other_Commercial_Buildings-Cooling_DX | 640
Space Cooling | HOTEL OCCUPANCY CONTROLS (HVAC + LIGHTING) | Electrically heated facility | No controls installed | - | - | - | - | - | - | 310 | 0.15852 | 10 | PSP-Business-Other_Commercial_Buildings-Cooling_DX | 670
Space Cooling | HOTEL OCCUPANCY CONTROLS (HVAC + LIGHTING) | Gas heated facility | No controls installed | - | - | - | - | - | - | 122 | 0.062386 | 10 | PSP-Business-Other_Commercial_Buildings-Cooling_DX | 670
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Single Package with Economizer >= 3.0 to < 5.4 tons, All Heating Type, 12.5 EER | Single Package with Economizer >= 3.0 to < 5.4 tons, All Heating Type, 13.0 SEER (Approximately 11.14 EER) | 600 | - | - | - | - | 0.49321 | 295.9282 | 0.15128 | 15 | EM&V-Commercial-Cooling | 1428
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Single Package with Economizer >= 5.4 to <= 7.5 tons, All Other Heating, 12.0 EER / 13.8 IEER | Single Package with Economizer >= 5.4 to <= 7.5 tons, All Other Heating, 11 EER / 12.7 IEER | 600 | - | - | - | - | 0.58712 | 352.2727 | 0.18009 | 15 | EM&V-Commercial-Cooling | 2193
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Single Package with Economizer >= 5.4 to <= 7.5 tons, Electric Resistance, 12.2 EER / 14.0 IEER | Single Package with Economizer >= 5.4 to <= 7.5 tons, Electric Resistance, 11.2 EER / 12.9 IEER | 600 | - | - | - | - | 0.56718 | 340.3103 | 0.17397 | 15 | EM&V-Commercial-Cooling | 2193
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System >= 3.0 to < 5.4 tons, All Heating Type, 12.5 EER | Split System >= 3.0 to < 5.4 tons, All Heating Type, 13.0 SEER (Approximately 11.14 EER) | 600 | - | - | - | - | 0.49321 | 295.9282 | 0.15128 | 15 | EM&V-Commercial-Cooling | 1428
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System >= 5.4 to <= 7.5 tons, All Other Heating, 12.0 EER / 13.8 IEER | Split System >= 5.4 to <= 7.5 tons, All Other Heating, 11 EER / 12.7 IEER | 600 | - | - | - | - | 0.58712 | 352.2727 | 0.18009 | 15 | EM&V-Commercial-Cooling | 2193
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System >= 5.4 to <= 7.5 tons, Electric Resistance, 12.2 EER / 14.0 IEER | Split System >= 5.4 to <= 7.5 tons, Electric Resistance, 11.2 EER / 12.9 IEER | 600 | - | - | - | - | 0.56718 | 340.3103 | 0.17397 | 15 | EM&V-Commercial-Cooling | 2193
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System/Single Package >= 11.25 to < 20 tons, All Other, 12.0 EER / 14.0 IEER | Split System/Single Package >= 11.25 to < 20 tons, All Other, 10.8 EER / 12.2 IEER | 600 | - | - | - | - | 1.7361 | 1041.6667 | 0.53252 | 15 | EM&V-Commercial-Cooling | 3906.25
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System/Single Package >= 11.25 to < 20 tons, Electric Resistance, 12.2 EER / 14.2 IEER | Split System/Single Package >= 11.25 to < 20 tons, Electric Resistance, 11 EER / 12.4 IEER | 600 | - | - | - | - | 1.6766 | 1005.9612 | 0.51427 | 15 | EM&V-Commercial-Cooling | 3906.25
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System/Single Package >= 20 to < 63 tons, All Other, 10.6 EER / 13.0 IEER | Split System/Single Package >= 20 to < 63 tons, All Other, 9.8 EER / 11.4 IEER | 600 | - | - | - | - | 3.8506 | 2310.3581 | 1.1811 | 15 | EM&V-Commercial-Cooling | 7470
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System/Single Package >= 20 to < 63 tons, Electric Resistance, 10.8 EER / 13.2 IEER | Split System/Single Package >= 20 to < 63 tons, Electric Resistance, 10 EER / 11.6 IEER | 600 | - | - | - | - | 3.7037 | 2222.2222 | 1.136 | 15 | EM&V-Commercial-Cooling | 7470
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System/Single Package >= 63 tons, All Other, 10.2 EER / 12.1 IEER | Split System/Single Package >= 63 tons, All Other, 9.5 EER / 11.1 IEER | 600 | - | - | - | - | 5.4902 | 3294.1177 | 1.684 | 15 | EM&V-Commercial-Cooling | 11340
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System/Single Package >= 63 tons, Electric Resistance, 10.4 EER / 12.3 IEER | Split System/Single Package >= 63 tons, Electric Resistance, 9.7 EER / 11.3 IEER | 600 | - | - | - | - | 5.2736 | 3164.1554 | 1.6176 | 15 | EM&V-Commercial-Cooling | 11340
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System/Single Package >= 7.5 to < 11.25 tons, All Other, 12.0 EER /13.8 IEER | Split System/Single Package >= 7.5 to < 11.25 tons, All Other, 11 EER/12.7 IEER | 600 | - | - | - | - | 0.85227 | 511.3636 | 0.26142 | 15 | EM&V-Commercial-Cooling | 2343.75
Space Cooling | UNITARY AIR-CONDITIONING UNIT | Split System/Single Package >= 7.5 to < 11.25 tons, Electric Resistance, 12.2 EER / 14.0 IEER | Split System/Single Package >= 7.5 to < 11.25 tons, Electric Resistance, 11.2 EER / 12.9 IEER | 600 | - | - | - | - | 0.82333 | 493.9988 | 0.25254 | 15 | EM&V-Commercial-Cooling | 2343.75
Space Cooling and Heating | PACKAGED TERMINAL AIR CONDITIONERS (PTAC) | Cooling Capacity <7000 Btu/h and EER >= 12.9 | Cooling Capacity <7000 Btu/h and EER = 11.9 | 650 | - | - | - | - | 0.0456 | 29.6398 | 0.0069149 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 135.3
Space Cooling and Heating | PACKAGED TERMINAL AIR CONDITIONERS (PTAC) | Cooling Capacity >=7000 Btu/h & <=15000 Btu/h and EER >= [14.0-(0.3 × Cap)] x 1.06 | Cooling Capacity >=7000 Btu/h & <=15000 Btu/h and EER = 14.0-(0.3 × Cap) | 650 | - | - | - | - | 0.058191 | 37.824 | 0.0088242 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 216.3
Space Cooling and Heating | PACKAGED TERMINAL AIR CONDITIONERS (PTAC) | Cooling Capacity >15000 Btu/h and EER >= 10.5 | Cooling Capacity >15000 Btu/h and EER = 9.5 | 650 | - | - | - | - | 0.14354 | 93.3014 | 0.021767 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 307.5
Space Cooling and Heating | PACKAGED TERMINAL HEAT PUMPS (PTHP) | Cooling Capacity <7000 Btu/h and EER >= 12.9 and COP >= 3.5 | Cooling Capacity <7000 Btu/h and EER = 11.9 and COP = 3.3 | 2650 | - | - | - | - | 0.0456 | 100.6902 | 0.023491 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 68.8
Space Cooling and Heating | PACKAGED TERMINAL HEAT PUMPS (PTHP) | Cooling Capacity >=7000 Btu/h & <=15000 Btu/h and EER >= [14.0 - (0.3 × Cap)] x 1.06 and COP >= [3.7 - (0.052 x Cap)] x 1.06 | Cooling Capacity >=7000 Btu/h & <=15000 Btu/h and EER = 14.0 - (0.3 × Cap) and COP = 3.7 - (0.052 x Cap) | 2650 | - | - | - | - | 0.058191 | 154.5029 | 0.036045 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 108.2
Space Cooling and Heating | PACKAGED TERMINAL HEAT PUMPS (PTHP) | Cooling Capacity >15000 Btu/h and EER >= 10.5 and COP >= 3.2 | Cooling Capacity >15000 Btu/h and EER = 9.5 and COP =2.9 | 2650 | - | - | - | - | 0.14354 | 368.9283 | 0.08607 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 147.5
Space Cooling and Heating | ROOM AIR CONDITIONERS | <8,000 Btu/h and CEER >= 12.1 | <8,000 Btu/h and CEER >= 11.0 | 200 | - | - | - | - | 0.0795 | 15.8992 | 0.008128 | 10 | EM&V-Commercial-Cooling | 76
Space Cooling and Heating | ROOM AIR CONDITIONERS | >=28000 Btu/h and CEER >= 9.9 | >=28000 Btu/h and CEER >= 9.0 | 200 | - | - | - | - | 0.29857 | 59.7143 | 0.030527 | 10 | EM&V-Commercial-Cooling | 76
Space Cooling and Heating | ROOM AIR CONDITIONERS | 14000 to 19999 Btu/h and CEER >= 11.8 | 14000 to 19999 Btu/h and CEER >= 10.7 | 200 | - | - | - | - | 0.21188 | 42.377 | 0.021664 | 10 | EM&V-Commercial-Cooling | 76
Space Cooling and Heating | ROOM AIR CONDITIONERS | 20000 to 27999 Btu/h and CEER >= 10.3 | 20000 to 27999 Btu/h and CEER >= 9.4 | 200 | - | - | - | - | 0.25905 | 51.3509 | 0.026252 | 10 | EM&V-Commercial-Cooling | 76
Space Cooling and Heating | ROOM AIR CONDITIONERS | 8000 to 13999 Btu/h and CEER >= 12.0 | 8000 to 13999 Btu/h and CEER >= 10.9 | 200 | - | - | - | - | 0.13727 | 27.4547 | 0.014035 | 10 | EM&V-Commercial-Cooling | 76
Space Cooling and Heating | UNITARY AIR SOURCE HEAT PUMP (ASHP) - SINGLE PACKAGE AND SPLIT SYSTEM | Single Package >=3.0 to <5.4 Tons, All Heating Type, 12 EER, 15 SEER, 8.2 HSPF | Single Package with Economizer >=3.0 to <5.4 tons, All Heating Type, 14 SEER | 2650 | - | - | - | - | 0.33042 | 2114.7413 | 0.49336 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 3024
Space Cooling and Heating | UNITARY AIR SOURCE HEAT PUMP (ASHP) - SINGLE PACKAGE AND SPLIT SYSTEM | Split System >=3.0 to <5.4 Tons, All Heating Type, 12.5 EER, 15 SEER, 8.5 HSPF | Split System >=3.0 to <5.4 tons, All Heating Type, 14 SEER | 2650 | - | - | - | - | 0.33042 | 2114.7413 | 0.49336 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 3024
Space Cooling and Heating | UNITARY AIR SOURCE HEAT PUMP (ASHP) - SINGLE PACKAGE AND SPLIT SYSTEM | Split System/Single Package >=11.25 to <20.0 Tons, All Other, 10.7 EER, 12.6 IEER, 3.3 COP, 2.1 COP | Split System/Single Package >=11.25 to <20.0 Tons, All Other, 10.4 EER, 11.4 IEER | 2650 | - | - | - | - | 1.4823 | 4811.6946 | 1.1226 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 9844
Space Cooling and Heating | UNITARY AIR SOURCE HEAT PUMP (ASHP) - SINGLE PACKAGE AND SPLIT SYSTEM | Split System/Single Package >=11.25 to <20.0 Tons, Electric Resistance, 10.9 EER, 12.8 IEER, 3.3 COP, 2.1 COP | Split System/Single Package >=11.25 to <20.0 Tons, Electric Resistance, 10.6 EER, 11.6 IEER | 2650 | - | - | - | - | 1.4823 | 4811.6946 | 1.1226 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 9844
Space Cooling and Heating | UNITARY AIR SOURCE HEAT PUMP (ASHP) - SINGLE PACKAGE AND SPLIT SYSTEM | Split System/Single Package >=20.0 to <63.3 Tons, All Other 10.1 EER, 11.6 IEER, 3.3 COP, 2.1 COP | Split System/Single Package >=20.0 to <=63.3 Tons, All Other, 9.3 EER, 10.4 IEER | 2650 | - | - | - | - | 4.3277 | 13330.8066 | 3.11 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 13280
Space Cooling and Heating | UNITARY AIR SOURCE HEAT PUMP (ASHP) - SINGLE PACKAGE AND SPLIT SYSTEM | Split System/Single Package >=20.0 to <63.3 Tons, Electric Resistance, 10.3 EER, 11.8 IEER, 3.3 COP, 2.1 COP | Split System/Single Package >=20.0 to <=63.3 Tons, Electric Resistance, 9.5 EER, 10.6 IEER | 2650 | - | - | - | - | 4.3277 | 13330.8066 | 3.11 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 13280
Space Cooling and Heating | UNITARY AIR SOURCE HEAT PUMP (ASHP) - SINGLE PACKAGE AND SPLIT SYSTEM | Split System/Single Package >=5.4 to <11.25 Tons, All Other, 11.6 EER, 13.4 IEER, 3.4 COP, 2.4 COP | Split System/Single Package >=5.4 to <11.25 tons, All Other, 10.8 EER, 12.0 IEER | 2650 | - | - | - | - | 0.751 | 2476.8955 | 0.57785 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 5744
Space Cooling and Heating | UNITARY AIR SOURCE HEAT PUMP (ASHP) - SINGLE PACKAGE AND SPLIT SYSTEM | Split System/Single Package >=5.4 to <11.25 Tons, Electric Resistance (or None), 11.8 EER, 13.6 IEER, 3.4 COP, 2.4 COP | Split System/Single Package >=5.4 to <11.25 Tons, Electric Resistance, 11.0 EER, 12.2 IEER | 2650 | - | - | - | - | 0.751 | 2476.8955 | 0.57785 | 15 | PSP-Business-Commercial-Space_Cooling_&_Heating | 5744
Space Heating | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | <100 W (<0.134HP) | Circulator pump with PSC motor | 2582 | 0.28 | 722.96 | 0.05 | 129.1 | 0.23 | 593.86 | 0.032376 | 15 | PSP-Business-Commercial-Forced_Air_Central_Heating | 1225
Space Heating | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=100<500 W (>=0.134<0.67HP) | Circulator pump with PSC motor | 2582 | 1.39 | 3588.98 | 0.25 | 645.5 | 1.14 | 2943.48 | 0.16047 | 15 | PSP-Business-Commercial-Forced_Air_Central_Heating | 1536
Space Heating | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=1490<2237 W (>=2<3HP) | Circulator pump with PSC motor | 2582 | 9.75 | 25174.5 | 1.76 | 4544.32 | 7.99 | 20630.18 | 1.1247 | 15 | PSP-Business-Commercial-Forced_Air_Central_Heating | 1896
Space Heating | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=500<750 W (>=0.67<1HP) | Circulator pump with PSC motor | 2582 | 3.89 | 10043.98 | 0.7 | 1807.4 | 3.19 | 8236.58 | 0.44904 | 15 | PSP-Business-Commercial-Forced_Air_Central_Heating | 1599
Space Heating | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | >=750<1490 W (>=1<2HP) | Circulator pump with PSC motor | 2582 | 4.88 | 12600.16 | 0.88 | 2272.16 | 4 | 10328 | 0.56307 | 15 | PSP-Business-Commercial-Forced_Air_Central_Heating | 1800
Space Heating | CIRCULATOR PUMPS WITH ELECTRONICALLY COMMUTATED MOTORS (ECMs) | 2237 W (3HP) | Circulator pump with PSC motor | 2582 | 14.63 | 37774.66 | 2.63 | 6790.66 | 12 | 30984 | 1.6892 | 15 | PSP-Business-Commercial-Forced_Air_Central_Heating | 2592
Lighting - Greenhouses | HORTICULTURAL LED GROW LIGHTS - INTER-LIGHTING | LED fixture installed within the canopy to illuminate a vertical growing surface for both replacement of existing fixtures and installation of new fixtures without replacements | Assumed T8 baseline of 10 fixtures provides the equivlent brightness at the same distance away from the vertical growing surface as one EE fixture. | 4957 | 0.415 | 2057.155 | 0.119 | 589.883 | 0.296 | 1467.292 | 0.0082 | 10 | CUSTOM-Business-Other_Commercial_Buildings-CUSTOM-Industrial-Agriculture-Horticultural Lighting - Veg | _
Lighting - Greenhouses | LED GROW LIGHTS - CANNABIS GREENHOUSES | LED top lighting fixture installed in a cannabis greenhouse | Measure mix of HPS, MH and T5HO | 2120 | 0.84963 | 1801.2156 | 0.40501 | 858.6212 | 0.44462 | 942.5944 | 0.011971 | 20 | CUSTOM-Business-Other_Commercial_Buildings-CUSTOM-Industrial-Agriculture-Horticultural Lighting - Cannabis | LED fixture cost is: ≤ 250 Watts = $ 456 per fixture > 250 Watts = $ 749 per fixture | Updated Incremental Costs
Lighting - Greenhouses | LED GROW LIGHTS - CANNABIS WAREHOUSES | LED top lighting fixture installed in a cannabis warehouse | Measure mix of HPS, MH and T5HO | 5475 | 0.91 | 4982 | 0.3911 | 2142 | 0.519 | 2840 | 0.036072 | 10 | CUSTOM-Business-Other_Commercial_Buildings-CUSTOM-Industrial-Agriculture-Horticultural Lighting - Cannabis | LED fixture cost is: ≤ 250 Watts = $ 456 per fixture > 250 Watts = $ 749 per fixture | Updated Incremental Costs
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) AIR-COOLED | Cooling Capacity <65,000 Btu/h, and SCOP >= 2.47 | Cooling Capacity <65,000 Btu/h, and SCOP >= 2.15 | 8760 | - | - | - | - | 0.43316 | 3794.4687 | 0.43316 | 15 | Custom Load Profile | 3178.3
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) AIR-COOLED | Cooling Capacity >=65,000 Btu/h and <240,000 Btu/h, and SCOP >= 2.35 | Cooling Capacity >=65,000 Btu/h and <240,000 Btu/h, and SCOP >= 2.05 | 8760 | - | - | - | - | 1.6732 | 14657.4958 | 1.6732 | 15 | Custom Load Profile | 11704.97
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) AIR-COOLED | Cooling Capacity =240,000 Btu/h and <760,000 Btu/h and SCOP >= 2.12 | Cooling Capacity =240,000 Btu/h and <760,000 Btu/h and SCOP >= 1.85 | 8760 | - | - | - | - | 4.1697 | 36526.3638 | 4.1697 | 15 | Custom Load Profile | 26316
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) WATER-COOLED | Cooling Capacity <65,000 Btu/h, and SCOP >= 2.93 | Cooling Capacity <65,000 Btu/h, and SCOP >= 2.55 | 8760 | - | - | - | - | 0.36508 | 3198.0885 | 0.36508 | 15 | Custom Load Profile | 3178.3
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) WATER-COOLED | Cooling Capacity >=65,000 Btu/h and <240,000 Btu/h, and SCOP >= 2.81 | Cooling Capacity >=65,000 Btu/h and <240,000 Btu/h, and SCOP >= 2.45 | 8760 | - | - | - | - | 1.3995 | 12259.5415 | 1.3995 | 15 | Custom Load Profile | 11704.97
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) WATER-COOLED | Cooling Capacity =240,000 Btu/h and <760,000 Btu/h and SCOP >= 2.70 | Cooling Capacity =240,000 Btu/h and <760,000 Btu/h and SCOP >= 2.35 | 8760 | - | - | - | - | 3.2806 | 28738.2265 | 3.2806 | 15 | Custom Load Profile | 26316
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) WATER-COOLED W/ FLUID ECONOMIZER | Cooling Capacity <65,000 Btu/h, and SCOP >= 2.87 | Cooling Capacity <65,000 Btu/h, and SCOP >= 2.50 | 8760 | - | - | - | - | 0.37239 | 3262.1785 | 0.37239 | 15 | Custom Load Profile | 3178.3
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) WATER-COOLED W/ FLUID ECONOMIZER | Cooling Capacity >=65,000 Btu/h and <240,000 Btu/h, and SCOP >= 2.75 | Cooling Capacity >=65,000 Btu/h and <240,000 Btu/h, and SCOP >= 2.40 | 8760 | - | - | - | - | 1.4287 | 12515.4818 | 1.4287 | 15 | Custom Load Profile | 11704.97
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) WATER-COOLED W/ FLUID ECONOMIZER | Cooling Capacity =240,000 Btu/h and <760,000 Btu/h and SCOP >= 2.64 | Cooling Capacity >=240,000 Btu/h and <760,000 Btu/h and SCOP >= 2.30 | 8760 | - | - | - | - | 3.3521 | 29364.3317 | 3.3521 | 15 | Custom Load Profile | 26316
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) GLYCOL-COOLED | Cooling Capacity <65,000 Btu/h, and SCOP >= 2.81 | Cooling Capacity <65,000 Btu/h, and SCOP >= 2.45 | 8760 | - | - | - | - | 0.38001 | 3328.8897 | 0.38001 | 15 | Custom Load Profile | 3178.3
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) GLYCOL-COOLED | Cooling Capacity >=65,000 Btu/h and <240,000 Btu/h, and SCOP >= 2.41 | Cooling Capacity >=65,000 Btu/h and <240,000 Btu/h, and SCOP >= 2.10 | 8760 | - | - | - | - | 1.6333 | 14307.6749 | 1.6333 | 15 | Custom Load Profile | 11704.97
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) GLYCOL-COOLED | Cooling Capacity =240,000 Btu/h and <760,000 Btu/h and SCOP >= 2.35 | Cooling Capacity =240,000 Btu/h and <760,000 Btu/h and SCOP >= 2.05 | 8760 | - | - | - | - | 3.7619 | 32954.1033 | 3.7619 | 15 | Custom Load Profile | 26316
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) GLYCOL-COOLED W/ ECONOMIZER | Cooling Capacity <65,000 Btu/h, and SCOP >= 2.75 | Cooling Capacity <65,000 Btu/h, and SCOP >= 2.40 | 8760 | - | - | - | - | 0.38794 | 3398.3864 | 0.38794 | 15 | Custom Load Profile | 3178.3
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) GLYCOL-COOLED W/ ECONOMIZER | Cooling Capacity >=65,000 Btu/h and <240,000 Btu/h, and SCOP >= 2.35 | Cooling Capacity >=65,000 Btu/h and <240,000 Btu/h, and SCOP >= 2.05 | 8760 | - | - | - | - | 1.6732 | 14657.4958 | 1.6732 | 15 | Custom Load Profile | 11704.97
Space Cooling and Heating | COMPUTER ROOM AIR CONDITIONERS (CRAC) GLYCOL-COOLED W/ ECONOMIZER | Cooling Capacity =240,000 Btu/h and <760,000 Btu/h and SCOP >= 2.29 | Cooling Capacity =240,000 Btu/h and <760,000 Btu/h and SCOP >= 2.00 | 8760 | - | - | - | - | 3.8562 | 33780.0207 | 3.8562 | 15 | Custom Load Profile | 26316
Lighting - Greenhouses | HORTICULTURAL LED GROW LIGHTS - VERTICAL FARMING (FOR REPLACEMENT OF EXISTING FIXTURES) | Replacing existing fixture with LED fixture mounted within vertical shelving units that are stacked on top of each other | The baseline is assumed to be a 358W T5/T8 fixture. | 5200 | 0.358 | 1861.6 | 0.184 | 956.8 | 0.174 | 904.8 | 0.0050669 | 9.5 | CUSTOM-Business-Other_Commercial_Buildings-CUSTOM-Industrial-Agriculture-Horticultural Lighting - Veg | -
Lighting - Greenhouses | HORTICULTURAL LED GROW LIGHTS - VERTICAL FARMING (FOR NEW INSTALLATIONS) | New install of LED fixture mounted within vertical shelving units that are stacked on top of each other for new installations (upgrade does not result in replacement of existing equipment) | The baseline is assumed to be LED fixture with the photosynthetic photon efficacy (PPE) of 1.6 µmol/J. | 5200 | 0.20902 | 1086.93 | 0.184 | 956.8 | 0.025025 | 130.13 | 0.00072873 | 9.5 | CUSTOM-Business-Other_Commercial_Buildings-CUSTOM-Industrial-Agriculture-Horticultural Lighting - Veg | -
Data Center | ENERGY STAR-CERTIFIED SERVERS | Energy Star-Certified Server | Non-Energy Star-Certified Server | 8760 |  |  |  |  | 0.328 | 2872 | 0.328 | 4 | Custom Load Profile | 544
Data Center | ENERGY STAR-CERTIFIED UNINTERRUPTIBLE POWER SUPPLY | Energy Star-Certified UPS - Single-normal-mode | Non-Energy Star-Certified UPS - Single-normal-mode | 8760 |  |  |  |  | 0.02 | 145.02 | 0.02 | 15 | Custom Load Profile | 80
Data Center | ENERGY STAR-CERTIFIED UNINTERRUPTIBLE POWER SUPPLY | Energy Star-Certified UPS - Multi-normal-mode | Non-Energy Star-Certified UPS - Multi-normal-mode | 8760 |  |  |  |  | 0.024 | 155.67 | 0.024 | 15 | Custom Load Profile | 80
Data Center | SERVER-VIRTUALIZATION | Server-Virtualization | Non-Virtualized Servers | 8760 |  |  |  |  | 0.82 | 7169 | 0.82 | 4 | Custom Load Profile | 646

## Business-Retrofit Quasi-Pres.
END_USE | CONSERVATION_MEASURE_NAME | DESCRIPTION | BASE_MEASURE | ASSUMED_ANNUAL_OPERATING_HOURS | FIRST_YEAR_DEMAND_SAVINGS | FIRST_YEAR_ENERGY_SAVINGS | PEAK_DEMAND_SAVINGS | EFFECTIVE_USEFUL_LIFE | END_USE_LOAD_PROFILE | INCREMENTAL_LIFE_CYCLE_COST
Chillers | HVAC CHILLER-AIR-COOLED CHILLERS | <150 Tons, <=0.876 kW/Ton IPLV.IP | <150 Tons, <=0.876 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $268/Ton
Chillers | HVAC CHILLER-AIR-COOLED CHILLERS | >=150 Tons, <=0.857 kW/Ton IPLV.IP | >=150 Tons, <=0.857 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $268/Ton
Chillers | HVAC CHILLER-WATER COOLED CENTRIFUGAL | <75 Tons, <=0.550 kW/Ton IPLV.IP | <75 Tons, <=0.550 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $210/Ton
Chillers | HVAC CHILLER-WATER COOLED CENTRIFUGAL | >=150 Tons and <300 Tons, <=0.52 kW/Ton IPLV.IP | >=150 Tons and <300 Tons, <=0.52 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $210/Ton
Chillers | HVAC CHILLER-WATER COOLED CENTRIFUGAL | >=300 Tons and <600 Tons, <=0.500 kW/Ton IPLV.IP | >=300 Tons and <600 Tons, <=0.500 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $210/Ton
Chillers | HVAC CHILLER-WATER COOLED CENTRIFUGAL | >=600 Tons, <=0.500 kW/Ton IPLV.IP | >=600 Tons, <=0.500 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $210/Ton
Chillers | HVAC CHILLER-WATER COOLED CENTRIFUGAL | >=75 Tons and <150 Tons, <=0.550 kW/Ton IPLV.IP | >=75 Tons and <150 Tons, <=0.550 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $210/Ton
Chillers | HVAC CHILLER-WATER COOLED POSITIVE DISPLACEMENT | <75 Tons, <=0.600 kW/Ton IPLV.IP | <75 Tons, <=0.600 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $270/Ton
Chillers | HVAC CHILLER-WATER COOLED POSITIVE DISPLACEMENT | >=150 Tons and <300 Tons, <=0.540 kW/Ton IPLV.IP | >=150 Tons and <300 Tons, <=0.540 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $270/Ton
Chillers | HVAC CHILLER-WATER COOLED POSITIVE DISPLACEMENT | >=300 Tons and <600 Tons, <=0.520 kW/Ton IPLV.IP | >=300 Tons and <600 Tons, <=0.520 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $270/Ton
Chillers | HVAC CHILLER-WATER COOLED POSITIVE DISPLACEMENT | >=600 Tons, <=0.500 kW/Ton IPLV.IP | >=600 Tons, <=0.500 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $270/Ton
Chillers | HVAC CHILLER-WATER COOLED POSITIVE DISPLACEMENT | >=75 Tons and <150 Tons, <=0.560 kW/Ton IPLV.IP | >=75 Tons and <150 Tons, <=0.560 kW/Ton IPLV.IP | 1000 | ΔkW=Tons* ΔIPLV | ΔkWh=Tons*ΔIPLV *EFLHcooling | ΔkW=ΔkWh* SPDF | 23 | EM&V-Commercial-Cooling | $270/Ton
Chillers | PROCESS CHILLER-WATER COOLED CENTRIFUGAL | <75 Tons, <=0.610 kW/Ton FL | <75 Tons, <=0.610 kW/Ton FL | 5700 | ΔkW=Tons* ΔFL | ΔkWh=Tons*ΔFL *Hours | ΔkW=kWh* SPDF | 23 | EM&V-Commercial-Cooling | $210/Ton
Chillers | PROCESS CHILLER-WATER COOLED CENTRIFUGAL | >=150 Tons and <300 Tons, <=0.560 kW/Ton FL | >=150 Tons and <300 Tons, <=0.560 kW/Ton FL | 5700 | ΔkW=Tons* ΔFL | ΔkWh=Tons*ΔFL *Hours | ΔkW=kWh* SPDF | 23 | EM&V-Commercial-Cooling | $210/Ton
Chillers | PROCESS CHILLER-WATER COOLED CENTRIFUGAL | >=300 Tons and <600 Tons, <=0.560 kW/Ton FL | >=300 Tons and <600 Tons, <=0.560 kW/Ton FL | 5700 | ΔkW=Tons* ΔFL | ΔkWh=Tons*ΔFL *Hours | ΔkW=kWh* SPDF | 23 | EM&V-Commercial-Cooling | $210/Ton
Chillers | PROCESS CHILLER-WATER COOLED CENTRIFUGAL | >=600 Tons, <=0.560 kW/Ton FL | >=600 Tons, <=0.560 kW/Ton FL | 5700 | ΔkW=Tons* ΔFL | ΔkWh=Tons*ΔFL *Hours | ΔkW=kWh* SPDF | 23 | EM&V-Commercial-Cooling | $210/Ton
Chillers | PROCESS CHILLER-WATER COOLED CENTRIFUGAL | >=75 Tons and <150 Tons, <=0.610 kW/Ton FL | >=75 Tons and <150 Tons, <=0.610 kW/Ton FL | 5700 | ΔkW=Tons* ΔFL | ΔkWh=Tons*ΔFL *Hours | ΔkW=kWh* SPDF | 23 | EM&V-Commercial-Cooling | $210/Ton
Chillers | PROCESS CHILLER-WATER COOLED POSITIVE DISPLACEMENT | <75 Tons, <=0.750 kW/Ton FL | <75 Tons, <=0.750 kW/Ton FL | 5700 | ΔkW=Tons* ΔFL | ΔkWh=Tons*ΔFL *Hours | ΔkW=kWh* SPDF | 23 | EM&V-Commercial-Cooling | $270/Ton
Chillers | PROCESS CHILLER-WATER COOLED POSITIVE DISPLACEMENT | >=150 Tons and <300 Tons, <=0.660 kW/Ton FL | >=150 Tons and <300 Tons, <=0.660 kW/Ton FL | 5700 | ΔkW=Tons* ΔFL | ΔkWh=Tons*ΔFL *Hours | ΔkW=kWh* SPDF | 23 | EM&V-Commercial-Cooling | $270/Ton
Chillers | PROCESS CHILLER-WATER COOLED POSITIVE DISPLACEMENT | >=300 Tons and <600 Tons, <=0.610 kW/Ton FL | >=300 Tons and <600 Tons, <=0.610 kW/Ton FL | 5700 | ΔkW=Tons* ΔFL | ΔkWh=Tons*ΔFL *Hours | ΔkW=kWh* SPDF | 23 | EM&V-Commercial-Cooling | $270/Ton
Chillers | PROCESS CHILLER-WATER COOLED POSITIVE DISPLACEMENT | >=600 Tons, <=0.560 kW/Ton FL | >=600 Tons, <=0.560 kW/Ton FL | 5700 | ΔkW=Tons* ΔFL | ΔkWh=Tons*ΔFL *Hours | ΔkW=kWh* SPDF | 23 | EM&V-Commercial-Cooling | $270/Ton
Chillers | PROCESS CHILLER-WATER COOLED POSITIVE DISPLACEMENT | >=75 Tons and <150 Tons, <=0.720 kW/Ton FL | >=75 Tons and <150 Tons, <=0.720 kW/Ton FL | 5700 | ΔkW=Tons* ΔFL | ΔkWh=Tons*ΔFL *Hours | ΔkW=kWh* SPDF | 23 | EM&V-Commercial-Cooling | $270/Ton
Electric Auxiliary | VARIABLE SPEED DOMESTIC COLD WATER BOOSTER PUMP SYSTEM | Replacement of a Constant Speed Domestic Cold Water Booster Pump System with a Variable Speed Domestic Cold Water Booster Pump System | Constant Speed Domestic Cold Water Booster Pump System |  | ΔkW=HP*0.12433 kW/HP | ΔkWh=HP*4414 kWh/HP | ΔkW=kWh *SPDF | 15 | Custom-Business-Cold Water_Booster_Pumps | $2,960/HP
Industrial Machine | ALL ELECTRIC INJECTION MOULDING MACHINE | Replacement of an existing hydraulic injection moulding machine with all electric injection moulding machine | Fully Hydraulic Injection Moulding Machine | 8000 | ΔkW=Clamping Tons*0.055 kW/Clamping Ton | ΔkWh=Clamping Tons*441 kWh/Clamping Ton | ΔkW=kWh *SPDF | 20 | PSP-Industrial-Miscellaneous_Industrial-Other | $297.7/Clamping Ton
Industrial Machine | HYBRID INJECTION MOULDING MACHINE | Replacement of an existing hydraulic injection moulding machine with a hybrid injection moulding machine | Fully Hydraulic Injection Moulding Machine | 8000 | ΔkW=Clamping Tons*0.046 kW/Clamping Ton | ΔkWh=Clamping Tons*198 kWh/Clamping Ton | ΔkW=kWh *SPDF | 20 | PSP-Industrial-Miscellaneous_Industrial-Other | $127.60/Clamping Ton
Lighting - Food Retail | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 6074 | - | 2976.26 kWh/ kW Contolled | 0.0001376 kW/kWh | 15 | PSP-Business-Food_Retail-Lighting_Interior_General | $1.08/Watt
Lighting - Hospital | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 6016 | - | 2947.84 kWh/ kW Contolled | 0.0001134 kW/kWh | 15 | PSP-Business-Hospital-Lighting_Interior_General | $1.08/Watt
Lighting - Large Hotel (Corridor/Lobby) | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 7884 | - | 3863.16 kWh/ kW Contolled | 0.0001309 kW/kWh | 15 | PSP-Business-Large_Hotel-Lighting_Interior_General | $1.08/Watt
Lighting - Large Non-Food Retail | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 4089 | - | 1799.16 kWh/ kW Contolled | 0.0001483 kW/kWh | 15 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | $1.08/Watt
Lighting - Large Office | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 3610 | - | 2310.40 kWh/ kW Contolled | 0.0001268 kW/kWh | 15 | PSP-Business-Large_Office-Lighting_Interior_General | $1.08/Watt
Lighting - Nursing Home | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 6849 | - | 3356.01 kWh/ kW Contolled | 0.0001382 kW/kWh | 15 | PSP-Business-Nursing_Home-Lighting_Interior_General | $1.08/Watt
Lighting - Other Commercial Buildings | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 4000 | - | 1960.00 kWh/ kW Contolled | 0.0000915 kW/kWh | 15 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | $1.08/Watt
Lighting - Other Non-Food Retail | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 3700 | - | 1628.00 kWh/ kW Contolled | 0.0001443 kW/kWh | 15 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | $1.08/Watt
Lighting - Restaurant | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 5110 | - | 3014.90 kWh/ kW Contolled | 0.0001576 kW/kWh | 15 | PSP-Business-Restaurant-Lighting_Interior_General | $1.08/Watt
Lighting - Schools | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 2596 | - | 1064.36 kWh/ kW Contolled | 0.0000395 kW/kWh | 15 | PSP-Business-Schools-Lighting_Interior_General | $1.08/Watt
Lighting - University Colleges | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 3255 | - | 911.40 kWh/ kW Contolled | 0.0001023 kW/kWh | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | $1.08/Watt
Lighting - Warehouse Wholesale | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total wattage (kW) of the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 4375 | - | 2975.00 kWh/ kW Contolled | 0.0001185 kW/kWh | 15 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | $1.08/Watt
Refrigeration | ADD DOOR TO OPEN REFRIGERATED DISPLAY CASE | Coolers | Open Multi-Deck Refrigerated Display Case | 8760 | ΔkW = FT * 302.65 / 8760 | ΔkWh = FT * 302.65 | ΔkW = ΔkWh * SPDF | 15 | PSP-Business-Commercial-Refrigerated_Display_Case_Food Retail | $ = FT * $510 per linear foot
Refrigeration | ADD DOOR TO OPEN REFRIGERATED DISPLAY CASE | Freezers | Open Multi-Deck Refrigerated Display Case | 8760 | ΔkW = FT * 1405.59 / 8760 | ΔkWh = FT * 1405.59 | ΔkW = ΔkWh * SPDF | 15 | PSP-Business-Commercial-Refrigerated_Display_Case_Food Retail | $ = FT * $510 per linear foot
Refrigeration | REFRIGERATION COMPRESSORS | High-Efficiency Discus Compressors | Non-High-Efficiency Discus or Scroll Compressor in a Refrigeration System | 5858 | ΔkW = HP * 590 / 5858 | ΔkWh = HP * 590 | ΔkW = ΔkWh * SPDF | 15 | PSP-Business-Commercial-Refrigerated_Display_Case_Food Retail | $226 per HP
Refrigeration | REFRIGERATION COMPRESSORS | High-Efficiency Scroll Compressors | Non-High-Efficiency Discus or Scroll Compressor in a Refrigeration System | 5858 | ΔkW = HP * 334.33 / 5858 | ΔkWh = HP * 334.33 | ΔkW = ΔkWh * SPDF | 15 | PSP-Business-Commercial-Refrigerated_Display_Case_Food Retail | $235 per HP
Industrial Machine | Energy Management Information System (>400,000 GJ) | Implementation or Augmentation of an Energy Management Information System | No Energy Management Information System | 5702 | ΔkW = ΔkWH / 5702 | ΔkWh = Annual Energy Consumption (GJ) * 277.778 (kWh/GJ) * 0.06 * 0.3 | ΔkW = ΔkWh * SPDF | 15 | PSP-Industrial-Miscellaneous_Industrial-Other | -
Distributed Energy Resources – Solar PV | SOLAR PHOTOVOLTAIC SYSTEM Small to Medium Generation >10 kW and <= 1 MW | Enter the total maximum power in kW-AC capacity of the Solar Photovoltaic System being installed. | Electricity supply by grid | - | ΔkW = SystemkW x kWdeemed | ΔkWh = SystemkW x kWhdeemed | ΔkW = ΔkWh * SPDF | 20 | Custom Load Profile | -
Distributed Energy Resources – Solar PV | SOLAR PHOTOVOLTAIC SYSTEM Micro Generation <= 10 kW | Enter the total maximum power in kW-AC capacity of the Solar Photovoltaic System being installed. | Electricity supply by grid | - | ΔkW = SystemkW x kWdeemed | ΔkWh = SystemkW x kWhdeemed | ΔkW = ΔkWh * SPDF | 20 | Custom Load Profile | -
Lighting - Greenhouses | LED GROW LIGHTS - VEGETABLE GREENHOUSES | LED top lighting fixture installed in a vegetables/fruits/flowers greenhouse. | High Pressure Sodium with 1.7 micromol/J Photosynthetic Photon Flux Efficacy | - | - | ((PPFee / (PPEbl * 1000)) - kWee) * Hours * WHFe | ΔkWpeak = ΔkWh * SPDF | 9.5 | CUSTOM-Business-Other_Commercial_Buildings-CUSTOM-Industrial-Agriculture-Horticultural Lighting - Veg | LED fixture cost is: ≤ 250 Watts = $ 456 per fixture > 250 Watts = $ 749 per fixture
Lighting - Greenhouses | GREENHOUSE ADVANCED LIGHTING CONTROL | Enter the total wattage (kW) of the lighting fixtures which are being controlled by the Greenhouse Advanced Lighting Control System. | No existing controls or basic lighting control systems | - | - | (kWh/yr) = kWcontrolled x SF x HOU | - | 16 | CUSTOM-Business-Other_Commercial_Buildings-CUSTOM-Industrial-Agriculture-Horticultural Lighting - Veg | $2780/kW
Lighting - Industrial | NETWORKED LIGHTING CONTROLS - RETROFIT | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 4473 |  | 3041.64 kWh/ kW Contolled | 0.0001080 kW/kWh | 15 | PSP-Business-Lighting_Industrial_General | $1.08/Watt
Lighting - Food Retail | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 6074 |  | 2351.25 kWh/ 1000 Sq-Ft | 0.0001376 kW/kWh | 15 | PSP-Business-Food_Retail-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Hospital | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 6016 |  | 3095.23 kWh/ 1000 Sq-Ft | 0.0001134 kW/kWh | 15 | PSP-Business-Hospital-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Large Hotel (Corridor/Lobby) | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 7884 |  | 2897.37 kWh/ 1000 Sq-Ft | 0.0001309 kW/kWh | 15 | PSP-Business-Large_Hotel-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Large Non-Food Retail | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 4089 |  | 1907.11 kWh/ 1000 Sq-Ft | 0.0001483 kW/kWh | 15 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Large Office | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 3610 |  | 1825.22 kWh/ 1000 Sq-Ft | 0.0001268 kW/kWh | 15 | PSP-Business-Large_Office-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Nursing Home | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 6849 |  | 2047.17 KWh/ 1000 Sq-Ft | 0.0001382 kW/kWh | 15 | PSP-Business-Nursing_Home-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Other Commercial Buildings | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 4000 |  | 1470 kWh/1000 Sq-Ft | 0.0000915 kW/kWh | 15 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Other Non-Food Retail | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 3700 |  | 1725.68 kWh/ 1000 Sq-Ft | 0.0001443 kW/kWh | 15 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Restaurant | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 5110 |  | 2532.52 kWh/ 1000 Sq-Ft | 0.0001576 kW/kWh | 15 | PSP-Business-Restaurant-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Schools | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 2596 |  | 872.78 kWh/ 1000 Sq-Ft | 0.0000395 kW/kWh | 15 | PSP-Business-Schools-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - University Colleges | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 3255 |  | 1080.99 kWh/ 1000 Sq-Ft | 0.0001023 kW/kWh | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Warehouse Wholesale | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 4375 |  | 1428 kWh/ 1000 Sq-Ft | 0.0001185 kW/kWh | 15 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Lighting - Industrial | NETWORKED LIGHTING CONTROLS - NEW INSTALLATION | Enter the total area (sqft) covered by the luminaires being controlled by the Networked Lighting Control system | No existing controls or basic lighting control systems | 4473 |  | 2737.48 kWh/ 1000 Sq-Ft | 0.0001080 kW/kWh | 15 | PSP-Business-Lighting_Industrial_General | Interior Networked Lighting Controls <10,000 sqft building 1.24 per sq-ft Interior Networked Lighting Controls 10,000-100,000 sqft building 0.85 per sq-ft Interior Networked Lighting Controls >100,000 sqft building 0.58 per sq-ft
Demand Control Ventilation | DEMAND CONTROL VENTILATION - INTERIOR CONDITIONED SPACES |  |  |  |  | 112.125 kWh/ton | 0.000054 kW/ton | 10 | PSP-Business-Other_Commercial_Buildings-CE_Space_Heating | $45/ton

## Business - SBP
END_USE | CONSERVATION_MEASURE_NAME | DESCRIPTION | BASE_MEASURE | ASSUMED_ANNUAL_OPERATING_HOURS | BASE_CASE_KW | BASE_CASE_KWH | CONSERVATION_CASE_KW | CONSERVATION_CASE_KWH | FIRST_YEAR_DEMAND_SAVINGS | FIRST_YEAR_ENERGY_SAVINGS | PEAK_DEMAND_SAVINGS | EFFECTIVE_USEFUL_LIFE | END_USE_LOAD_PROFILE | INCREMENTAL_LIFE_CYCLE_COST
Refrigeration | AUTOMATIC DOOR CLOSER (for Walk-in Coolers) | AUTOMATIC DOOR CLOSER (for Walk-in Coolers) | NO AUTOMATIC DOOR CLOSER | - | - | - | - | - | 0.312 | 1566 | 0.183 | 8 | PSP-Business-Commercial-Refrigeration | 250
Refrigeration | AUTOMATIC DOOR CLOSER (for Walk-in Freezers) | AUTOMATIC DOOR CLOSER (for Walk-in Freezers) | NO AUTOMATIC DOOR CLOSER | - | - | - | - | - | 0.371 | 3031 | 0.354 | 8 | PSP-Business-Commercial-Refrigeration | 250
Refrigeration | CONDENSER COIL CLEANING (for Coolers) | CONDENSER COIL CLEANING (for Coolers) | Dirty Condenser Coils | - | - | - | - | - | - | 289 | 0.033779 | 1 | PSP-Business-Commercial-Refrigeration | 20
Refrigeration | CONDENSER COIL CLEANING (for Freezers) | CONDENSER COIL CLEANING (for Freezers) | Dirty Condenser Coils | - | - | - | - | - | - | 243 | 0.028403 | 1 | PSP-Business-Commercial-Refrigeration | 20
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Coolers) | 1/15 HP (50W) ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.17144 | 856.0417 | 0.059211 | 295.65 | 0.11223 | 560.3917 | 0.065 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Coolers) | 1/20 HP (37W) ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.12687 | 633.4709 | 0.043816 | 218.781 | 0.083051 | 414.6899 | 0.049 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Coolers) | 1/25 HP (30W) ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.10286 | 513.625 | 0.035526 | 177.39 | 0.067339 | 336.235 | 0.039 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Coolers) | 1/5 HP (150W) ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.51432 | 2568.1252 | 0.17763 | 886.95 | 0.33669 | 1681.1752 | 0.196 | 15 | PSP-Business-Commercial-Refrigeration | 418
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Coolers) | 12 Watt ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.046698 | 233.1711 | 0.014595 | 72.8737 | 0.032103 | 160.2974 | 0.019 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Coolers) | 16 Watt ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.062264 | 310.8948 | 0.019459 | 97.165 | 0.042804 | 213.7298 | 0.025 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Coolers) | 9 Watt ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.045054 | 224.9645 | 0.01125 | 56.1735 | 0.033804 | 168.791 | 0.02 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Freezers) | 1/15 HP (50W) ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.17144 | 856.0417 | 0.059211 | 295.65 | 0.11223 | 560.3917 | 0.065 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Freezers) | 1/20 HP (37W) ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.12687 | 633.4709 | 0.043816 | 218.781 | 0.083051 | 414.6899 | 0.049 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Freezers) | 1/25 HP (30W) ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.10286 | 513.625 | 0.035526 | 177.39 | 0.067339 | 336.235 | 0.039 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Freezers) | 1/5 HP (150W) ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.51432 | 2568.1252 | 0.17763 | 886.95 | 0.33669 | 1681.1752 | 0.196 | 15 | PSP-Business-Commercial-Refrigeration | 418
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Freezers) | 12 Watt ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.046698 | 233.1711 | 0.014595 | 72.8737 | 0.032103 | 160.2974 | 0.019 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Freezers) | 16 Watt ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.062264 | 310.8948 | 0.019459 | 97.165 | 0.042804 | 213.7298 | 0.025 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR CONDENSER FANS (for Freezers) | 9 Watt ECM Condenser Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.045054 | 224.9645 | 0.01125 | 56.1735 | 0.033804 | 168.791 | 0.02 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Coolers) | 1/15 HP (50W) ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.17144 | 2014.4879 | 0.059211 | 691.3626 | 0.11223 | 1323.1253 | 0.155 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Coolers) | 1/20 HP (37W) ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.12687 | 1490.7211 | 0.043816 | 511.6083 | 0.083051 | 979.1127 | 0.114 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Coolers) | 1/25 HP (30W) ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.10286 | 1208.6927 | 0.035526 | 414.8176 | 0.067339 | 793.8752 | 0.093 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Coolers) | 1/5 HP (150W) ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.51432 | 6043.4637 | 0.17763 | 2074.0878 | 0.33669 | 3969.376 | 0.464 | 15 | PSP-Business-Commercial-Refrigeration | 418
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Coolers) | 12 Watt ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.046698 | 548.8038 | 0.014595 | 170.4115 | 0.032103 | 378.3923 | 0.044 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Coolers) | 16 Watt ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.062264 | 731.7384 | 0.019459 | 227.2154 | 0.042804 | 504.523 | 0.059 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Coolers) | 9 Watt ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.045054 | 529.9089 | 0.01125 | 131.3589 | 0.033804 | 398.55 | 0.047 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Freezers) | 1/15 HP (50W) ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.17144 | 2560.1884 | 0.059211 | 875.452 | 0.11223 | 1684.7364 | 0.197 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Freezers) | 1/20 HP (37W) ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.12687 | 1894.5394 | 0.043816 | 647.8345 | 0.083051 | 1246.7049 | 0.146 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Freezers) | 1/25 HP (30W) ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.10286 | 1536.113 | 0.035526 | 525.2712 | 0.067339 | 1010.8418 | 0.118 | 15 | PSP-Business-Commercial-Refrigeration | 310
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Freezers) | 1/5 HP (150W) ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.51432 | 7680.5652 | 0.17763 | 2626.356 | 0.33669 | 5054.2092 | 0.591 | 15 | PSP-Business-Commercial-Refrigeration | 418
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Freezers) | 12 Watt ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.046698 | 697.5351 | 0.014595 | 215.7871 | 0.032103 | 481.748 | 0.056 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Freezers) | 16 Watt ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.062264 | 930.0468 | 0.019459 | 287.7161 | 0.042804 | 642.3307 | 0.075 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | ECM MOTORS FOR EVAPORATOR FANS (for Freezers) | 9 Watt ECM Evaporator Fan Motor Replacement | Shaded Pole Motor (SP) and/or Permanent Split Capacitor (PSC) | - | 0.045054 | 673.8261 | 0.01125 | 166.3359 | 0.033804 | 507.4902 | 0.059 | 15 | PSP-Business-Commercial-Refrigeration | 137
Refrigeration | Night Cover (for reach-in Coolers) | 4' Night Cover | NO NIGHT COVER | - | - | - | - | - | - | 1518 | 0 | 5 | PSP-Business-Commercial-Refrigeration | 280
Refrigeration | Night Cover (for reach-in Coolers) | 6' Night Cover | NO NIGHT COVER | - | - | - | - | - | - | 2174 | 0 | 5 | PSP-Business-Commercial-Refrigeration | 360
Refrigeration | STRIP CURTAINS (for Walk-in Coolers) | STRIP CURTAINS (for Walk-in Coolers) | NO STRIP CURTAINS | - | - | - | - | - | - | 768 | 0.09 | 4 | PSP-Business-Commercial-Refrigeration | 230
Refrigeration | STRIP CURTAINS (for Walk-in Freezers) | STRIP CURTAINS (for Walk-in Freezers) | NO STRIP CURTAINS | - | - | - | - | - | - | 2983 | 0.349 | 4 | PSP-Business-Commercial-Refrigeration | 230
HVAC | Smart Thermostat | Web Enabled Smart Thermostat | Non-programable thermostat | - | - | - | - | - | 0.792 | 877 | 0.239 | 11 | PSP-Business-Commercial-Cooling_DX | 250

## Business - IDP
Framework | END_USE | CONSERVATION_MEASURE_NAME | DESCRIPTION | BASE_MEASURE | ASSUMED_ANNUAL_OPERATING_HOURS | BASE_CASE_KW | BASE_CASE_KWH | CONSERVATION_CASE_KW | CONSERVATION_CASE_KWH | FIRST_YEAR_DEMAND_SAVINGS | FIRST_YEAR_ENERGY_SAVINGS | PEAK_DEMAND_SAVINGS | EFFECTIVE_USEFUL_LIFE | END_USE_LOAD_PROFILE | INCREMENTAL_LIFE_CYCLE_COST
eDSM | Lighting - Food Retail | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 6074 | 0.03182 | 193.2913 | 0.019 | 115.406 | 0.01282 | 77.8853 | 0.010721 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 5.16
eDSM | Lighting - Hospital | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 5182 | 0.03182 | 164.9054 | 0.019 | 98.458 | 0.01282 | 66.4474 | 0.0075372 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 5.16
eDSM | Lighting - Large Hotel (Corridor/Lobby) | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 7884 | 0.03182 | 250.8905 | 0.019 | 149.796 | 0.01282 | 101.0945 | 0.013228 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 5.16
eDSM | Lighting - Large Non-Food Retail | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 3121 | 0.03182 | 99.3102 | 0.019 | 59.299 | 0.01282 | 40.0112 | 0.0059337 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 5.16
eDSM | Lighting - Large Office | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 3610 | 0.03182 | 114.8801 | 0.019 | 68.59 | 0.01282 | 46.2901 | 0.0058704 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 5.16
eDSM | Lighting - Nursing Home | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 4308 | 0.03182 | 137.0924 | 0.019 | 81.852 | 0.01282 | 55.2404 | 0.0076337 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 5.16
eDSM | Lighting - Other Commercial Buildings | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 4000 | 0.03182 | 127.291 | 0.019 | 76 | 0.01282 | 51.291 | 0.0046955 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 5.16
eDSM | Lighting - Other Non-Food Retail | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 4089 | 0.03182 | 130.1232 | 0.019 | 77.691 | 0.01282 | 52.4322 | 0.0075655 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 5.16
eDSM | Lighting - Restaurant | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 5110 | 0.03182 | 162.6142 | 0.019 | 97.09 | 0.01282 | 65.5242 | 0.010327 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 5.16
eDSM | Lighting - Schools | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 2596 | 0.03182 | 82.6118 | 0.019 | 49.324 | 0.01282 | 33.2878 | 0.0013139 | 19 | PSP-Business-Schools-Lighting_Interior_General | 5.16
eDSM | Lighting - University Colleges | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 3255 | 0.03182 | 103.583 | 0.019 | 61.845 | 0.01282 | 41.738 | 0.0042716 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 5.16
eDSM | Lighting - Warehouse Wholesale | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 4408 | 0.03182 | 140.2626 | 0.019 | 83.752 | 0.01282 | 56.5106 | 0.0066968 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 5.16
eDSM | Lighting - Food Retail | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 6074 | 0.05996 | 364.2131 | 0.028 | 170.072 | 0.03196 | 194.1411 | 0.026722 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 0.71
eDSM | Lighting - Hospital | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 5182 | 0.05996 | 310.7264 | 0.028 | 145.096 | 0.03196 | 165.6304 | 0.018788 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 0.71
eDSM | Lighting - Large Hotel (Corridor/Lobby) | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 7884 | 0.05996 | 472.7455 | 0.028 | 220.752 | 0.03196 | 251.9935 | 0.032974 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 0.71
eDSM | Lighting - Large Non-Food Retail | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 3121 | 0.05996 | 187.1352 | 0.028 | 87.388 | 0.03196 | 99.7472 | 0.014793 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 0.71
eDSM | Lighting - Large Office | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 3610 | 0.05996 | 216.4651 | 0.028 | 101.08 | 0.03196 | 115.3851 | 0.014633 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 0.71
eDSM | Lighting - Nursing Home | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 4308 | 0.05996 | 258.3191 | 0.028 | 120.624 | 0.03196 | 137.6951 | 0.019028 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 0.71
eDSM | Lighting - Other Commercial Buildings | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 4000 | 0.05996 | 239.8506 | 0.028 | 112 | 0.03196 | 127.8506 | 0.011704 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 0.71
eDSM | Lighting - Other Non-Food Retail | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 4089 | 0.05996 | 245.1873 | 0.028 | 114.492 | 0.03196 | 130.6952 | 0.018858 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 0.71
eDSM | Lighting - Restaurant | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 5110 | 0.05996 | 306.4091 | 0.028 | 143.08 | 0.03196 | 163.3291 | 0.025742 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 0.71
eDSM | Lighting - Schools | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 2596 | 0.05996 | 155.663 | 0.028 | 72.688 | 0.03196 | 82.975 | 0.0032751 | 19 | PSP-Business-Schools-Lighting_Interior_General | 0.71
eDSM | Lighting - University Colleges | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 3255 | 0.05996 | 195.1784 | 0.028 | 91.14 | 0.03196 | 104.0384 | 0.010648 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 0.71
eDSM | Lighting - Warehouse Wholesale | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 4408 | 0.05996 | 264.3037 | 0.028 | 123.424 | 0.03196 | 140.8797 | 0.016695 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 0.71
eDSM | Lighting - Food Retail | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 6074 | 0.03139 | 190.6848 | 0.018 | 109.332 | 0.01339 | 81.3528 | 0.011198 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 3.08
eDSM | Lighting - Food Retail | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 6074 | 0.02475 | 150.3275 | 0.013 | 78.962 | 0.01175 | 71.3655 | 0.0098231 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | -2.06
eDSM | Lighting - Hospital | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 5182 | 0.03139 | 162.6817 | 0.018 | 93.276 | 0.01339 | 69.4057 | 0.0078727 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 3.08
eDSM | Lighting - Hospital | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 5182 | 0.02475 | 128.2511 | 0.013 | 67.366 | 0.01175 | 60.8851 | 0.0069062 | 10 | PSP-Business-Hospital-Lighting_Interior_General | -2.06
eDSM | Lighting - Large Hotel (Corridor/Lobby) | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 7884 | 0.03139 | 247.5073 | 0.018 | 141.912 | 0.01339 | 105.5953 | 0.013817 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 3.08
eDSM | Lighting - Large Hotel (Corridor/Lobby) | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 7884 | 0.02475 | 195.1239 | 0.013 | 102.492 | 0.01175 | 92.6319 | 0.012121 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | -2.06
eDSM | Lighting - Large Non-Food Retail | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 3121 | 0.03139 | 97.9682 | 0.018 | 56.178 | 0.01339 | 41.7902 | 0.0061975 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 3.08
eDSM | Lighting - Large Non-Food Retail | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 3121 | 0.02475 | 77.2448 | 0.013 | 40.573 | 0.01175 | 36.6718 | 0.0054385 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -2.06
eDSM | Lighting - Large Office | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 3610 | 0.03139 | 113.331 | 0.018 | 64.98 | 0.01339 | 48.351 | 0.0061318 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 3.08
eDSM | Lighting - Large Office | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 3610 | 0.02475 | 89.3451 | 0.013 | 46.93 | 0.01175 | 42.4151 | 0.005379 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | -2.06
eDSM | Lighting - Nursing Home | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 4308 | 0.03139 | 135.2437 | 0.018 | 77.544 | 0.01339 | 57.6997 | 0.0079735 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 3.08
eDSM | Lighting - Nursing Home | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 4308 | 0.02475 | 106.6202 | 0.013 | 56.004 | 0.01175 | 50.6162 | 0.0069946 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | -2.06
eDSM | Lighting - Other Commercial Buildings | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 4000 | 0.03139 | 125.5745 | 0.018 | 72 | 0.01339 | 53.5745 | 0.0049046 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 3.08
eDSM | Lighting - Other Commercial Buildings | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 4000 | 0.02475 | 98.9974 | 0.013 | 52 | 0.01175 | 46.9974 | 0.0043024 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -2.06
eDSM | Lighting - Other Non-Food Retail | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 4089 | 0.03139 | 128.3685 | 0.018 | 73.602 | 0.01339 | 54.7665 | 0.0079023 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 3.08
eDSM | Lighting - Other Non-Food Retail | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 4089 | 0.02475 | 101.2001 | 0.013 | 53.157 | 0.01175 | 48.0431 | 0.0069322 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -2.06
eDSM | Lighting - Restaurant | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 5110 | 0.03139 | 160.4214 | 0.018 | 91.98 | 0.01339 | 68.4414 | 0.010787 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 3.08
eDSM | Lighting - Restaurant | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 5110 | 0.02475 | 126.4692 | 0.013 | 66.43 | 0.01175 | 60.0392 | 0.0094627 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | -2.06
eDSM | Lighting - Schools | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 2596 | 0.03139 | 81.4978 | 0.018 | 46.728 | 0.01339 | 34.7698 | 0.0013724 | 19 | PSP-Business-Schools-Lighting_Interior_General | 3.08
eDSM | Lighting - Schools | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 2596 | 0.02475 | 64.2493 | 0.013 | 33.748 | 0.01175 | 30.5013 | 0.0012039 | 19 | PSP-Business-Schools-Lighting_Interior_General | -2.06
eDSM | Lighting - University Colleges | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 3255 | 0.03139 | 102.1862 | 0.018 | 58.59 | 0.01339 | 43.5962 | 0.0044618 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 3.08
eDSM | Lighting - University Colleges | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 3255 | 0.02475 | 80.5591 | 0.013 | 42.315 | 0.01175 | 38.2441 | 0.0039141 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | -2.06
eDSM | Lighting - Warehouse Wholesale | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 4408 | 0.03139 | 138.3671 | 0.018 | 79.344 | 0.01339 | 59.0231 | 0.0069946 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 3.08
eDSM | Lighting - Warehouse Wholesale | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 4408 | 0.02475 | 109.098 | 0.013 | 57.304 | 0.01175 | 51.794 | 0.0061379 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -2.06
eDSM | Lighting - Food Retail | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 6074 | 0.07013 | 425.9447 | 0.044 | 267.256 | 0.02613 | 158.6888 | 0.021843 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 145
eDSM | Lighting - Food Retail | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 6074 | 0.11712 | 711.4165 | 0.093 | 564.882 | 0.02412 | 146.5345 | 0.02017 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 167
eDSM | Lighting - Hospital | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 5182 | 0.07013 | 363.3924 | 0.044 | 228.008 | 0.02613 | 135.3844 | 0.015357 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 145
eDSM | Lighting - Hospital | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 5182 | 0.11712 | 606.9411 | 0.093 | 481.926 | 0.02412 | 125.0151 | 0.014181 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 167
eDSM | Lighting - Large Hotel (Corridor/Lobby) | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 7884 | 0.07013 | 552.8726 | 0.044 | 346.896 | 0.02613 | 205.9766 | 0.026952 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 145
eDSM | Lighting - Large Hotel (Corridor/Lobby) | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 7884 | 0.11712 | 923.4126 | 0.093 | 733.212 | 0.02412 | 190.2006 | 0.024888 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 167
eDSM | Lighting - Large Non-Food Retail | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 3121 | 0.07013 | 218.8757 | 0.044 | 137.324 | 0.02613 | 81.5517 | 0.012094 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 145
eDSM | Lighting - Large Non-Food Retail | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 3121 | 0.11712 | 365.5315 | 0.093 | 290.253 | 0.02412 | 75.2785 | 0.011164 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 167
eDSM | Lighting - Large Office | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 3610 | 0.07013 | 253.1545 | 0.044 | 158.84 | 0.02613 | 94.3145 | 0.011961 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 145
eDSM | Lighting - Large Office | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 3610 | 0.11712 | 422.8208 | 0.093 | 335.73 | 0.02412 | 87.0908 | 0.011045 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 167
eDSM | Lighting - Nursing Home | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4308 | 0.07013 | 302.1024 | 0.044 | 189.552 | 0.02613 | 112.5504 | 0.015553 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 145
eDSM | Lighting - Nursing Home | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4308 | 0.11712 | 504.574 | 0.093 | 400.644 | 0.02412 | 103.93 | 0.014362 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 167
eDSM | Lighting - Other Commercial Buildings | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4000 | 0.07013 | 280.5036 | 0.044 | 176 | 0.02613 | 104.5036 | 0.0095669 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 145
eDSM | Lighting - Other Commercial Buildings | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4000 | 0.11712 | 468.4995 | 0.093 | 372 | 0.02412 | 96.4995 | 0.0088342 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 167
eDSM | Lighting - Other Non-Food Retail | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4089 | 0.07013 | 286.7448 | 0.044 | 179.916 | 0.02613 | 106.8288 | 0.015414 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 145
eDSM | Lighting - Other Non-Food Retail | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4089 | 0.11712 | 478.9237 | 0.093 | 380.277 | 0.02412 | 98.6467 | 0.014234 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 167
eDSM | Lighting - Restaurant | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 5110 | 0.07013 | 358.3434 | 0.044 | 224.84 | 0.02613 | 133.5034 | 0.021041 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 145
eDSM | Lighting - Restaurant | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 5110 | 0.11712 | 598.5082 | 0.093 | 475.23 | 0.02412 | 123.2781 | 0.01943 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 167
eDSM | Lighting - Schools | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 2596 | 0.07013 | 182.0469 | 0.044 | 114.224 | 0.02613 | 67.8229 | 0.0026771 | 19 | PSP-Business-Schools-Lighting_Interior_General | 145
eDSM | Lighting - Schools | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 2596 | 0.11712 | 304.0562 | 0.093 | 241.428 | 0.02412 | 62.6282 | 0.002472 | 19 | PSP-Business-Schools-Lighting_Interior_General | 167
eDSM | Lighting - University Colleges | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 3255 | 0.07013 | 228.2598 | 0.044 | 143.22 | 0.02613 | 85.0398 | 0.0087033 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 145
eDSM | Lighting - University Colleges | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 3255 | 0.11712 | 381.2415 | 0.093 | 302.715 | 0.02412 | 78.5265 | 0.0080367 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 167
eDSM | Lighting - Warehouse Wholesale | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4408 | 0.07013 | 309.133 | 0.044 | 193.952 | 0.02613 | 115.181 | 0.01365 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 145
eDSM | Lighting - Warehouse Wholesale | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4408 | 0.11712 | 516.265 | 0.093 | 409.944 | 0.02412 | 106.321 | 0.0126 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 167
eDSM | Lighting - Food Retail | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 6074 | 0.071 | 431.254 | 0.045 | 273.33 | 0.026 | 157.924 | 0.021737 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 56.48
eDSM | Lighting - Food Retail | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 6074 | 0.122 | 741.028 | 0.084 | 510.216 | 0.038 | 230.812 | 0.03177 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 20.04
eDSM | Lighting - Hospital | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 5182 | 0.071 | 367.922 | 0.045 | 233.19 | 0.026 | 134.732 | 0.015283 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 56.48
eDSM | Lighting - Hospital | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 5182 | 0.122 | 632.204 | 0.084 | 435.288 | 0.038 | 196.916 | 0.022336 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 20.04
eDSM | Lighting - Large Hotel (Corridor/Lobby) | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 7884 | 0.071 | 559.764 | 0.045 | 354.78 | 0.026 | 204.984 | 0.026822 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 56.48
eDSM | Lighting - Large Hotel (Corridor/Lobby) | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 7884 | 0.122 | 961.848 | 0.084 | 662.256 | 0.038 | 299.592 | 0.039202 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 20.04
eDSM | Lighting - Large Non-Food Retail | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 3121 | 0.071 | 221.591 | 0.045 | 140.445 | 0.026 | 81.146 | 0.012034 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 56.48
eDSM | Lighting - Large Non-Food Retail | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 3121 | 0.122 | 380.762 | 0.084 | 262.164 | 0.038 | 118.598 | 0.017588 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 20.04
eDSM | Lighting - Large Office | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 3610 | 0.071 | 256.31 | 0.045 | 162.45 | 0.026 | 93.86 | 0.011903 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 56.48
eDSM | Lighting - Large Office | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 3610 | 0.122 | 440.42 | 0.084 | 303.24 | 0.038 | 137.18 | 0.017397 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 20.04
eDSM | Lighting - Nursing Home | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 4308 | 0.071 | 305.868 | 0.045 | 193.86 | 0.026 | 112.008 | 0.015478 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 56.48
eDSM | Lighting - Nursing Home | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 4308 | 0.122 | 525.576 | 0.084 | 361.872 | 0.038 | 163.704 | 0.022622 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 20.04
eDSM | Lighting - Other Commercial Buildings | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamps 8’ T12 and T8 | 4000 | 0.071 | 284 | 0.045 | 180 | 0.026 | 104 | 0.0095208 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 56.48
eDSM | Lighting - Other Commercial Buildings | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 4000 | 0.122 | 488 | 0.084 | 336 | 0.038 | 152 | 0.013915 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 20.04
eDSM | Lighting - Other Non-Food Retail | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 4089 | 0.071 | 290.319 | 0.045 | 184.005 | 0.026 | 106.314 | 0.01534 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 56.48
eDSM | Lighting - Other Non-Food Retail | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 4089 | 0.122 | 498.858 | 0.084 | 343.476 | 0.038 | 155.382 | 0.02242 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 20.04
eDSM | Lighting - Restaurant | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 5110 | 0.071 | 362.81 | 0.045 | 229.95 | 0.026 | 132.86 | 0.02094 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 56.48
eDSM | Lighting - Restaurant | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 5110 | 0.122 | 623.42 | 0.084 | 429.24 | 0.038 | 194.18 | 0.030604 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 20.04
eDSM | Lighting - Schools | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 2596 | 0.071 | 184.316 | 0.045 | 116.82 | 0.026 | 67.496 | 0.0026642 | 19 | PSP-Business-Schools-Lighting_Interior_General | 56.48
eDSM | Lighting - Schools | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 2596 | 0.122 | 316.712 | 0.084 | 218.064 | 0.038 | 98.648 | 0.0038938 | 19 | PSP-Business-Schools-Lighting_Interior_General | 20.04
eDSM | Lighting - University Colleges | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 3255 | 0.071 | 231.105 | 0.045 | 146.475 | 0.026 | 84.63 | 0.0086614 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 56.48
eDSM | Lighting - University Colleges | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 3255 | 0.122 | 397.11 | 0.084 | 273.42 | 0.038 | 123.69 | 0.012659 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 20.04
eDSM | Lighting - Warehouse Wholesale | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamp 8’ T12 and T8 | 4408 | 0.071 | 312.968 | 0.045 | 198.36 | 0.026 | 114.608 | 0.013582 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 56.48
eDSM | Lighting - Warehouse Wholesale | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 4408 | 0.122 | 537.776 | 0.084 | 370.272 | 0.038 | 167.504 | 0.01985 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 20.04
eDSM | Lighting - Food Retail | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 6074 | 0.06915 | 420.0248 | 0.0377 | 228.9898 | 0.03145 | 191.035 | 0.026295 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | -4.18
eDSM | Lighting - Hospital | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 5182 | 0.06915 | 358.3419 | 0.0377 | 195.3614 | 0.03145 | 162.9805 | 0.018487 | 10 | PSP-Business-Hospital-Lighting_Interior_General | -4.18
eDSM | Lighting - Large Hotel (Corridor/Lobby) | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 7884 | 0.06915 | 545.1886 | 0.0377 | 297.2268 | 0.03145 | 247.9618 | 0.032446 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | -4.18
eDSM | Lighting - Large Non-Food Retail | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 3121 | 0.06915 | 215.8171 | 0.0377 | 117.6617 | 0.03145 | 98.1555 | 0.014557 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -4.18
eDSM | Lighting - Large Office | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 3610 | 0.06915 | 249.6361 | 0.0377 | 136.097 | 0.03145 | 113.5391 | 0.014399 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | -4.18
eDSM | Lighting - Nursing Home | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 4308 | 0.06915 | 297.9037 | 0.0377 | 162.4116 | 0.03145 | 135.4921 | 0.018724 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | -4.18
eDSM | Lighting - Other Commercial Buildings | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 4000 | 0.06915 | 276.6051 | 0.0377 | 150.8 | 0.03145 | 125.8051 | 0.011517 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -4.18
eDSM | Lighting - Other Non-Food Retail | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 4089 | 0.06915 | 282.7595 | 0.0377 | 154.1553 | 0.03145 | 128.6042 | 0.018556 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -4.18
eDSM | Lighting - Restaurant | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 5110 | 0.06915 | 353.363 | 0.0377 | 192.647 | 0.03145 | 160.716 | 0.02533 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | -4.18
eDSM | Lighting - Schools | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 2596 | 0.06915 | 179.5167 | 0.0377 | 97.8692 | 0.03145 | 81.6475 | 0.0032227 | 19 | PSP-Business-Schools-Lighting_Interior_General | -4.18
eDSM | Lighting - University Colleges | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 3255 | 0.06915 | 225.0874 | 0.0377 | 122.7135 | 0.03145 | 102.3739 | 0.010477 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | -4.18
eDSM | Lighting - Warehouse Wholesale | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 4408 | 0.06915 | 304.8132 | 0.0377 | 166.1816 | 0.03145 | 138.6316 | 0.016429 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -4.18
eDSM | Lighting - Food Retail | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 6074 | 0.06438 | 391.0719 | 0.0386 | 234.4564 | 0.02578 | 156.6155 | 0.021557 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 114.37
eDSM | Lighting - Food Retail | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 6074 | 0.06618 | 401.9719 | 0.039 | 236.886 | 0.02718 | 165.0859 | 0.022723 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 61.99
eDSM | Lighting - Food Retail | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 6074 | 0.09193 | 558.3989 | 0.044 | 267.256 | 0.04793 | 291.1429 | 0.040074 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 116.78
eDSM | Lighting - Hospital | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 5182 | 0.06438 | 333.6409 | 0.0386 | 200.0252 | 0.02578 | 133.6156 | 0.015156 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 114.37
eDSM | Lighting - Hospital | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 5182 | 0.06618 | 342.9402 | 0.039 | 202.098 | 0.02718 | 140.8422 | 0.015976 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 61.99
eDSM | Lighting - Hospital | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 5182 | 0.09193 | 476.395 | 0.044 | 228.008 | 0.04793 | 248.387 | 0.028175 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 116.78
eDSM | Lighting - Large Hotel (Corridor/Lobby) | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 7884 | 0.06438 | 507.608 | 0.0386 | 304.3224 | 0.02578 | 203.2856 | 0.0266 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 114.37
eDSM | Lighting - Large Hotel (Corridor/Lobby) | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 7884 | 0.06618 | 521.7561 | 0.039 | 307.476 | 0.02718 | 214.2801 | 0.028039 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 61.99
eDSM | Lighting - Large Hotel (Corridor/Lobby) | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 7884 | 0.09193 | 724.797 | 0.044 | 346.896 | 0.04793 | 377.901 | 0.049449 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 116.78
eDSM | Lighting - Large Non-Food Retail | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 3121 | 0.06438 | 200.93 | 0.0386 | 120.4706 | 0.02578 | 80.4594 | 0.011932 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 114.37
eDSM | Lighting - Large Non-Food Retail | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 3121 | 0.06618 | 206.5478 | 0.039 | 121.719 | 0.02718 | 84.8288 | 0.01258 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 61.99
eDSM | Lighting - Large Non-Food Retail | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 3121 | 0.09193 | 286.9135 | 0.044 | 137.324 | 0.04793 | 149.5895 | 0.022184 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 116.78
eDSM | Lighting - Large Office | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 3610 | 0.06438 | 232.4283 | 0.0386 | 139.346 | 0.02578 | 93.0823 | 0.011805 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 114.37
eDSM | Lighting - Large Office | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 3610 | 0.06618 | 238.9066 | 0.039 | 140.79 | 0.02718 | 98.1166 | 0.012443 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 61.99
eDSM | Lighting - Large Office | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 3610 | 0.09193 | 331.8769 | 0.044 | 158.84 | 0.04793 | 173.0369 | 0.021944 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 116.78
eDSM | Lighting - Nursing Home | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4308 | 0.06438 | 277.3687 | 0.0386 | 166.2888 | 0.02578 | 111.0799 | 0.01535 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 114.37
eDSM | Lighting - Nursing Home | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4308 | 0.06618 | 285.0996 | 0.039 | 168.012 | 0.02718 | 117.0876 | 0.01618 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 61.99
eDSM | Lighting - Nursing Home | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4308 | 0.09193 | 396.0459 | 0.044 | 189.552 | 0.04793 | 206.4939 | 0.028535 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 116.78
eDSM | Lighting - Other Commercial Buildings | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4000 | 0.06438 | 257.5383 | 0.0386 | 154.4 | 0.02578 | 103.1383 | 0.0094419 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 114.37
eDSM | Lighting - Other Commercial Buildings | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4000 | 0.06618 | 264.7164 | 0.039 | 156 | 0.02718 | 108.7164 | 0.0099526 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 61.99
eDSM | Lighting - Other Commercial Buildings | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4000 | 0.09193 | 367.7306 | 0.044 | 176 | 0.04793 | 191.7306 | 0.017552 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 116.78
eDSM | Lighting - Other Non-Food Retail | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4089 | 0.06438 | 263.2685 | 0.0386 | 157.8354 | 0.02578 | 105.4331 | 0.015213 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 114.37
eDSM | Lighting - Other Non-Food Retail | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4089 | 0.06618 | 270.6064 | 0.039 | 159.471 | 0.02718 | 111.1354 | 0.016036 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 61.99
eDSM | Lighting - Other Non-Food Retail | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4089 | 0.09193 | 375.9126 | 0.044 | 179.916 | 0.04793 | 195.9966 | 0.028281 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 116.78
eDSM | Lighting - Restaurant | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 5110 | 0.06438 | 329.0052 | 0.0386 | 197.246 | 0.02578 | 131.7592 | 0.020766 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 114.37
eDSM | Lighting - Restaurant | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 5110 | 0.06618 | 338.1753 | 0.039 | 199.29 | 0.02718 | 138.8853 | 0.02189 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 61.99
eDSM | Lighting - Restaurant | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 5110 | 0.09193 | 469.7758 | 0.044 | 224.84 | 0.04793 | 244.9359 | 0.038604 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 116.78
eDSM | Lighting - Schools | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 2596 | 0.06438 | 167.1423 | 0.0386 | 100.2056 | 0.02578 | 66.9367 | 0.0026421 | 19 | PSP-Business-Schools-Lighting_Interior_General | 114.37
eDSM | Lighting - Schools | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 2596 | 0.06618 | 171.801 | 0.039 | 101.244 | 0.02718 | 70.557 | 0.002785 | 19 | PSP-Business-Schools-Lighting_Interior_General | 61.99
eDSM | Lighting - Schools | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 2596 | 0.09193 | 238.6572 | 0.044 | 114.224 | 0.04793 | 124.4332 | 0.0049116 | 19 | PSP-Business-Schools-Lighting_Interior_General | 116.78
eDSM | Lighting - University Colleges | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 3255 | 0.06438 | 209.5718 | 0.0386 | 125.643 | 0.02578 | 83.9288 | 0.0085896 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 114.37
eDSM | Lighting - University Colleges | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 3255 | 0.06618 | 215.413 | 0.039 | 126.945 | 0.02718 | 88.468 | 0.0090542 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 61.99
eDSM | Lighting - University Colleges | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 3255 | 0.09193 | 299.2408 | 0.044 | 143.22 | 0.04793 | 156.0208 | 0.015968 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 116.78
eDSM | Lighting - Warehouse Wholesale | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4408 | 0.06438 | 283.787 | 0.0386 | 170.1488 | 0.02578 | 113.6382 | 0.013467 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 114.37
eDSM | Lighting - Warehouse Wholesale | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4408 | 0.06618 | 291.7214 | 0.039 | 171.912 | 0.02718 | 119.8094 | 0.014198 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 61.99
eDSM | Lighting - Warehouse Wholesale | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4408 | 0.09193 | 405.2274 | 0.044 | 193.952 | 0.04793 | 211.2754 | 0.025037 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 116.78
eDSM | Lighting - Food Retail | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 6074 | 0.06437 | 390.9976 | 0.031 | 188.294 | 0.03337 | 202.7036 | 0.027901 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 83.95
eDSM | Lighting - Food Retail | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 6074 | 0.06617 | 401.9069 | 0.032 | 194.368 | 0.03417 | 207.5389 | 0.028567 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 38.87
eDSM | Lighting - Food Retail | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 6074 | 0.09191 | 558.2782 | 0.042 | 255.108 | 0.04991 | 303.1702 | 0.04173 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 104.06
eDSM | Lighting - Hospital | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 5182 | 0.06437 | 333.5775 | 0.031 | 160.642 | 0.03337 | 172.9355 | 0.019616 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 83.95
eDSM | Lighting - Hospital | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 5182 | 0.06617 | 342.8847 | 0.032 | 165.824 | 0.03417 | 177.0607 | 0.020084 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 38.87
eDSM | Lighting - Hospital | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 5182 | 0.09191 | 476.292 | 0.042 | 217.644 | 0.04991 | 258.648 | 0.029339 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 104.06
eDSM | Lighting - Large Hotel (Corridor/Lobby) | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 7884 | 0.06437 | 507.5116 | 0.031 | 244.404 | 0.03337 | 263.1076 | 0.034428 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 83.95
eDSM | Lighting - Large Hotel (Corridor/Lobby) | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 7884 | 0.06617 | 521.6718 | 0.032 | 252.288 | 0.03417 | 269.3838 | 0.035249 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 38.87
eDSM | Lighting - Large Hotel (Corridor/Lobby) | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 7884 | 0.09191 | 724.6404 | 0.042 | 331.128 | 0.04991 | 393.5124 | 0.051492 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 104.06
eDSM | Lighting - Large Non-Food Retail | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 3121 | 0.06437 | 200.8988 | 0.031 | 96.751 | 0.03337 | 104.1478 | 0.015445 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 83.95
eDSM | Lighting - Large Non-Food Retail | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 3121 | 0.06617 | 206.5166 | 0.032 | 99.872 | 0.03417 | 106.6446 | 0.015816 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 38.87
eDSM | Lighting - Large Non-Food Retail | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 3121 | 0.09191 | 286.8511 | 0.042 | 131.082 | 0.04991 | 155.7691 | 0.023101 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 104.06
eDSM | Lighting - Large Office | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 3610 | 0.06437 | 232.3842 | 0.031 | 111.91 | 0.03337 | 120.4742 | 0.015278 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 83.95
eDSM | Lighting - Large Office | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 3610 | 0.06617 | 238.868 | 0.032 | 115.52 | 0.03417 | 123.348 | 0.015643 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 38.87
eDSM | Lighting - Large Office | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 3610 | 0.09191 | 331.8052 | 0.042 | 151.62 | 0.04991 | 180.1852 | 0.022851 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 104.06
eDSM | Lighting - Nursing Home | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4308 | 0.06437 | 277.3161 | 0.031 | 133.548 | 0.03337 | 143.7681 | 0.019867 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 83.95
eDSM | Lighting - Nursing Home | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4308 | 0.06617 | 285.0535 | 0.032 | 137.856 | 0.03417 | 147.1975 | 0.020341 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 38.87
eDSM | Lighting - Nursing Home | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4308 | 0.09191 | 395.9603 | 0.042 | 180.936 | 0.04991 | 215.0243 | 0.029714 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 104.06
eDSM | Lighting - Other Commercial Buildings | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4000 | 0.06437 | 257.4894 | 0.031 | 124 | 0.03337 | 133.4894 | 0.01222 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 83.95
eDSM | Lighting - Other Commercial Buildings | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4000 | 0.06617 | 264.6737 | 0.032 | 128 | 0.03417 | 136.6737 | 0.012512 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 38.87
eDSM | Lighting - Other Commercial Buildings | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4000 | 0.09191 | 367.6511 | 0.042 | 168 | 0.04991 | 199.6511 | 0.018277 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 104.06
eDSM | Lighting - Other Non-Food Retail | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4089 | 0.06437 | 263.2185 | 0.031 | 126.759 | 0.03337 | 136.4595 | 0.01969 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 83.95
eDSM | Lighting - Other Non-Food Retail | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4089 | 0.06617 | 270.5626 | 0.032 | 130.848 | 0.03417 | 139.7146 | 0.02016 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 38.87
eDSM | Lighting - Other Non-Food Retail | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4089 | 0.09191 | 375.8314 | 0.042 | 171.738 | 0.04991 | 204.0934 | 0.029449 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 104.06
eDSM | Lighting - Restaurant | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 5110 | 0.06437 | 328.9427 | 0.031 | 158.41 | 0.03337 | 170.5327 | 0.026877 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 83.95
eDSM | Lighting - Restaurant | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 5110 | 0.06617 | 338.1206 | 0.032 | 163.52 | 0.03417 | 174.6006 | 0.027519 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 38.87
eDSM | Lighting - Restaurant | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 5110 | 0.09191 | 469.6743 | 0.042 | 214.62 | 0.04991 | 255.0543 | 0.040199 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 104.06
eDSM | Lighting - Schools | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 2596 | 0.06437 | 167.1106 | 0.031 | 80.476 | 0.03337 | 86.6346 | 0.0034196 | 19 | PSP-Business-Schools-Lighting_Interior_General | 83.95
eDSM | Lighting - Schools | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 2596 | 0.06617 | 171.7732 | 0.032 | 83.072 | 0.03417 | 88.7012 | 0.0035012 | 19 | PSP-Business-Schools-Lighting_Interior_General | 38.87
eDSM | Lighting - Schools | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 2596 | 0.09191 | 238.6056 | 0.042 | 109.032 | 0.04991 | 129.5736 | 0.0051145 | 19 | PSP-Business-Schools-Lighting_Interior_General | 104.06
eDSM | Lighting - University Colleges | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 3255 | 0.06437 | 209.532 | 0.031 | 100.905 | 0.03337 | 108.627 | 0.011117 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 83.95
eDSM | Lighting - University Colleges | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 3255 | 0.06617 | 215.3782 | 0.032 | 104.16 | 0.03417 | 111.2182 | 0.011383 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 38.87
eDSM | Lighting - University Colleges | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 3255 | 0.09191 | 299.1761 | 0.042 | 136.71 | 0.04991 | 162.4661 | 0.016627 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 104.06
eDSM | Lighting - Warehouse Wholesale | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4408 | 0.06437 | 283.743 | 0.031 | 136.648 | 0.03337 | 147.095 | 0.017432 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 83.95
eDSM | Lighting - Warehouse Wholesale | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4408 | 0.06617 | 291.6774 | 0.032 | 141.056 | 0.03417 | 150.6214 | 0.01785 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 38.87
eDSM | Lighting - Warehouse Wholesale | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4408 | 0.09191 | 405.1393 | 0.042 | 185.136 | 0.04991 | 220.0033 | 0.026072 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 104.06
eDSM | Lighting - Food Retail | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 6074 | 0.236 | 1433.464 | 0.0857 | 520.5418 | 0.1503 | 912.9222 | 0.12566 | 10 | PSP-Business-Food_Retail-Lighting_Interior_General | -449.44
eDSM | Lighting - Food Retail | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 6074 | 0.289 | 1755.386 | 0.1019 | 618.9406 | 0.1871 | 1136.4454 | 0.15643 | 10 | PSP-Business-Food_Retail-Lighting_Interior_General | -449.44
eDSM | Lighting - Food Retail | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 6074 | 0.367 | 2229.158 | 0.139 | 844.286 | 0.228 | 1384.872 | 0.19062 | 10 | PSP-Business-Food_Retail-Lighting_Interior_General | -135.51
eDSM | Lighting - Food Retail | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 6074 | 0.35 | 2125.9 | 0.194 | 1178.356 | 0.156 | 947.544 | 0.13042 | 10 | PSP-Business-Food_Retail-Lighting_Interior_General | -135.51
eDSM | Lighting - Food Retail | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 6074 | 0.901 | 5472.674 | 0.345 | 2095.53 | 0.556 | 3377.144 | 0.46485 | 10 | PSP-Business-Food_Retail-Lighting_Interior_General | -135.51
eDSM | Lighting - Hospital | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 5182 | 0.236 | 1222.952 | 0.0857 | 444.0974 | 0.1503 | 778.8546 | 0.088346 | 11 | PSP-Business-Hospital-Lighting_Interior_General | -449.44
eDSM | Lighting - Hospital | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 5182 | 0.289 | 1497.598 | 0.1019 | 528.0458 | 0.1871 | 969.5522 | 0.10998 | 11 | PSP-Business-Hospital-Lighting_Interior_General | -449.44
eDSM | Lighting - Hospital | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 5182 | 0.367 | 1901.794 | 0.139 | 720.298 | 0.228 | 1181.496 | 0.13402 | 11 | PSP-Business-Hospital-Lighting_Interior_General | -135.51
eDSM | Lighting - Hospital | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 5182 | 0.35 | 1813.7 | 0.194 | 1005.308 | 0.156 | 808.392 | 0.091696 | 11 | PSP-Business-Hospital-Lighting_Interior_General | -135.51
eDSM | Lighting - Hospital | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 5182 | 0.901 | 4668.982 | 0.345 | 1787.79 | 0.556 | 2881.192 | 0.32682 | 11 | PSP-Business-Hospital-Lighting_Interior_General | -135.51
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 7884 | 0.236 | 1860.624 | 0.0857 | 675.6588 | 0.1503 | 1184.9652 | 0.15505 | 8 | PSP-Business-Large_Hotel-Lighting_Interior_General | -449.44
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 7884 | 0.289 | 2278.476 | 0.1019 | 803.3796 | 0.1871 | 1475.0964 | 0.19302 | 8 | PSP-Business-Large_Hotel-Lighting_Interior_General | -449.44
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 7884 | 0.367 | 2893.428 | 0.139 | 1095.876 | 0.228 | 1797.552 | 0.23521 | 8 | PSP-Business-Large_Hotel-Lighting_Interior_General | -135.51
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 7884 | 0.35 | 2759.4 | 0.194 | 1529.496 | 0.156 | 1229.904 | 0.16093 | 8 | PSP-Business-Large_Hotel-Lighting_Interior_General | -135.51
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 7884 | 0.901 | 7103.484 | 0.345 | 2719.98 | 0.556 | 4383.504 | 0.57359 | 8 | PSP-Business-Large_Hotel-Lighting_Interior_General | -135.51
eDSM | Lighting - Large Non-Food Retail | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 3121 | 0.236 | 736.556 | 0.0857 | 267.4697 | 0.1503 | 469.0863 | 0.069566 | 14 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -449.44
eDSM | Lighting - Large Non-Food Retail | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 3121 | 0.289 | 901.969 | 0.1019 | 318.0299 | 0.1871 | 583.9391 | 0.086599 | 14 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -449.44
eDSM | Lighting - Large Non-Food Retail | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 3121 | 0.367 | 1145.407 | 0.139 | 433.819 | 0.228 | 711.588 | 0.10553 | 14 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -135.51
eDSM | Lighting - Large Non-Food Retail | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 3121 | 0.35 | 1092.35 | 0.194 | 605.474 | 0.156 | 486.876 | 0.072204 | 14 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -135.51
eDSM | Lighting - Large Non-Food Retail | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 3121 | 0.901 | 2812.021 | 0.345 | 1076.745 | 0.556 | 1735.276 | 0.25734 | 14 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -135.51
eDSM | Lighting - Large Office | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 3610 | 0.236 | 851.96 | 0.0857 | 309.377 | 0.1503 | 542.583 | 0.068809 | 16 | PSP-Business-Large_Office-Lighting_Interior_General | -449.44
eDSM | Lighting - Large Office | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 3610 | 0.289 | 1043.29 | 0.1019 | 367.859 | 0.1871 | 675.431 | 0.085657 | 16 | PSP-Business-Large_Office-Lighting_Interior_General | -449.44
eDSM | Lighting - Large Office | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 3610 | 0.367 | 1324.87 | 0.139 | 501.79 | 0.228 | 823.08 | 0.10438 | 16 | PSP-Business-Large_Office-Lighting_Interior_General | -135.51
eDSM | Lighting - Large Office | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 3610 | 0.35 | 1263.5 | 0.194 | 700.34 | 0.156 | 563.16 | 0.071419 | 16 | PSP-Business-Large_Office-Lighting_Interior_General | -135.51
eDSM | Lighting - Large Office | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 3610 | 0.901 | 3252.61 | 0.345 | 1245.45 | 0.556 | 2007.16 | 0.25454 | 16 | PSP-Business-Large_Office-Lighting_Interior_General | -135.51
eDSM | Lighting - Nursing Home | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 4308 | 0.236 | 1016.688 | 0.0857 | 369.1956 | 0.1503 | 647.4924 | 0.089477 | 14 | PSP-Business-Nursing_Home-Lighting_Interior_General | -449.44
eDSM | Lighting - Nursing Home | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 4308 | 0.289 | 1245.012 | 0.1019 | 438.9852 | 0.1871 | 806.0268 | 0.11138 | 14 | PSP-Business-Nursing_Home-Lighting_Interior_General | -449.44
eDSM | Lighting - Nursing Home | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 4308 | 0.367 | 1581.036 | 0.139 | 598.812 | 0.228 | 982.224 | 0.13573 | 14 | PSP-Business-Nursing_Home-Lighting_Interior_General | -135.51
eDSM | Lighting - Nursing Home | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 4308 | 0.35 | 1507.8 | 0.194 | 835.752 | 0.156 | 672.048 | 0.09287 | 14 | PSP-Business-Nursing_Home-Lighting_Interior_General | -135.51
eDSM | Lighting - Nursing Home | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 4308 | 0.901 | 3881.508 | 0.345 | 1486.26 | 0.556 | 2395.248 | 0.331 | 14 | PSP-Business-Nursing_Home-Lighting_Interior_General | -135.51
eDSM | Lighting - Other Commercial Buildings | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 4000 | 0.236 | 944 | 0.0857 | 342.8 | 0.1503 | 601.2 | 0.055038 | 20 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -449.44
eDSM | Lighting - Other Commercial Buildings | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 4000 | 0.289 | 1156 | 0.1019 | 407.6 | 0.1871 | 748.4 | 0.068513 | 20 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -449.44
eDSM | Lighting - Other Commercial Buildings | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 4000 | 0.367 | 1468 | 0.139 | 556 | 0.228 | 912 | 0.08349 | 20 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -135.51
eDSM | Lighting - Other Commercial Buildings | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 4000 | 0.35 | 1400 | 0.194 | 776 | 0.156 | 624 | 0.057125 | 20 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -135.51
eDSM | Lighting - Other Commercial Buildings | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 4000 | 0.901 | 3604 | 0.345 | 1380 | 0.556 | 2224 | 0.2036 | 20 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -135.51
eDSM | Lighting - Other Non-Food Retail | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 4089 | 0.236 | 965.004 | 0.0857 | 350.4273 | 0.1503 | 614.5767 | 0.088678 | 14 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -449.44
eDSM | Lighting - Other Non-Food Retail | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 4089 | 0.289 | 1181.721 | 0.1019 | 416.6691 | 0.1871 | 765.0519 | 0.11039 | 14 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -449.44
eDSM | Lighting - Other Non-Food Retail | LED HIGH BAY FIXTURE | >= 15,500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 4089 | 0.367 | 1500.663 | 0.139 | 568.371 | 0.228 | 932.292 | 0.13452 | 14 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -135.51
eDSM | Lighting - Other Non-Food Retail | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 4089 | 0.35 | 1431.15 | 0.194 | 793.266 | 0.156 | 637.884 | 0.092041 | 14 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -135.51
eDSM | Lighting - Other Non-Food Retail | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 4089 | 0.901 | 3684.189 | 0.345 | 1410.705 | 0.556 | 2273.484 | 0.32804 | 14 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -135.51
eDSM | Lighting - Restaurant | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 5110 | 0.236 | 1205.96 | 0.0857 | 437.927 | 0.1503 | 768.033 | 0.12105 | 12 | PSP-Business-Restaurant-Lighting_Interior_General | -449.44
eDSM | Lighting - Restaurant | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 5110 | 0.289 | 1476.79 | 0.1019 | 520.709 | 0.1871 | 956.081 | 0.15069 | 12 | PSP-Business-Restaurant-Lighting_Interior_General | -449.44
eDSM | Lighting - Restaurant | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 5110 | 0.367 | 1875.37 | 0.139 | 710.29 | 0.228 | 1165.08 | 0.18363 | 12 | PSP-Business-Restaurant-Lighting_Interior_General | -135.51
eDSM | Lighting - Restaurant | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 5110 | 0.35 | 1788.5 | 0.194 | 991.34 | 0.156 | 797.16 | 0.12564 | 12 | PSP-Business-Restaurant-Lighting_Interior_General | -135.51
eDSM | Lighting - Restaurant | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 5110 | 0.901 | 4604.11 | 0.345 | 1762.95 | 0.556 | 2841.16 | 0.44779 | 12 | PSP-Business-Restaurant-Lighting_Interior_General | -135.51
eDSM | Lighting - Schools | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 2596 | 0.236 | 612.656 | 0.0857 | 222.4772 | 0.1503 | 390.1788 | 0.015401 | 22 | PSP-Business-Schools-Lighting_Interior_General | -449.44
eDSM | Lighting - Schools | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 2596 | 0.289 | 750.244 | 0.1019 | 264.5324 | 0.1871 | 485.7116 | 0.019172 | 22 | PSP-Business-Schools-Lighting_Interior_General | -449.44
eDSM | Lighting - Schools | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 2596 | 0.367 | 952.732 | 0.139 | 360.844 | 0.228 | 591.888 | 0.023363 | 22 | PSP-Business-Schools-Lighting_Interior_General | -135.51
eDSM | Lighting - Schools | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 2596 | 0.35 | 908.6 | 0.194 | 503.624 | 0.156 | 404.976 | 0.015985 | 22 | PSP-Business-Schools-Lighting_Interior_General | -135.51
eDSM | Lighting - Schools | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 2596 | 0.901 | 2338.996 | 0.345 | 895.62 | 0.556 | 1443.376 | 0.056972 | 22 | PSP-Business-Schools-Lighting_Interior_General | -135.51
eDSM | Lighting - University Colleges | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 3255 | 0.236 | 768.18 | 0.0857 | 278.9535 | 0.1503 | 489.2265 | 0.050069 | 18 | PSP-Business-University_Colleges-Lighting_Interior_General | -449.44
eDSM | Lighting - University Colleges | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 3255 | 0.289 | 940.695 | 0.1019 | 331.6845 | 0.1871 | 609.0105 | 0.062329 | 18 | PSP-Business-University_Colleges-Lighting_Interior_General | -449.44
eDSM | Lighting - University Colleges | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 3255 | 0.367 | 1194.585 | 0.139 | 452.445 | 0.228 | 742.14 | 0.075954 | 18 | PSP-Business-University_Colleges-Lighting_Interior_General | -135.51
eDSM | Lighting - University Colleges | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 3255 | 0.35 | 1139.25 | 0.194 | 631.47 | 0.156 | 507.78 | 0.051968 | 18 | PSP-Business-University_Colleges-Lighting_Interior_General | -135.51
eDSM | Lighting - University Colleges | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 3255 | 0.901 | 2932.755 | 0.345 | 1122.975 | 0.556 | 1809.78 | 0.18522 | 18 | PSP-Business-University_Colleges-Lighting_Interior_General | -135.51
eDSM | Lighting - Warehouse Wholesale | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 4408 | 0.236 | 1040.288 | 0.0857 | 377.7656 | 0.1503 | 662.5224 | 0.078513 | 16 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -449.44
eDSM | Lighting - Warehouse Wholesale | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 4408 | 0.289 | 1273.912 | 0.1019 | 449.1752 | 0.1871 | 824.7368 | 0.097736 | 16 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -449.44
eDSM | Lighting - Warehouse Wholesale | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 4408 | 0.367 | 1617.736 | 0.139 | 612.712 | 0.228 | 1005.024 | 0.1191 | 16 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -135.51
eDSM | Lighting - Warehouse Wholesale | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 4408 | 0.35 | 1542.8 | 0.194 | 855.152 | 0.156 | 687.648 | 0.08149 | 16 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -135.51
eDSM | Lighting - Warehouse Wholesale | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 4408 | 0.901 | 3971.608 | 0.345 | 1520.76 | 0.556 | 2450.848 | 0.29044 | 16 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -135.51
eDSM | Lighting - Food Retail | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 6074 | 0.11477 | 697.1368 | 0.053 | 321.922 | 0.06177 | 375.2148 | 0.051646 | 8 | PSP-Business-Food_Retail-Lighting_Interior_General | 184
eDSM | Lighting - Hospital | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 5182 | 0.11477 | 594.7585 | 0.053 | 274.646 | 0.06177 | 320.1125 | 0.036311 | 10 | PSP-Business-Hospital-Lighting_Interior_General | 184
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 7884 | 0.11477 | 904.8776 | 0.053 | 417.852 | 0.06177 | 487.0256 | 0.063728 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 184
eDSM | Lighting - Large Non-Food Retail | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 3121 | 0.11477 | 358.1972 | 0.053 | 165.413 | 0.06177 | 192.7842 | 0.02859 | 12 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 184
eDSM | Lighting - Large Office | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 3610 | 0.11477 | 414.3339 | 0.053 | 191.33 | 0.06177 | 223.0039 | 0.028281 | 14 | PSP-Business-Large_Office-Lighting_Interior_General | 184
eDSM | Lighting - Nursing Home | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 4308 | 0.11477 | 494.4461 | 0.053 | 228.324 | 0.06177 | 266.1221 | 0.036775 | 12 | PSP-Business-Nursing_Home-Lighting_Interior_General | 184
eDSM | Lighting - Other Commercial Buildings | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 4000 | 0.11477 | 459.0957 | 0.053 | 212 | 0.06177 | 247.0957 | 0.022621 | 18 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 184
eDSM | Lighting - Other Non-Food Retail | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 4089 | 0.11477 | 469.3106 | 0.053 | 216.717 | 0.06177 | 252.5936 | 0.036447 | 12 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 184
eDSM | Lighting - Restaurant | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 5110 | 0.11477 | 586.4947 | 0.053 | 270.83 | 0.06177 | 315.6647 | 0.049752 | 10 | PSP-Business-Restaurant-Lighting_Interior_General | 184
eDSM | Lighting - Schools | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 2596 | 0.11477 | 297.9531 | 0.053 | 137.588 | 0.06177 | 160.3651 | 0.0063299 | 19 | PSP-Business-Schools-Lighting_Interior_General | 184
eDSM | Lighting - University Colleges | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 3255 | 0.11477 | 373.5891 | 0.053 | 172.515 | 0.06177 | 201.0741 | 0.020579 | 15 | PSP-Business-University_Colleges-Lighting_Interior_General | 184
eDSM | Lighting - Warehouse Wholesale | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 4408 | 0.11477 | 505.9062 | 0.053 | 233.624 | 0.06177 | 272.2822 | 0.032267 | 13 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 184
eDSM | Lighting - Food Retail | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 6074 | 0.0165 | 100.221 | 0.0094 | 57.0956 | 0.0071 | 43.1254 | 0.005936 | 7 | PSP-Business-Food_Retail-Lighting_Interior_General | 15.71
eDSM | Lighting - Food Retail | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 6074 | 0.022 | 133.628 | 0.012 | 72.888 | 0.01 | 60.74 | 0.0083605 | 7 | PSP-Business-Food_Retail-Lighting_Interior_General | 55.36
eDSM | Lighting - Food Retail | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 6074 | 0.026 | 157.924 | 0.0153 | 92.9322 | 0.0107 | 64.9918 | 0.0089458 | 7 | PSP-Business-Food_Retail-Lighting_Interior_General | 55.82
eDSM | Lighting - Hospital | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 5182 | 0.0165 | 85.503 | 0.0094 | 48.7108 | 0.0071 | 36.7922 | 0.0041734 | 8 | PSP-Business-Hospital-Lighting_Interior_General | 15.71
eDSM | Lighting - Hospital | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 5182 | 0.022 | 114.004 | 0.012 | 62.184 | 0.01 | 51.82 | 0.005878 | 8 | PSP-Business-Hospital-Lighting_Interior_General | 55.36
eDSM | Lighting - Hospital | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 5182 | 0.026 | 134.732 | 0.0153 | 79.2846 | 0.0107 | 55.4474 | 0.0062894 | 8 | PSP-Business-Hospital-Lighting_Interior_General | 55.82
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 7884 | 0.0165 | 130.086 | 0.0094 | 74.1096 | 0.0071 | 55.9764 | 0.0073246 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 15.71
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 7884 | 0.022 | 173.448 | 0.012 | 94.608 | 0.01 | 78.84 | 0.010316 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 55.36
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 7884 | 0.026 | 204.984 | 0.0153 | 120.6252 | 0.0107 | 84.3588 | 0.011038 | 6 | PSP-Business-Large_Hotel-Lighting_Interior_General | 55.82
eDSM | Lighting - Large Non-Food Retail | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 3121 | 0.0165 | 51.4965 | 0.0094 | 29.3374 | 0.0071 | 22.1591 | 0.0032862 | 11 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 15.71
eDSM | Lighting - Large Non-Food Retail | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 3121 | 0.022 | 68.662 | 0.012 | 37.452 | 0.01 | 31.21 | 0.0046285 | 11 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 55.36
eDSM | Lighting - Large Non-Food Retail | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 3121 | 0.026 | 81.146 | 0.0153 | 47.7513 | 0.0107 | 33.3947 | 0.0049525 | 11 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 55.82
eDSM | Lighting - Large Office | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 3610 | 0.0165 | 59.565 | 0.0094 | 33.934 | 0.0071 | 25.631 | 0.0032505 | 12 | PSP-Business-Large_Office-Lighting_Interior_General | 15.71
eDSM | Lighting - Large Office | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 3610 | 0.022 | 79.42 | 0.012 | 43.32 | 0.01 | 36.1 | 0.0045781 | 12 | PSP-Business-Large_Office-Lighting_Interior_General | 55.36
eDSM | Lighting - Large Office | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 3610 | 0.026 | 93.86 | 0.0153 | 55.233 | 0.0107 | 38.627 | 0.0048986 | 12 | PSP-Business-Large_Office-Lighting_Interior_General | 55.82
eDSM | Lighting - Nursing Home | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 4308 | 0.0165 | 71.082 | 0.0094 | 40.4952 | 0.0071 | 30.5868 | 0.0042268 | 10 | PSP-Business-Nursing_Home-Lighting_Interior_General | 15.71
eDSM | Lighting - Nursing Home | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 4308 | 0.022 | 94.776 | 0.012 | 51.696 | 0.01 | 43.08 | 0.0059532 | 10 | PSP-Business-Nursing_Home-Lighting_Interior_General | 55.36
eDSM | Lighting - Nursing Home | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 4308 | 0.026 | 112.008 | 0.0153 | 65.9124 | 0.0107 | 46.0956 | 0.0063699 | 10 | PSP-Business-Nursing_Home-Lighting_Interior_General | 55.82
eDSM | Lighting - Other Commercial Buildings | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 4000 | 0.0165 | 66 | 0.0094 | 37.6 | 0.0071 | 28.4 | 0.0025999 | 15 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 15.71
eDSM | Lighting - Other Commercial Buildings | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 4000 | 0.022 | 88 | 0.012 | 48 | 0.01 | 40 | 0.0036619 | 15 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 55.36
eDSM | Lighting - Other Commercial Buildings | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 4000 | 0.026 | 104 | 0.0153 | 61.2 | 0.0107 | 42.8 | 0.0039182 | 15 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 55.82
eDSM | Lighting - Other Non-Food Retail | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 4089 | 0.0165 | 67.4685 | 0.0094 | 38.4366 | 0.0071 | 29.0319 | 0.004189 | 11 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 15.71
eDSM | Lighting - Other Non-Food Retail | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 4089 | 0.022 | 89.958 | 0.012 | 49.068 | 0.01 | 40.89 | 0.0059001 | 11 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 55.36
eDSM | Lighting - Other Non-Food Retail | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 4089 | 0.026 | 106.314 | 0.0153 | 62.5617 | 0.0107 | 43.7523 | 0.0063131 | 11 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 55.82
eDSM | Lighting - Restaurant | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 5110 | 0.0165 | 84.315 | 0.0094 | 48.034 | 0.0071 | 36.281 | 0.0057182 | 9 | PSP-Business-Restaurant-Lighting_Interior_General | 15.71
eDSM | Lighting - Restaurant | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 5110 | 0.022 | 112.42 | 0.012 | 61.32 | 0.01 | 51.1 | 0.0080538 | 9 | PSP-Business-Restaurant-Lighting_Interior_General | 55.36
eDSM | Lighting - Restaurant | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 5110 | 0.026 | 132.86 | 0.0153 | 78.183 | 0.0107 | 54.677 | 0.0086176 | 9 | PSP-Business-Restaurant-Lighting_Interior_General | 55.82
eDSM | Lighting - Schools | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 2596 | 0.0165 | 42.834 | 0.0094 | 24.4024 | 0.0071 | 18.4316 | 0.00072752 | 17 | PSP-Business-Schools-Lighting_Interior_General | 15.71
eDSM | Lighting - Schools | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 2596 | 0.022 | 57.112 | 0.012 | 31.152 | 0.01 | 25.96 | 0.0010247 | 17 | PSP-Business-Schools-Lighting_Interior_General | 55.36
eDSM | Lighting - Schools | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 2596 | 0.026 | 67.496 | 0.0153 | 39.7188 | 0.0107 | 27.7772 | 0.0010964 | 17 | PSP-Business-Schools-Lighting_Interior_General | 55.82
eDSM | Lighting - University Colleges | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 3255 | 0.0165 | 53.7075 | 0.0094 | 30.597 | 0.0071 | 23.1105 | 0.0023652 | 14 | PSP-Business-University_Colleges-Lighting_Interior_General | 15.71
eDSM | Lighting - University Colleges | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 3255 | 0.022 | 71.61 | 0.012 | 39.06 | 0.01 | 32.55 | 0.0033313 | 14 | PSP-Business-University_Colleges-Lighting_Interior_General | 55.36
eDSM | Lighting - University Colleges | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 3255 | 0.026 | 84.63 | 0.0153 | 49.8015 | 0.0107 | 34.8285 | 0.0035645 | 14 | PSP-Business-University_Colleges-Lighting_Interior_General | 55.82
eDSM | Lighting - Warehouse Wholesale | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 4408 | 0.0165 | 72.732 | 0.0094 | 41.4352 | 0.0071 | 31.2968 | 0.0037089 | 12 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 15.71
eDSM | Lighting - Warehouse Wholesale | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 4408 | 0.022 | 96.976 | 0.012 | 52.896 | 0.01 | 44.08 | 0.0052237 | 12 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 55.36
eDSM | Lighting - Warehouse Wholesale | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 4408 | 0.026 | 114.608 | 0.0153 | 67.4424 | 0.0107 | 47.1656 | 0.0055894 | 12 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 55.82
eDSM | Lighting - Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 6074 | 0.0365 | 221.701 | 0.0075 | 45.555 | 0.029 | 176.146 | 0.024246 | 4 | PSP-Business-Food_Retail-Lighting_Interior_General | -55.06
eDSM | Lighting - Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 6074 | 0.0405 | 245.997 | 0.011 | 66.814 | 0.0295 | 179.183 | 0.024664 | 4 | PSP-Business-Food_Retail-Lighting_Interior_General | -27.42
eDSM | Lighting - Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 6074 | 0.0515 | 312.811 | 0.013 | 78.962 | 0.0385 | 233.849 | 0.032188 | 4 | PSP-Business-Food_Retail-Lighting_Interior_General | -37.86
eDSM | Lighting - Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 6074 | 0.07 | 425.18 | 0.0175 | 106.295 | 0.0525 | 318.885 | 0.043893 | 4 | PSP-Business-Food_Retail-Lighting_Interior_General | -138.68
eDSM | Lighting - Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 6074 | 0.0275 | 167.035 | 0.006 | 36.444 | 0.0215 | 130.591 | 0.017975 | 4 | PSP-Business-Food_Retail-Lighting_Interior_General | -94.29
eDSM | Lighting - Hospital | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 5182 | 0.0365 | 189.143 | 0.0075 | 38.865 | 0.029 | 150.278 | 0.017046 | 5 | PSP-Business-Hospital-Lighting_Interior_General | -55.06
eDSM | Lighting - Hospital | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 5182 | 0.0405 | 209.871 | 0.011 | 57.002 | 0.0295 | 152.869 | 0.01734 | 5 | PSP-Business-Hospital-Lighting_Interior_General | -27.42
eDSM | Lighting - Hospital | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 5182 | 0.0515 | 266.873 | 0.013 | 67.366 | 0.0385 | 199.507 | 0.02263 | 5 | PSP-Business-Hospital-Lighting_Interior_General | -37.86
eDSM | Lighting - Hospital | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 5182 | 0.07 | 362.74 | 0.0175 | 90.685 | 0.0525 | 272.055 | 0.030859 | 5 | PSP-Business-Hospital-Lighting_Interior_General | -138.68
eDSM | Lighting - Hospital | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 5182 | 0.0275 | 142.505 | 0.006 | 31.092 | 0.0215 | 111.413 | 0.012638 | 5 | PSP-Business-Hospital-Lighting_Interior_General | -94.29
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 7884 | 0.0365 | 287.766 | 0.0075 | 59.13 | 0.029 | 228.636 | 0.029917 | 3 | PSP-Business-Large_Hotel-Lighting_Interior_General | -55.06
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 7884 | 0.0405 | 319.302 | 0.011 | 86.724 | 0.0295 | 232.578 | 0.030433 | 3 | PSP-Business-Large_Hotel-Lighting_Interior_General | -27.42
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 7884 | 0.0515 | 406.026 | 0.013 | 102.492 | 0.0385 | 303.534 | 0.039718 | 3 | PSP-Business-Large_Hotel-Lighting_Interior_General | -37.86
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 7884 | 0.07 | 551.88 | 0.0175 | 137.97 | 0.0525 | 413.91 | 0.054161 | 3 | PSP-Business-Large_Hotel-Lighting_Interior_General | -138.68
eDSM | Lighting - Large Hotel (Corridor/Lobby) | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 7884 | 0.0275 | 216.81 | 0.006 | 47.304 | 0.0215 | 169.506 | 0.02218 | 3 | PSP-Business-Large_Hotel-Lighting_Interior_General | -94.29
eDSM | Lighting - Large Non-Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 3121 | 0.0365 | 113.9165 | 0.0075 | 23.4075 | 0.029 | 90.509 | 0.013423 | 6 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -55.06
eDSM | Lighting - Large Non-Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 3121 | 0.0405 | 126.4005 | 0.011 | 34.331 | 0.0295 | 92.0695 | 0.013654 | 6 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -27.42
eDSM | Lighting - Large Non-Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 3121 | 0.0515 | 160.7315 | 0.013 | 40.573 | 0.0385 | 120.1585 | 0.01782 | 6 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -37.86
eDSM | Lighting - Large Non-Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 3121 | 0.07 | 218.47 | 0.0175 | 54.6175 | 0.0525 | 163.8525 | 0.0243 | 6 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -138.68
eDSM | Lighting - Large Non-Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 3121 | 0.0275 | 85.8275 | 0.006 | 18.726 | 0.0215 | 67.1015 | 0.0099512 | 6 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | -94.29
eDSM | Lighting - Large Office | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 3610 | 0.0365 | 131.765 | 0.0075 | 27.075 | 0.029 | 104.69 | 0.013277 | 7 | PSP-Business-Large_Office-Lighting_Interior_General | -55.06
eDSM | Lighting - Large Office | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 3610 | 0.0405 | 146.205 | 0.011 | 39.71 | 0.0295 | 106.495 | 0.013506 | 7 | PSP-Business-Large_Office-Lighting_Interior_General | -27.42
eDSM | Lighting - Large Office | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 3610 | 0.0515 | 185.915 | 0.013 | 46.93 | 0.0385 | 138.985 | 0.017626 | 7 | PSP-Business-Large_Office-Lighting_Interior_General | -37.86
eDSM | Lighting - Large Office | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 3610 | 0.07 | 252.7 | 0.0175 | 63.175 | 0.0525 | 189.525 | 0.024035 | 7 | PSP-Business-Large_Office-Lighting_Interior_General | -138.68
eDSM | Lighting - Large Office | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 3610 | 0.0275 | 99.275 | 0.006 | 21.66 | 0.0215 | 77.615 | 0.009843 | 7 | PSP-Business-Large_Office-Lighting_Interior_General | -94.29
eDSM | Lighting - Nursing Home | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 4308 | 0.0365 | 157.242 | 0.0075 | 32.31 | 0.029 | 124.932 | 0.017264 | 6 | PSP-Business-Nursing_Home-Lighting_Interior_General | -55.06
eDSM | Lighting - Nursing Home | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 4308 | 0.0405 | 174.474 | 0.011 | 47.388 | 0.0295 | 127.086 | 0.017562 | 6 | PSP-Business-Nursing_Home-Lighting_Interior_General | -27.42
eDSM | Lighting - Nursing Home | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 4308 | 0.0515 | 221.862 | 0.013 | 56.004 | 0.0385 | 165.858 | 0.02292 | 6 | PSP-Business-Nursing_Home-Lighting_Interior_General | -37.86
eDSM | Lighting - Nursing Home | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 4308 | 0.07 | 301.56 | 0.0175 | 75.39 | 0.0525 | 226.17 | 0.031254 | 6 | PSP-Business-Nursing_Home-Lighting_Interior_General | -138.68
eDSM | Lighting - Nursing Home | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 4308 | 0.0275 | 118.47 | 0.006 | 25.848 | 0.0215 | 92.622 | 0.012799 | 6 | PSP-Business-Nursing_Home-Lighting_Interior_General | -94.29
eDSM | Lighting - Other Commercial Buildings | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 4000 | 0.0365 | 146 | 0.0075 | 30 | 0.029 | 116 | 0.010619 | 9 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -55.06
eDSM | Lighting - Other Commercial Buildings | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 4000 | 0.0405 | 162 | 0.011 | 44 | 0.0295 | 118 | 0.010802 | 9 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -27.42
eDSM | Lighting - Other Commercial Buildings | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 4000 | 0.0515 | 206 | 0.013 | 52 | 0.0385 | 154 | 0.014098 | 9 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -37.86
eDSM | Lighting - Other Commercial Buildings | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 4000 | 0.07 | 280 | 0.0175 | 70 | 0.0525 | 210 | 0.019225 | 9 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -138.68
eDSM | Lighting - Other Commercial Buildings | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 4000 | 0.0275 | 110 | 0.006 | 24 | 0.0215 | 86 | 0.007873 | 9 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | -94.29
eDSM | Lighting - Other Non-Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 4089 | 0.0365 | 149.2485 | 0.0075 | 30.6675 | 0.029 | 118.581 | 0.01711 | 6 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -55.06
eDSM | Lighting - Other Non-Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 4089 | 0.0405 | 165.6045 | 0.011 | 44.979 | 0.0295 | 120.6255 | 0.017405 | 6 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -27.42
eDSM | Lighting - Other Non-Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 4089 | 0.0515 | 210.5835 | 0.013 | 53.157 | 0.0385 | 157.4265 | 0.022715 | 6 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -37.86
eDSM | Lighting - Other Non-Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 4089 | 0.07 | 286.23 | 0.0175 | 71.5575 | 0.0525 | 214.6725 | 0.030975 | 6 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -138.68
eDSM | Lighting - Other Non-Food Retail | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 4089 | 0.0275 | 112.4475 | 0.006 | 24.534 | 0.0215 | 87.9135 | 0.012685 | 6 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | -94.29
eDSM | Lighting - Restaurant | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 5110 | 0.0365 | 186.515 | 0.0075 | 38.325 | 0.029 | 148.19 | 0.023356 | 5 | PSP-Business-Restaurant-Lighting_Interior_General | -55.06
eDSM | Lighting - Restaurant | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 5110 | 0.0405 | 206.955 | 0.011 | 56.21 | 0.0295 | 150.745 | 0.023759 | 5 | PSP-Business-Restaurant-Lighting_Interior_General | -27.42
eDSM | Lighting - Restaurant | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 5110 | 0.0515 | 263.165 | 0.013 | 66.43 | 0.0385 | 196.735 | 0.031007 | 5 | PSP-Business-Restaurant-Lighting_Interior_General | -37.86
eDSM | Lighting - Restaurant | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 5110 | 0.07 | 357.7 | 0.0175 | 89.425 | 0.0525 | 268.275 | 0.042282 | 5 | PSP-Business-Restaurant-Lighting_Interior_General | -138.68
eDSM | Lighting - Restaurant | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 5110 | 0.0275 | 140.525 | 0.006 | 30.66 | 0.0215 | 109.865 | 0.017316 | 5 | PSP-Business-Restaurant-Lighting_Interior_General | -94.29
eDSM | Lighting - Schools | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 2596 | 0.0365 | 94.754 | 0.0075 | 19.47 | 0.029 | 75.284 | 0.0029716 | 10 | PSP-Business-Schools-Lighting_Interior_General | -55.06
eDSM | Lighting - Schools | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 2596 | 0.0405 | 105.138 | 0.011 | 28.556 | 0.0295 | 76.582 | 0.0030228 | 10 | PSP-Business-Schools-Lighting_Interior_General | -27.42
eDSM | Lighting - Schools | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 2596 | 0.0515 | 133.694 | 0.013 | 33.748 | 0.0385 | 99.946 | 0.003945 | 10 | PSP-Business-Schools-Lighting_Interior_General | -37.86
eDSM | Lighting - Schools | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 2596 | 0.07 | 181.72 | 0.0175 | 45.43 | 0.0525 | 136.29 | 0.0053796 | 10 | PSP-Business-Schools-Lighting_Interior_General | -138.68
eDSM | Lighting - Schools | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 2596 | 0.0275 | 71.39 | 0.006 | 15.576 | 0.0215 | 55.814 | 0.0022031 | 10 | PSP-Business-Schools-Lighting_Interior_General | -94.29
eDSM | Lighting - University Colleges | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 3255 | 0.0365 | 118.8075 | 0.0075 | 24.4125 | 0.029 | 94.395 | 0.0096608 | 8 | PSP-Business-University_Colleges-Lighting_Interior_General | -55.06
eDSM | Lighting - University Colleges | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 3255 | 0.0405 | 131.8275 | 0.011 | 35.805 | 0.0295 | 96.0225 | 0.0098273 | 8 | PSP-Business-University_Colleges-Lighting_Interior_General | -27.42
eDSM | Lighting - University Colleges | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 3255 | 0.0515 | 167.6325 | 0.013 | 42.315 | 0.0385 | 125.3175 | 0.012826 | 8 | PSP-Business-University_Colleges-Lighting_Interior_General | -37.86
eDSM | Lighting - University Colleges | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 3255 | 0.07 | 227.85 | 0.0175 | 56.9625 | 0.0525 | 170.8875 | 0.017489 | 8 | PSP-Business-University_Colleges-Lighting_Interior_General | -138.68
eDSM | Lighting - University Colleges | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 3255 | 0.0275 | 89.5125 | 0.006 | 19.53 | 0.0215 | 69.9825 | 0.0071623 | 8 | PSP-Business-University_Colleges-Lighting_Interior_General | -94.29
eDSM | Lighting - Warehouse Wholesale | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 4408 | 0.0365 | 160.892 | 0.0075 | 33.06 | 0.029 | 127.832 | 0.015149 | 7 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -55.06
eDSM | Lighting - Warehouse Wholesale | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 4408 | 0.0405 | 178.524 | 0.011 | 48.488 | 0.0295 | 130.036 | 0.01541 | 7 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -27.42
eDSM | Lighting - Warehouse Wholesale | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 4408 | 0.0515 | 227.012 | 0.013 | 57.304 | 0.0385 | 169.708 | 0.020111 | 7 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -37.86
eDSM | Lighting - Warehouse Wholesale | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 4408 | 0.07 | 308.56 | 0.0175 | 77.14 | 0.0525 | 231.42 | 0.027425 | 7 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -138.68
eDSM | Lighting - Warehouse Wholesale | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 4408 | 0.0275 | 121.22 | 0.006 | 26.448 | 0.0215 | 94.772 | 0.011231 | 7 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | -94.29
eDSM | Lighting - Refrigeration | REFRIGERATED DISPLAY CASE LED FIXTURE - HORIZONTAL (UNDERSHELF) INSTALLATION | < 13W Nominal 24"-48" | Average of 2'-4' T8 (17W, 25W, 32W) | 6074 | 0.026 | 157.924 | 0.012 | 72.888 | 0.014 | 85.036 | 0.01209 | 8 | PSP-Business-Commercial-Refrigerated_Display_Case_Food Retail | 236.42
eDSM | Lighting - Refrigeration | REFRIGERATED DISPLAY CASE LED FIXTURE - VERTICAL INSTALLATION | < 30W Nominal 48"-72" | Average of 4'-6' T8 (32W, 40W, 44W, 46W, 55W, 66W) | 6074 | 0.041 | 249.034 | 0.029 | 176.146 | 0.012 | 72.888 | 0.010363 | 8 | PSP-Business-Commercial-Refrigerated_Display_Case_Food Retail | 230.48
eDSM | Lighting - Food Retail | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 6074 | 0.3 | 1822.2 | 0.3 | 1112.4531 | 0 | 709.7469 | 0.097693 | 5 | PSP-Business-Food_Retail-Lighting_Interior_General | 218
eDSM | Lighting - Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 6074 | 0.03 | 182.22 | 0.03 | 111.2453 | 0 | 70.9747 | 0.0097693 | 5 | PSP-Business-Food_Retail-Lighting_Interior_General | 356.95
eDSM | Lighting - Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 6074 | 0.12 | 728.88 | 0.12 | 444.9812 | 0 | 283.8988 | 0.039077 | 5 | PSP-Business-Food_Retail-Lighting_Interior_General | 291.21
eDSM | Lighting - Food Retail | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 6074 | 0.15 | 911.1 | 0.15 | 651.4365 | 0 | 259.6635 | 0.035741 | 5 | PSP-Business-Food_Retail-Lighting_Interior_General | 120.48
eDSM | Lighting - Hospital | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5182 | 0.3 | 1554.6 | 0.3 | 949.0833 | 0 | 605.5167 | 0.068684 | 6 | PSP-Business-Hospital-Lighting_Interior_General | 218
eDSM | Lighting - Hospital | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5182 | 0.03 | 155.46 | 0.03 | 94.9083 | 0 | 60.5517 | 0.0068684 | 6 | PSP-Business-Hospital-Lighting_Interior_General | 356.95
eDSM | Lighting - Hospital | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5182 | 0.12 | 621.84 | 0.12 | 379.6333 | 0 | 242.2067 | 0.027474 | 6 | PSP-Business-Hospital-Lighting_Interior_General | 291.21
eDSM | Lighting - Hospital | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5182 | 0.15 | 777.3 | 0.15 | 555.7695 | 0 | 221.5305 | 0.025128 | 6 | PSP-Business-Hospital-Lighting_Interior_General | 120.48
eDSM | Lighting - Large Hotel (Corridor/Lobby) | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 7884 | 0.3 | 2365.2 | 0.3 | 1443.9546 | 0 | 921.2454 | 0.12055 | 4 | PSP-Business-Large_Hotel-Lighting_Interior_General | 218
eDSM | Lighting - Large Hotel (Corridor/Lobby) | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 7884 | 0.03 | 236.52 | 0.03 | 144.3955 | 0 | 92.1245 | 0.012055 | 4 | PSP-Business-Large_Hotel-Lighting_Interior_General | 356.95
eDSM | Lighting - Large Hotel (Corridor/Lobby) | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 7884 | 0.12 | 946.08 | 0.12 | 577.5818 | 0 | 368.4982 | 0.048219 | 4 | PSP-Business-Large_Hotel-Lighting_Interior_General | 291.21
eDSM | Lighting - Large Hotel (Corridor/Lobby) | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 7884 | 0.15 | 1182.6 | 0.15 | 845.559 | 0 | 337.041 | 0.044102 | 4 | PSP-Business-Large_Hotel-Lighting_Interior_General | 120.48
eDSM | Lighting - Large Non-Food Retail | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3121 | 0.3 | 936.3 | 0.3 | 571.6112 | 0 | 364.6888 | 0.054084 | 8 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 218
eDSM | Lighting - Large Non-Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3121 | 0.03 | 93.63 | 0.03 | 57.1611 | 0 | 36.4689 | 0.0054084 | 8 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 356.95
eDSM | Lighting - Large Non-Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3121 | 0.12 | 374.52 | 0.12 | 228.6445 | 0 | 145.8755 | 0.021634 | 8 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 291.21
eDSM | Lighting - Large Non-Food Retail | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3121 | 0.15 | 468.15 | 0.15 | 334.7273 | 0 | 133.4227 | 0.019787 | 8 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 120.48
eDSM | Lighting - Large Office | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3610 | 0.3 | 1083 | 0.3 | 661.1715 | 0 | 421.8285 | 0.053496 | 9 | PSP-Business-Large_Office-Lighting_Interior_General | 218
eDSM | Lighting - Large Office | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3610 | 0.03 | 108.3 | 0.03 | 66.1171 | 0 | 42.1829 | 0.0053496 | 9 | PSP-Business-Large_Office-Lighting_Interior_General | 356.95
eDSM | Lighting - Large Office | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3610 | 0.12 | 433.2 | 0.12 | 264.4686 | 0 | 168.7314 | 0.021398 | 9 | PSP-Business-Large_Office-Lighting_Interior_General | 291.21
eDSM | Lighting - Large Office | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3610 | 0.15 | 541.5 | 0.15 | 387.1725 | 0 | 154.3275 | 0.019572 | 9 | PSP-Business-Large_Office-Lighting_Interior_General | 120.48
eDSM | Lighting - Nursing Home | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4308 | 0.3 | 1292.4 | 0.3 | 789.0102 | 0 | 503.3898 | 0.069563 | 7 | PSP-Business-Nursing_Home-Lighting_Interior_General | 218
eDSM | Lighting - Nursing Home | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4308 | 0.03 | 129.24 | 0.03 | 78.901 | 0 | 50.339 | 0.0069563 | 7 | PSP-Business-Nursing_Home-Lighting_Interior_General | 356.95
eDSM | Lighting - Nursing Home | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4308 | 0.12 | 516.96 | 0.12 | 315.6041 | 0 | 201.3559 | 0.027825 | 7 | PSP-Business-Nursing_Home-Lighting_Interior_General | 291.21
eDSM | Lighting - Nursing Home | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4308 | 0.15 | 646.2 | 0.15 | 462.033 | 0 | 184.167 | 0.02545 | 7 | PSP-Business-Nursing_Home-Lighting_Interior_General | 120.48
eDSM | Lighting - Other Commercial Buildings | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4000 | 0.3 | 1200 | 0.3 | 732.6 | 0 | 467.4 | 0.042789 | 11 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 218
eDSM | Lighting - Other Commercial Buildings | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4000 | 0.03 | 120 | 0.03 | 73.26 | 0 | 46.74 | 0.0042789 | 11 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 356.95
eDSM | Lighting - Other Commercial Buildings | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4000 | 0.12 | 480 | 0.12 | 293.04 | 0 | 186.96 | 0.017116 | 11 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 291.21
eDSM | Lighting - Other Commercial Buildings | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4000 | 0.15 | 600 | 0.15 | 429 | 0 | 171 | 0.015654 | 11 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 120.48
eDSM | Lighting - Other Non-Food Retail | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4089 | 0.3 | 1226.7 | 0.3 | 748.9004 | 0 | 477.7996 | 0.068942 | 8 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 218
eDSM | Lighting - Other Non-Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4089 | 0.03 | 122.67 | 0.03 | 74.89 | 0 | 47.78 | 0.0068942 | 8 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 356.95
eDSM | Lighting - Other Non-Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4089 | 0.12 | 490.68 | 0.12 | 299.5601 | 0 | 191.1199 | 0.027577 | 8 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 291.21
eDSM | Lighting - Other Non-Food Retail | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4089 | 0.15 | 613.35 | 0.15 | 438.5453 | 0 | 174.8048 | 0.025223 | 8 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 120.48
eDSM | Lighting - Restaurant | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5110 | 0.3 | 1533 | 0.3 | 935.8965 | 0 | 597.1035 | 0.094109 | 6 | PSP-Business-Restaurant-Lighting_Interior_General | 218
eDSM | Lighting - Restaurant | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5110 | 0.03 | 153.3 | 0.03 | 93.5897 | 0 | 59.7103 | 0.0094109 | 6 | PSP-Business-Restaurant-Lighting_Interior_General | 356.95
eDSM | Lighting - Restaurant | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5110 | 0.12 | 613.2 | 0.12 | 374.3586 | 0 | 238.8414 | 0.037643 | 6 | PSP-Business-Restaurant-Lighting_Interior_General | 291.21
eDSM | Lighting - Restaurant | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5110 | 0.15 | 766.5 | 0.15 | 548.0475 | 0 | 218.4525 | 0.03443 | 6 | PSP-Business-Restaurant-Lighting_Interior_General | 120.48
eDSM | Lighting - Schools | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 2596 | 0.3 | 778.8 | 0.3 | 475.4574 | 0 | 303.3426 | 0.011973 | 12 | PSP-Business-Schools-Lighting_Interior_General | 218
eDSM | Lighting - Schools | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 2596 | 0.03 | 77.88 | 0.03 | 47.5457 | 0 | 30.3343 | 0.0011973 | 12 | PSP-Business-Schools-Lighting_Interior_General | 356.95
eDSM | Lighting - Schools | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 2596 | 0.12 | 311.52 | 0.12 | 190.183 | 0 | 121.337 | 0.0047894 | 12 | PSP-Business-Schools-Lighting_Interior_General | 291.21
eDSM | Lighting - Schools | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 2596 | 0.15 | 389.4 | 0.15 | 278.421 | 0 | 110.979 | 0.0043805 | 12 | PSP-Business-Schools-Lighting_Interior_General | 120.48
eDSM | Lighting - University Colleges | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3255 | 0.3 | 976.5 | 0.3 | 596.1532 | 0 | 380.3467 | 0.038926 | 10 | PSP-Business-University_Colleges-Lighting_Interior_General | 218
eDSM | Lighting - University Colleges | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3255 | 0.03 | 97.65 | 0.03 | 67.3157 | 0 | 30.3343 | 0.0031045 | 10 | PSP-Business-University_Colleges-Lighting_Interior_General | 356.95
eDSM | Lighting - University Colleges | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3255 | 0.12 | 390.6 | 0.12 | 238.4613 | 0 | 152.1387 | 0.01557 | 10 | PSP-Business-University_Colleges-Lighting_Interior_General | 291.21
eDSM | Lighting - University Colleges | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3255 | 0.15 | 488.25 | 0.15 | 349.0987 | 0 | 139.1513 | 0.014241 | 10 | PSP-Business-University_Colleges-Lighting_Interior_General | 120.48
eDSM | Lighting - Warehouse Wholesale | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4408 | 0.3 | 1322.4 | 0.3 | 807.3252 | 0 | 515.0748 | 0.061039 | 9 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 218
eDSM | Lighting - Warehouse Wholesale | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4408 | 0.03 | 132.24 | 0.03 | 96.6685 | 0 | 35.5715 | 0.0042154 | 9 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 356.95
eDSM | Lighting - Warehouse Wholesale | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4408 | 0.12 | 528.96 | 0.12 | 322.9301 | 0 | 206.0299 | 0.024416 | 9 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 291.21
eDSM | Lighting - Warehouse Wholesale | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4408 | 0.15 | 661.2 | 0.15 | 472.758 | 0 | 188.442 | 0.022331 | 9 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 120.48
eDSM | Lighting - Industrial | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 4473 | 0.0405 | 181.1565 | 0.011 | 49.203 | 0.0295 | 131.9535 | 0.014252 | 9 | PSP-Business-Lighting_Industrial_General | -27.42
eDSM | Lighting - Industrial | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 4473 | 0.07 | 313.11 | 0.0175 | 78.2775 | 0.0525 | 234.8325 | 0.025365 | 9 | PSP-Business-Lighting_Industrial_General | -138.68
eDSM | Lighting - Industrial | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 4473 | 0.0275 | 123.0075 | 0.006 | 26.838 | 0.0215 | 96.1695 | 0.010387 | 9 | PSP-Business-Lighting_Industrial_General | -94.29
eDSM | Lighting - Industrial | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 4473 | 0.0365 | 163.2645 | 0.0075 | 33.5475 | 0.029 | 129.717 | 0.014011 | 9 | PSP-Business-Lighting_Industrial_General | -55.06
eDSM | Lighting - Industrial | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 4473 | 0.0515 | 230.3595 | 0.013 | 58.149 | 0.0385 | 172.2105 | 0.018601 | 9 | PSP-Business-Lighting_Industrial_General | -37.86
eDSM | Lighting - Industrial | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 4473 | 0.026 | 116.298 | 0.0153 | 68.4369 | 0.0107 | 47.8611 | 0.0051695 | 15 | PSP-Business-Lighting_Industrial_General | 55.82
eDSM | Lighting - Industrial | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 4473 | 0.022 | 98.406 | 0.012 | 53.676 | 0.01 | 44.73 | 0.0048314 | 15 | PSP-Business-Lighting_Industrial_General | 55.36
eDSM | Lighting - Industrial | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 4473 | 0.0165 | 73.8045 | 0.0094 | 42.0462 | 0.0071 | 31.7583 | 0.0034303 | 15 | PSP-Business-Lighting_Industrial_General | 15.71
eDSM | Lighting - Industrial | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 4473 | 0.11477 | 513.3662 | 0.053 | 237.069 | 0.06177 | 276.2972 | 0.029843 | 18 | PSP-Business-Lighting_Industrial_General | 184
eDSM | Lighting - Industrial | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 4473 | 0.901 | 4030.173 | 0.345 | 1543.185 | 0.556 | 2486.988 | 0.26862 | 20 | PSP-Business-Lighting_Industrial_General | -135.51
eDSM | Lighting - Industrial | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 4473 | 0.236 | 1055.628 | 0.0857 | 383.3361 | 0.1503 | 672.2919 | 0.072615 | 20 | PSP-Business-Lighting_Industrial_General | -449.44
eDSM | Lighting - Industrial | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 4473 | 0.289 | 1292.697 | 0.1019 | 455.7987 | 0.1871 | 836.8983 | 0.090395 | 20 | PSP-Business-Lighting_Industrial_General | -449.44
eDSM | Lighting - Industrial | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 4473 | 0.367 | 1641.591 | 0.139 | 621.747 | 0.228 | 1019.844 | 0.11015 | 20 | PSP-Business-Lighting_Industrial_General | -135.51
eDSM | Lighting - Industrial | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 4473 | 0.35 | 1565.55 | 0.194 | 867.762 | 0.156 | 697.788 | 0.075369 | 20 | PSP-Business-Lighting_Industrial_General | -135.51
eDSM | Lighting - Industrial | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4473 | 0.06437 | 287.927 | 0.031 | 138.663 | 0.03337 | 149.264 | 0.016122 | 18 | PSP-Business-Lighting_Industrial_General | 83.95
eDSM | Lighting - Industrial | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4473 | 0.09191 | 411.1134 | 0.042 | 187.866 | 0.04991 | 223.2474 | 0.024113 | 18 | PSP-Business-Lighting_Industrial_General | 104.06
eDSM | Lighting - Industrial | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4473 | 0.06617 | 295.9784 | 0.032 | 143.136 | 0.03417 | 152.8424 | 0.016509 | 18 | PSP-Business-Lighting_Industrial_General | 38.87
eDSM | Lighting - Industrial | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4473 | 0.06438 | 287.9717 | 0.0386 | 172.6578 | 0.02578 | 115.3139 | 0.012455 | 18 | PSP-Business-Lighting_Industrial_General | 114.37
eDSM | Lighting - Industrial | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4473 | 0.06618 | 296.0231 | 0.039 | 174.447 | 0.02718 | 121.5761 | 0.013132 | 18 | PSP-Business-Lighting_Industrial_General | 61.99
eDSM | Lighting - Industrial | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4473 | 0.09193 | 411.2029 | 0.044 | 196.812 | 0.04793 | 214.3909 | 0.023157 | 18 | PSP-Business-Lighting_Industrial_General | 116.78
eDSM | Lighting - Industrial | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 4473 | 0.06915 | 309.308 | 0.0377 | 168.6321 | 0.03145 | 140.6759 | 0.015195 | 18 | PSP-Business-Lighting_Industrial_General | -4.18
eDSM | Lighting - Industrial | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 4473 | 0.122 | 545.706 | 0.084 | 375.732 | 0.038 | 169.974 | 0.018359 | 18 | PSP-Business-Lighting_Industrial_General | 20.04
eDSM | Lighting - Industrial | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamps 8’ T12 and T8 | 4473 | 0.071 | 317.583 | 0.045 | 201.285 | 0.026 | 116.298 | 0.012562 | 18 | PSP-Business-Lighting_Industrial_General | 56.48
eDSM | Lighting - Industrial | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4473 | 0.07013 | 313.6915 | 0.044 | 196.812 | 0.02613 | 116.8795 | 0.012624 | 18 | PSP-Business-Lighting_Industrial_General | 145
eDSM | Lighting - Industrial | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4473 | 0.11712 | 523.8778 | 0.093 | 415.989 | 0.02412 | 107.8888 | 0.011653 | 18 | PSP-Business-Lighting_Industrial_General | 167
eDSM | Lighting - Industrial | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 4473 | 0.02475 | 110.7067 | 0.013 | 58.149 | 0.01175 | 52.5578 | 0.0056768 | 18 | PSP-Business-Lighting_Industrial_General | -2.06
eDSM | Lighting - Industrial | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 4473 | 0.03139 | 140.4075 | 0.018 | 80.514 | 0.01339 | 59.8935 | 0.0064692 | 18 | PSP-Business-Lighting_Industrial_General | 3.08
eDSM | Lighting - Industrial | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 4473 | 0.05996 | 268.2011 | 0.028 | 125.244 | 0.03196 | 142.9571 | 0.015441 | 18 | PSP-Business-Lighting_Industrial_General | 0.71
eDSM | Lighting - Industrial | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 4473 | 0.03182 | 142.3309 | 0.019 | 84.987 | 0.01282 | 57.3439 | 0.0061938 | 18 | PSP-Business-Lighting_Industrial_General | 5.16
eDSM | Lighting - Industrial | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4473 | 0.3 | 1341.9 | 0.3 | 819.23 | 0 | 522.67 | 0.056454 | 11 | PSP-Business-Lighting_Industrial_General | 218
eDSM | Lighting - Industrial | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4473 | 0.03 | 134.19 | 0.03 | 81.923 | 0 | 52.267 | 0.0056454 | 11 | PSP-Business-Lighting_Industrial_General | 356.95
eDSM | Lighting - Industrial | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4473 | 0.12 | 536.76 | 0.12 | 327.692 | 0 | 209.068 | 0.022582 | 11 | PSP-Business-Lighting_Industrial_General | 291.21
eDSM | Lighting - Industrial | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4473 | 0.15 | 670.95 | 0.15 | 479.7292 | 0 | 191.2207 | 0.020654 | 11 | PSP-Business-Lighting_Industrial_General | 120.48
2021-2024 | Lighting - Food Retail | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 6074 | 0.3 | 1822.2 | 0.3 | 1112.4531 | 0 | 709.7469 | 0.10082 | 5 | PSP-Business-Food_Retail-Lighting_Interior_General | 218
2021-2024 | Lighting - Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 6074 | 0.03 | 182.22 | 0.03 | 111.2453 | 0 | 70.9747 | 0.01008 | 5 | PSP-Business-Food_Retail-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 6074 | 0.12 | 728.88 | 0.12 | 444.9812 | 0 | 283.8988 | 0.04033 | 5 | PSP-Business-Food_Retail-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Food Retail | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 6074 | 0.15 | 911.1 | 0.15 | 651.4365 | 0 | 259.6635 | 0.03689 | 5 | PSP-Business-Food_Retail-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Hospital | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5182 | 0.3 | 1554.6 | 0.3 | 949.0833 | 0 | 605.5167 | 0.08083 | 6 | PSP-Business-Hospital-Lighting_Interior_General | 218
2021-2024 | Lighting - Hospital | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5182 | 0.03 | 155.46 | 0.03 | 94.9083 | 0 | 60.5517 | 0.00808 | 6 | PSP-Business-Hospital-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Hospital | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5182 | 0.12 | 621.84 | 0.12 | 379.6333 | 0 | 242.2067 | 0.03233 | 6 | PSP-Business-Hospital-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Hospital | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5182 | 0.15 | 777.3 | 0.15 | 555.7695 | 0 | 221.5305 | 0.02957 | 6 | PSP-Business-Hospital-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Large Hotel (Corridor/Lobby) | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 7884 | 0.3 | 2365.2 | 0.3 | 1443.9546 | 0 | 921.2454 | 0.11127 | 4 | PSP-Business-Large_Hotel-Lighting_Interior_General | 218
2021-2024 | Lighting - Large Hotel (Corridor/Lobby) | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 7884 | 0.03 | 236.52 | 0.03 | 144.3955 | 0 | 92.1245 | 0.01112 | 4 | PSP-Business-Large_Hotel-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Large Hotel (Corridor/Lobby) | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 7884 | 0.12 | 946.08 | 0.12 | 577.5818 | 0 | 368.4982 | 0.04451 | 4 | PSP-Business-Large_Hotel-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Large Hotel (Corridor/Lobby) | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 7884 | 0.15 | 1182.6 | 0.15 | 845.559 | 0 | 337.041 | 0.04071 | 4 | PSP-Business-Large_Hotel-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Large Non-Food Retail | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3121 | 0.3 | 936.3 | 0.3 | 571.6112 | 0 | 364.6888 | 0.053974 | 8 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 218
2021-2024 | Lighting - Large Non-Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3121 | 0.03 | 93.63 | 0.03 | 57.1611 | 0 | 36.4689 | 0.0053974 | 8 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Large Non-Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3121 | 0.12 | 374.52 | 0.12 | 228.6445 | 0 | 145.8755 | 0.02159 | 8 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Large Non-Food Retail | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3121 | 0.15 | 468.15 | 0.15 | 334.7273 | 0 | 133.4227 | 0.019747 | 8 | PSP-Business-Large_Non_Food_Retail-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Large Office | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3610 | 0.3 | 1083 | 0.3 | 661.1715 | 0 | 421.8285 | 0.07533 | 9 | PSP-Business-Large_Office-Lighting_Interior_General | 218
2021-2024 | Lighting - Large Office | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3610 | 0.03 | 108.3 | 0.03 | 66.1171 | 0 | 42.1829 | 0.00753 | 9 | PSP-Business-Large_Office-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Large Office | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3610 | 0.12 | 433.2 | 0.12 | 264.4686 | 0 | 168.7314 | 0.03013 | 9 | PSP-Business-Large_Office-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Large Office | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3610 | 0.15 | 541.5 | 0.15 | 387.1725 | 0 | 154.3275 | 0.02756 | 9 | PSP-Business-Large_Office-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Nursing Home | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4308 | 0.3 | 1292.4 | 0.3 | 789.0102 | 0 | 503.3898 | 0.07611 | 7 | PSP-Business-Nursing_Home-Lighting_Interior_General | 218
2021-2024 | Lighting - Nursing Home | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4308 | 0.03 | 129.24 | 0.03 | 78.901 | 0 | 50.339 | 0.00761 | 7 | PSP-Business-Nursing_Home-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Nursing Home | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4308 | 0.12 | 516.96 | 0.12 | 315.6041 | 0 | 201.3559 | 0.03045 | 7 | PSP-Business-Nursing_Home-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Nursing Home | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4308 | 0.15 | 646.2 | 0.15 | 462.033 | 0 | 184.167 | 0.02784 | 7 | PSP-Business-Nursing_Home-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Other Commercial Buildings | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4000 | 0.3 | 1200 | 0.3 | 732.6 | 0 | 467.4 | 0.07375 | 11 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 218
2021-2024 | Lighting - Other Commercial Buildings | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4000 | 0.03 | 120 | 0.03 | 73.26 | 0 | 46.74 | 0.00737 | 11 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Other Commercial Buildings | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4000 | 0.12 | 480 | 0.12 | 293.04 | 0 | 186.96 | 0.0295 | 11 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Other Commercial Buildings | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4000 | 0.15 | 600 | 0.15 | 429 | 0 | 171 | 0.02698 | 11 | PSP-Business-Other_Commercial_Buildings-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Other Non-Food Retail | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4089 | 0.3 | 1226.7 | 0.3 | 748.9004 | 0 | 477.7996 | 0.08811 | 8 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 218
2021-2024 | Lighting - Other Non-Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4089 | 0.03 | 122.67 | 0.03 | 74.89 | 0 | 47.78 | 0.00881 | 8 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Other Non-Food Retail | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4089 | 0.12 | 490.68 | 0.12 | 299.5601 | 0 | 191.1199 | 0.03524 | 8 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Other Non-Food Retail | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4089 | 0.15 | 613.35 | 0.15 | 438.5453 | 0 | 174.8048 | 0.03223 | 8 | PSP-Business-Other_Non_Food_Retail-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Restaurant | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5110 | 0.3 | 1533 | 0.3 | 935.8965 | 0 | 597.1035 | 0.09784 | 6 | PSP-Business-Restaurant-Lighting_Interior_General | 218
2021-2024 | Lighting - Restaurant | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5110 | 0.03 | 153.3 | 0.03 | 93.5897 | 0 | 59.7103 | 0.00978 | 6 | PSP-Business-Restaurant-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Restaurant | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5110 | 0.12 | 613.2 | 0.12 | 374.3586 | 0 | 238.8414 | 0.03914 | 6 | PSP-Business-Restaurant-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Restaurant | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 5110 | 0.15 | 766.5 | 0.15 | 548.0475 | 0 | 218.4525 | 0.0358 | 6 | PSP-Business-Restaurant-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Schools | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 2596 | 0.3 | 778.8 | 0.3 | 475.4574 | 0 | 303.3426 | 0.01526 | 12 | PSP-Business-Schools-Lighting_Interior_General | 218
2021-2024 | Lighting - Schools | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 2596 | 0.03 | 77.88 | 0.03 | 47.5457 | 0 | 30.3343 | 0.00153 | 12 | PSP-Business-Schools-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Schools | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 2596 | 0.12 | 311.52 | 0.12 | 190.183 | 0 | 121.337 | 0.0061 | 12 | PSP-Business-Schools-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Schools | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 2596 | 0.15 | 389.4 | 0.15 | 278.421 | 0 | 110.979 | 0.00558 | 12 | PSP-Business-Schools-Lighting_Interior_General | 120.48
2021-2024 | Lighting - University Colleges | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3255 | 0.3 | 976.5 | 0.3 | 596.1532 | 0 | 380.3467 | 0.05011 | 10 | PSP-Business-University_Colleges-Lighting_Interior_General | 218
2021-2024 | Lighting - University Colleges | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3255 | 0.03 | 97.65 | 0.03 | 67.3157 | 0 | 30.3343 | 0.00399 | 10 | PSP-Business-University_Colleges-Lighting_Interior_General | 356.95
2021-2024 | Lighting - University Colleges | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3255 | 0.12 | 390.6 | 0.12 | 238.4613 | 0 | 152.1387 | 0.02004 | 10 | PSP-Business-University_Colleges-Lighting_Interior_General | 291.21
2021-2024 | Lighting - University Colleges | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 3255 | 0.15 | 488.25 | 0.15 | 349.0987 | 0 | 139.1513 | 0.01833 | 10 | PSP-Business-University_Colleges-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Warehouse Wholesale | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4408 | 0.3 | 1322.4 | 0.3 | 807.3252 | 0 | 515.0748 | 0.10123 | 9 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 218
2021-2024 | Lighting - Warehouse Wholesale | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4408 | 0.03 | 132.24 | 0.03 | 96.6685 | 0 | 35.5715 | 0.006989 | 9 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 356.95
2021-2024 | Lighting - Warehouse Wholesale | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4408 | 0.12 | 528.96 | 0.12 | 322.9301 | 0 | 206.0299 | 0.040493 | 9 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 291.21
2021-2024 | Lighting - Warehouse Wholesale | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4408 | 0.15 | 661.2 | 0.15 | 472.758 | 0 | 188.442 | 0.03159 | 9 | PSP-Business-Warehouse_Wholesale-Lighting_Interior_General | 120.48
2021-2024 | Lighting - Industrial | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 16W >= 600 Lumens | 38W - 43W Halogen or Incandescent Lamp | 4473 | 0.0405 | 181.1565 | 0.011 | 49.203 | 0.0295 | 131.9535 | 0.019717 | 9 | PSP-Business-Lighting_Industrial_General | -27.42
2021-2024 | Lighting - Industrial | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 30W >= 1100 Lumens | 60W - 80W Halogen or Incandescent Lamp | 4473 | 0.07 | 313.11 | 0.0175 | 78.2775 | 0.0525 | 234.8325 | 0.035089 | 9 | PSP-Business-Lighting_Industrial_General | -138.68
2021-2024 | Lighting - Industrial | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 7W >= 250 Lumens | 20W - 35W Halogen or Incandescent Lamp | 4473 | 0.0275 | 123.0075 | 0.006 | 26.838 | 0.0215 | 96.1695 | 0.01437 | 9 | PSP-Business-Lighting_Industrial_General | -94.29
2021-2024 | Lighting - Industrial | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 14W >= 400 Lumens | 35W - 38W Halogen or Incandescent Lamp | 4473 | 0.0365 | 163.2645 | 0.0075 | 33.5475 | 0.029 | 129.717 | 0.019383 | 9 | PSP-Business-Lighting_Industrial_General | -55.06
2021-2024 | Lighting - Industrial | LED REFLECTOR (FLOOD/SPOT) LAMP PIN & SCREW BASE | <= 20W >= 800 Lumens | 43W - 60W Halogen or Incandescent Lamp | 4473 | 0.0515 | 230.3595 | 0.013 | 58.149 | 0.0385 | 172.2105 | 0.025732 | 9 | PSP-Business-Lighting_Industrial_General | -37.86
2021-2024 | Lighting - Industrial | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 800 Lumens | ENERGY STAR® 26W CFL | 4473 | 0.026 | 116.298 | 0.0153 | 68.4369 | 0.0107 | 47.8611 | 0.0071515 | 15 | PSP-Business-Lighting_Industrial_General | 55.82
2021-2024 | Lighting - Industrial | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 600 and < 800 Lumens | ENERGY STAR® 22W CFL | 4473 | 0.022 | 98.406 | 0.012 | 53.676 | 0.01 | 44.73 | 0.0066836 | 15 | PSP-Business-Lighting_Industrial_General | 55.36
2021-2024 | Lighting - Industrial | LED RECESSED DOWNLIGHTS | LED Downlight with Light Output >= 400 and < 600 Lumens | ENERGY STAR® 15W or 18W CFL | 4473 | 0.0165 | 73.8045 | 0.0094 | 42.0462 | 0.0071 | 31.7583 | 0.0047454 | 15 | PSP-Business-Lighting_Industrial_General | 15.71
2021-2024 | Lighting - Industrial | LED LOW-BAY FIXTURES | <=100W <=10000 Lumens | Measure mix of 4-lamp Tandem T12, T8 and T5 Strip Fixture | 4473 | 0.11477 | 513.3662 | 0.053 | 237.069 | 0.06177 | 276.2972 | 0.041285 | 18 | PSP-Business-Lighting_Industrial_General | 184
2021-2024 | Lighting - Industrial | LED HIGH BAY FIXTURE | >= 34700 Lumens & >= 305W | Average 1000 watt HID lamp/ T8 HO | 4473 | 0.901 | 4030.173 | 0.345 | 1543.185 | 0.556 | 2486.988 | 0.37161 | 20 | PSP-Business-Lighting_Industrial_General | -135.51
2021-2024 | Lighting - Industrial | LED HIGH BAY FIXTURE | >= 10000 Lumens & < 105W | Average 250 watt HID lamp/ T8 HO | 4473 | 0.236 | 1055.628 | 0.0857 | 383.3361 | 0.1503 | 672.2919 | 0.10046 | 20 | PSP-Business-Lighting_Industrial_General | -449.44
2021-2024 | Lighting - Industrial | LED HIGH BAY FIXTURE | >= 12200 Lumens & < 132W | Average 320 watt HID lamp/ T8 HO | 4473 | 0.289 | 1292.697 | 0.1019 | 455.7987 | 0.1871 | 836.8983 | 0.12505 | 20 | PSP-Business-Lighting_Industrial_General | -449.44
2021-2024 | Lighting - Industrial | LED HIGH BAY FIXTURE | >= 15500 Lumens & < 178W | Average 400 watt HID lamp/ T8 HO | 4473 | 0.367 | 1641.591 | 0.139 | 621.747 | 0.228 | 1019.844 | 0.15239 | 20 | PSP-Business-Lighting_Industrial_General | -135.51
2021-2024 | Lighting - Industrial | LED HIGH BAY FIXTURE | >= 20100 Lumens & < 305W | Average 750 watt HID lamp/ T8 HO | 4473 | 0.634 | 2835.882 | 0.194 | 867.762 | 0.44 | 1968.12 | 0.29408 | 20 | PSP-Business-Lighting_Industrial_General | -135.51
2021-2024 | Lighting - Industrial | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 1' x 4' LED troffer / 4' LED linear ambient retrofit kit (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4473 | 0.06437 | 287.927 | 0.031 | 138.663 | 0.03337 | 149.264 | 0.022303 | 18 | PSP-Business-Lighting_Industrial_General | 83.95
2021-2024 | Lighting - Industrial | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 4' LED troffer / 4' linear ambient retrofit kit (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4473 | 0.09191 | 411.1134 | 0.042 | 187.866 | 0.04991 | 223.2474 | 0.033358 | 18 | PSP-Business-Lighting_Industrial_General | 104.06
2021-2024 | Lighting - Industrial | INTEGRAL LED TROFFER & LINEAR AMBIENT RETROFIT KITS | 2' x 2' LED troffer / 2' linear ambient retrofit kit (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4473 | 0.06617 | 295.9784 | 0.032 | 143.136 | 0.03417 | 152.8424 | 0.022838 | 18 | PSP-Business-Lighting_Industrial_General | 38.87
2021-2024 | Lighting - Industrial | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 1' x 4' LED troffer / 4' LED linear ambient fixture (>= 1500 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 2 lamps | 4473 | 0.06438 | 287.9717 | 0.0386 | 172.6578 | 0.02578 | 115.3139 | 0.01723 | 18 | PSP-Business-Lighting_Industrial_General | 114.37
2021-2024 | Lighting - Industrial | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 2' LED troffer / 2' LED linear ambient fixture (>= 2000 Lumens) | Measure Mix of T12U-bend 34W and T8U-bend 32W - 2 lamps | 4473 | 0.06618 | 296.0231 | 0.039 | 174.447 | 0.02718 | 121.5761 | 0.018166 | 18 | PSP-Business-Lighting_Industrial_General | 61.99
2021-2024 | Lighting - Industrial | INTEGRAL LED TROFFER & LED LINEAR AMBIENT FIXTURE | 2' x 4' LED troffer / 4' LED linear ambient fixture (>= 3000 Lumens) | Measure Mix of 4' T12 40W and T8 32W - 3 lamps | 4473 | 0.09193 | 411.2029 | 0.044 | 196.812 | 0.04793 | 214.3909 | 0.032035 | 18 | PSP-Business-Lighting_Industrial_General | 116.78
2021-2024 | Lighting - Industrial | 8' T8 LED LAMP | <= 43W >= 3200 Lumens | Measure Mix of 8' T12 75W and T8 59W w/ electronic ballast | 4473 | 0.06915 | 309.308 | 0.0377 | 168.6321 | 0.03145 | 140.6759 | 0.02102 | 18 | PSP-Business-Lighting_Industrial_General | -4.18
2021-2024 | Lighting - Industrial | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 9000 Lumens | Mixture of two lamps 8’ T12 and T8 | 4473 | 0.122 | 545.706 | 0.084 | 375.732 | 0.038 | 169.974 | 0.025398 | 18 | PSP-Business-Lighting_Industrial_General | 20.04
2021-2024 | Lighting - Industrial | 8' LED LINEAR AMBIENT RETROFIT KIT | >= 4500 < 9000 Lumens | Mixture of one lamps 8’ T12 and T8 | 4473 | 0.071 | 317.583 | 0.045 | 201.285 | 0.026 | 116.298 | 0.017377 | 18 | PSP-Business-Lighting_Industrial_General | 56.48
2021-2024 | Lighting - Industrial | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 4500 <9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4473 | 0.07013 | 313.6915 | 0.044 | 196.812 | 0.02613 | 116.8795 | 0.017464 | 18 | PSP-Business-Lighting_Industrial_General | 145
2021-2024 | Lighting - Industrial | 8' LED LINEAR AMBIENT FIXTURES | 8' LED linear ambient fixture (>= 9000 Lumens) | Measure mix of T8 (Electronic Ballast) and T12 (8' ES Magnetic Ballast & 8' Magnetic Ballast) | 4473 | 0.11712 | 523.8778 | 0.093 | 415.989 | 0.02412 | 107.8888 | 0.016121 | 18 | PSP-Business-Lighting_Industrial_General | 167
2021-2024 | Lighting - Industrial | 4' T8 LED / LED U-BEND LAMP | <=15W >= 1500 Lumens | Measure Mix of 4' T12 34W, T8 25W fluorescent lamp and T8 LED | 4473 | 0.02475 | 110.7067 | 0.013 | 58.149 | 0.01175 | 52.5578 | 0.0078533 | 18 | PSP-Business-Lighting_Industrial_General | -2.06
2021-2024 | Lighting - Industrial | 4' T8 LED / LED U-BEND LAMP | <= 22W >= 2100 Lumens | Measure Mix of 4' T12 40W, T8 32W fluorescent lamp and T8 LED | 4473 | 0.03139 | 140.4075 | 0.018 | 80.514 | 0.01339 | 59.8935 | 0.0089494 | 18 | PSP-Business-Lighting_Industrial_General | 3.08
2021-2024 | Lighting - Industrial | 4' T5HO LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <= 32W >= 3200 Lumens | Measure Mix of 4' T5HO fluorescent lamp 54W and T5HO LED | 4473 | 0.05996 | 268.2011 | 0.028 | 125.244 | 0.03196 | 142.9571 | 0.021361 | 18 | PSP-Business-Lighting_Industrial_General | 0.71
2021-2024 | Lighting - Industrial | 4' T5 LED TUBE REPLACEMENT (UL TYPE A, B, & C) | <=28W >= 1600 Lumens | Measure Mix of 4' T5 fluorescent lamp 28W and T5 LED | 4473 | 0.03182 | 142.3309 | 0.019 | 84.987 | 0.01282 | 57.3439 | 0.0085684 | 18 | PSP-Business-Lighting_Industrial_General | 5.16
2021-2024 | Lighting - Industrial | OCCUPANCY SENSORS | Ceiling/Wall Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4473 | 0.3 | 1341.9 | 0.3 | 819.23 | 0 | 522.67 | 0.078098 | 11 | PSP-Business-Lighting_Industrial_General | 218
2021-2024 | Lighting - Industrial | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (all other) for fixtures < 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4473 | 0.03 | 134.19 | 0.03 | 81.923 | 0 | 52.267 | 0.0078098 | 11 | PSP-Business-Lighting_Industrial_General | 356.95
2021-2024 | Lighting - Industrial | OCCUPANCY SENSORS | Fixture Mounted Occupancy Sensor (High Bay) for fixtures >= 100W | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4473 | 0.12 | 536.76 | 0.12 | 327.692 | 0 | 209.068 | 0.031239 | 11 | PSP-Business-Lighting_Industrial_General | 291.21
2021-2024 | Lighting - Industrial | OCCUPANCY SENSORS | Switch Plate Mounted | Measure Mix of 95% No Occupancy Sensor and 5% Replacing Existing Occupancy Sensor or Other Type of Control | 4473 | 0.15 | 670.95 | 0.15 | 479.7292 | 0 | 191.2207 | 0.028573 | 11 | PSP-Business-Lighting_Industrial_General | 120.48