## Summer Planning Forecast
The IRRP planning forecast accounts for the median weather gross forecast provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Transformer Station | Net Extreme Weather Station Peak Demand Forecast, Coincident to Niagara Region (MW)
| 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Allanburg TS | 45.1107 | 45.2889 | 45.3621 | 45.4782 | 45.6788 | 45.799 | 45.9722 | 46.078 | 46.2325 | 46.3584 | 46.4797 | 46.6936 | 46.9468 | 47.2376 | 47.6114 | 48.0695 | 48.5559 | 49.0461 | 49.5288 | 50.0508
Beamsville TS | 68.9469 | 68.8409 | 68.8916 | 69.0035 | 69.5476 | 69.9489 | 70.4514 | 65.6623 | 71.491 | 72.0333 | 72.5618 | 73.224 | 73.9523 | 74.7546 | 75.6427 | 76.6614 | 77.7235 | 78.8056 | 79.8941 | 81.0602
Bunting TS | 56.8232 | 57.2383 | 57.2418 | 57.3 | 57.7396 | 58.1475 | 58.725 | 59.3533 | 60.123 | 60.8721 | 61.6539 | 62.6011 | 63.6758 | 64.8924 | 66.2183 | 67.6135 | 69.0222 | 70.4466 | 71.8874 | 71.9578
Carlton TS | 86.3709 | 86.8958 | 87.7079 | 88.6987 | 89.7998 | 90.8266 | 92.081 | 93.349 | 94.7588 | 96.2778 | 97.7006 | 99.2802 | 100.9712 | 102.8262 | 102.682 | 102.6795 | 102.698 | 102.7247 | 102.7436 | 102.8455
Crowland TS | 94.0343 | 95.3017 | 96.9152 | 98.6628 | 100.5361 | 101.9925 | 103.6567 | 105.2921 | 107.1228 | 108.7456 | 108.7058 | 108.9512 | 109.2732 | 109.6729 | 110.1814 | 110.9945 | 111.8835 | 112.7867 | 113.6745 | 114.7115
Dunnville TS | 31.8947 | 32.151 | 32.2358 | 32.3316 | 32.4774 | 32.5977 | 32.7076 | 32.7378 | 32.7831 | 32.8382 | 32.9057 | 33.0229 | 33.1716 | 33.3453 | 33.625 | 33.9299 | 34.2477 | 34.556 | 34.8459 | 35.1353
Glendale TS (T1/T2) | 32.4307 | 32.6566 | 32.6585 | 32.6901 | 32.9294 | 33.1513 | 33.4655 | 33.8074 | 34.2262 | 34.6337 | 35.0591 | 35.5745 | 36.1592 | 36.8212 | 37.5426 | 38.3017 | 39.0682 | 39.8432 | 40.6271 | 40.6655
Glendale TS (T3/T4) | 6.1537 | 6.3366 | 6.4048 | 6.4822 | 6.6372 | 6.7983 | 6.9878 | 7.1947 | 7.4297 | 7.657 | 7.8957 | 8.1611 | 8.4491 | 8.7611 | 9.0944 | 9.4344 | 9.7762 | 10.1213 | 10.4709 | 10.4808
Kalar MTS | 45.8482 | 46.2496 | 46.7766 | 53.5094 | 59.8617 | 63.5803 | 64.9167 | 66.2354 | 67.6537 | 67.8891 | 68.1024 | 68.4528 | 68.8691 | 69.3613 | 69.9311 | 70.6284 | 71.3601 | 72.1038 | 72.8453 | 73.6575
Murray TS (T11/T12) | 73.0302 | 72.6478 | 72.6143 | 72.7098 | 72.9442 | 72.881 | 73.0459 | 73.251 | 73.6108 | 73.826 | 73.9746 | 74.3284 | 74.7347 | 75.2078 | 75.6821 | 76.396 | 77.1648 | 77.96 | 78.7641 | 79.7068
Murray TS (T13/T14) | 22.8145 | 22.6941 | 22.6839 | 22.7141 | 22.7878 | 22.7681 | 22.82 | 22.8848 | 22.998 | 23.0659 | 23.1128 | 23.2239 | 23.3515 | 23.4999 | 23.6483 | 23.8719 | 24.1128 | 24.3619 | 24.6138 | 24.9093
Niagara West MTS | 39.1234 | 38.9998 | 38.9668 | 38.9713 | 39.4088 | 39.7633 | 40.1707 | 40.5521 | 40.9905 | 41.426 | 41.8622 | 42.3849 | 42.9555 | 43.5767 | 44.2784 | 45.061 | 45.8762 | 46.7057 | 47.5399 | 48.4209
NOTL DS | 33.1101 | 34.2988 | 35.6059 | 36.967 | 37.352 | 37.633 | 37.9889 | 38.3586 | 38.7938 | 39.1787 | 39.5512 | 40.0037 | 40.4795 | 40.9799 | 41.5054 | 42.125 | 42.7747 | 43.4392 | 44.1109 | 44.8375
NOTL York MTS | 16.9017 | 17.0113 | 17.1731 | 17.3576 | 18.0765 | 18.7546 | 19.4645 | 19.6726 | 19.911 | 20.1313 | 20.3489 | 20.6041 | 20.8725 | 21.1541 | 21.4559 | 21.7993 | 22.1576 | 22.5227 | 22.8909 | 23.2829
Port Colborne TS | 36.6191 | 36.4788 | 36.2914 | 36.2382 | 36.2124 | 36.1285 | 35.9475 | 35.82 | 35.7348 | 35.6602 | 35.603 | 35.6014 | 35.634 | 35.5977 | 35.7606 | 35.9558 | 36.1665 | 36.3715 | 36.5622 | 36.7572
Stanley TS | 62.7914 | 62.6543 | 62.7163 | 62.8563 | 63.0876 | 63.1427 | 63.3108 | 63.4621 | 63.7134 | 63.9123 | 64.0911 | 64.4081 | 64.7797 | 65.2101 | 65.7153 | 66.3583 | 67.0401 | 67.7336 | 68.4244 | 69.1876
Thorold TS | 25.292 | 25.3218 | 25.2775 | 25.2581 | 25.2836 | 25.2665 | 25.2738 | 25.2499 | 25.2528 | 25.2385 | 25.2243 | 25.2597 | 25.315 | 25.3874 | 25.51 | 25.6759 | 25.8564 | 26.0369 | 26.211 | 26.4026
Vansickle TS | 53.57 | 53.4848 | 53.5128 | 53.8062 | 54.2629 | 54.6923 | 55.2881 | 55.9298 | 56.5788 | 57.2999 | 58.0427 | 58.9336 | 59.9311 | 61.0632 | 62.2158 | 63.4482 | 64.7015 | 65.9789 | 65.9905 | 66.0527
Vineland DS | 21.0801 | 21.1456 | 21.242 | 21.3503 | 21.4808 | 21.5829 | 22.4738 | 23.3554 | 24.2559 | 24.3992 | 24.5402 | 24.712 | 24.9011 | 25.1096 | 25.3418 | 25.6003 | 25.8671 | 26.1369 | 26.4065 | 26.6908
CNPI Station #17 MTS | 26.4609 | 26.4079 | 26.2981 | 26.2124 | 26.149 | 26.1406 | 26.0393 | 25.9081 | 25.909 | 25.8133 | 25.728 | 25.6855 | 25.7636 | 25.7645 | 25.8334 | 26.0262 | 26.1345 | 26.3357 | 26.4311 | 26.5327
CNPI Station #18 MTS | 36.1099 | 35.8663 | 35.7881 | 35.7401 | 35.7199 | 35.538 | 35.4659 | 35.3494 | 35.2756 | 35.1101 | 35.0588 | 35.0631 | 35.1 | 35.1635 | 35.2268 | 35.4208 | 35.6304 | 35.8348 | 36.0259 | 36.2232
Total Region (excluding tx-connected industrial customers) | 914.5166 | 917.9705 | 922.3643 | 934.3381 | 947.9731 | 957.1335 | 966.2529 | 969.5038 | 984.8453 | 992.3666 | 998.2027 | 1006.1695 | 1015.2864 | 1025.3868 | 1034.7027 | 1046.0517 | 1057.818 | 1069.852 | 1080.4891 | 1089.5689
This document and the information contained herein is provided for informational purposes only. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## DG
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | Total Contracted Distributed Generation (DG) Contribution to Peak (MW)
| 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Allanburg TS | 0.4691 | 0.4691 | 0.4691 | 0.4691 | 0.4691 | 0.4691 | 0.4691 | 0.4691 | 0.4691 | 0.43916 | 0.40857 | 0.26718 | 0.090208 | 0.07008 | 0.037098 | 0.019016 | 0 | 0 | 0 | 0
Beamsville TS | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0941 | 1.0468 | 0.98049 | 0.82964 | 0.57544 | 0.54217 | 0.52314 | 0.51099 | 0 | 0 | 0 | 0
Bunting TS | 3.0517 | 3.0517 | 3.0517 | 3.0517 | 3.0517 | 3.0517 | 0.27274 | 0.27274 | 0.27274 | 0.26658 | 0.25631 | 0.2035 | 0.11675 | 0.099502 | 0.079682 | 0.038239 | 0 | 0 | 0 | 0
Carlton TS | 5.6844 | 5.6844 | 5.6844 | 5.6844 | 5.6844 | 5.6844 | 5.6844 | 0.68235 | 0.68235 | 0.6642 | 0.56559 | 0.41905 | 0.22174 | 0.1415 | 0.11387 | 0.052085 | 0 | 0 | 0 | 0
Crowland TS | 6.4611 | 6.4611 | 6.4611 | 6.4611 | 6.4611 | 6.4611 | 6.4611 | 6.4611 | 6.4611 | 6.4473 | 6.3327 | 6.0804 | 0.62704 | 0.56795 | 0.52369 | 0.46154 | 0 | 0 | 0 | 0
Dunnville TS | 5.0401 | 5.0401 | 5.0401 | 5.0401 | 5.0401 | 5.0401 | 3.5353 | 3.4441 | 3.4441 | 3.4127 | 3.3158 | 3.3126 | 3.3126 | 0.13713 | 0.032901 | 0.026728 | 0 | 0 | 0 | 0
Glendale TS (T1/T2) | 0.23811 | 0.23811 | 0.23811 | 0.23811 | 0.23811 | 0.23811 | 0.23811 | 0.23811 | 0.23811 | 0.23547 | 0.23547 | 0.13838 | 0.048164 | 0.044832 | 0.035047 | 0.021861 | 0 | 0 | 0 | 0
Glendale TS (T3/T4) | 0.029877 | 0.029877 | 0.029877 | 0.029877 | 0.029877 | 0.029877 | 0.029877 | 0.029877 | 0.029877 | 0.029877 | 0.029877 | 0.024116 | 0.024116 | 0.010237 | 0.0067665 | 0.0050315 | 0 | 0 | 0 | 0
Kalar MTS | 0.86103 | 0.86103 | 0.86103 | 0.86103 | 0.86103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Murray TS (T11/T12) | 0.14465 | 0.14465 | 0.14465 | 0.14465 | 0.14465 | 0.14465 | 0.14465 | 0.14465 | 0.14465 | 0.13336 | 0.11306 | 0.067035 | 0.033983 | 0.010063 | 0.0052744 | 0.0052744 | 0 | 0 | 0 | 0
Murray TS (T13/T14) | 0.042566 | 0.042566 | 0.042566 | 0.042566 | 0.042566 | 0.042566 | 0.042566 | 0.042566 | 0.042566 | 0.042566 | 0.042566 | 0.039096 | 0.0096015 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Niagara West MTS | 4.9024 | 4.9024 | 4.9024 | 4.9024 | 4.9024 | 4.9024 | 4.9024 | 4.9024 | 4.9024 | 4.7468 | 4.7121 | 4.7121 | 2.2721 | 2.2721 | 2.1853 | 0.09716 | 0 | 0 | 0 | 0
NOTL DS | 0.79554 | 0.79554 | 0.79554 | 0.79554 | 0.79554 | 0.79554 | 0.79554 | 0.79554 | 0.47722 | 0.3345 | 0.27113 | 0.20754 | 0.1634 | 0.14952 | 0.13339 | 0.12867 | 0 | 0 | 0 | 0
NOTL York MTS | 1.7303 | 1.7303 | 1.7303 | 1.7303 | 1.7303 | 1.7303 | 1.7303 | 0.34084 | 0.34084 | 0.3284 | 0.25108 | 0.15204 | 0.14309 | 0.13276 | 0.12235 | 0.12235 | 0 | 0 | 0 | 0
Port Colborne TS | 0.52053 | 0.52053 | 0.52053 | 0.52053 | 0.52053 | 0.52053 | 0.52053 | 0.52053 | 0.52053 | 0.52053 | 0.50679 | 0.45474 | 0.09598 | 0.069608 | 0.045318 | 0.031508 | 0 | 0 | 0 | 0
Stanley TS | 0.24681 | 0.24681 | 0.24681 | 0.24681 | 0.24681 | 0.24681 | 0.24681 | 0.24681 | 0.24681 | 0.24241 | 0.21656 | 0.19912 | 0.18179 | 0.061893 | 0.049885 | 0.041987 | 0 | 0 | 0 | 0
Thorold TS | 0.080773 | 0.080773 | 0.080773 | 0.080773 | 0.080773 | 0.080773 | 0.080773 | 0.080773 | 0.080773 | 0.076456 | 0.065113 | 0.049218 | 0.036796 | 0.022916 | 0.019515 | 0.013047 | 0 | 0 | 0 | 0
Vansickle TS | 0.36799 | 0.36799 | 0.36799 | 0.36799 | 0.36799 | 0.36799 | 0.36799 | 0.36799 | 0.36799 | 0.36694 | 0.35485 | 0.3095 | 0.11969 | 0.089665 | 0.070372 | 0.033225 | 0 | 0 | 0 | 0
Vineland DS | 0.58701 | 0.58701 | 0.58701 | 0.58701 | 0.58701 | 0.58701 | 0.58701 | 0.58701 | 0.35701 | 0.29817 | 0.25522 | 0.064396 | 0.051089 | 0.037764 | 0.021561 | 0.012733 | 0 | 0 | 0 | 0
CNPI Station #17 MTS | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0.033312 | 0 | 0 | 0 | 0
CNPI Station #18 MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Region (with contract expiry) | 32.3814 | 32.3814 | 32.3814 | 32.3814 | 32.3814 | 31.5204 | 27.2367 | 20.7539 | 20.2056 | 19.6655 | 18.9467 | 17.5629 | 8.1568 | 4.493 | 4.0385 | 1.6548 | 0 | 0 | 0 | 0
DRAFT

## CDM
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The analyses were conducted under normal weather conditions and can be adjusted to reflect extreme weather conditions. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | Total Conservation and Demand Management (CDM) Forecast (MW)
| 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Allanburg TS | 0.39686 | 0.90684 | 1.2992 | 1.6445 | 1.943 | 2.357 | 2.7209 | 3.1136 | 3.4426 | 3.7999 | 4.1632 | 4.4412 | 4.6842 | 4.8938 | 5.0274 | 5.0838 | 5.1178 | 5.1524 | 5.1981 | 5.2111
Beamsville TS | 0.51799 | 1.1765 | 1.6884 | 2.1476 | 2.5414 | 3.0835 | 3.5442 | 8.9915 | 4.4732 | 4.9378 | 5.43 | 5.8114 | 6.1458 | 6.4259 | 6.6412 | 6.7495 | 6.8332 | 6.9146 | 7.0068 | 7.0431
Bunting TS | 0.43209 | 0.99493 | 1.4646 | 1.9139 | 2.2747 | 2.7454 | 3.1401 | 3.5886 | 4.0089 | 4.4202 | 4.8746 | 5.2408 | 5.555 | 5.7958 | 6.003 | 6.1252 | 6.2344 | 6.3387 | 6.4493 | 6.3831
Carlton TS | 0.66478 | 1.5288 | 2.2701 | 2.995 | 3.575 | 4.3319 | 4.9722 | 5.698 | 6.3773 | 7.0541 | 7.7925 | 8.3831 | 8.8833 | 9.2607 | 9.3962 | 9.3985 | 9.3812 | 9.3561 | 9.3383 | 9.2425
Crowland TS | 1.0653 | 2.4582 | 3.4946 | 4.4036 | 5.1981 | 6.3895 | 7.3848 | 8.404 | 9.2366 | 10.2641 | 11.2138 | 11.8954 | 12.5047 | 13.0408 | 13.4744 | 13.6216 | 13.6975 | 13.7601 | 13.8373 | 13.7743
Dunnville TS | 0.2517 | 0.57702 | 0.85728 | 1.1143 | 1.3477 | 1.6351 | 1.925 | 2.2664 | 2.5704 | 2.8599 | 3.1327 | 3.3537 | 3.5403 | 3.6984 | 3.7521 | 3.7772 | 3.7873 | 3.8033 | 3.8337 | 3.8615
Glendale TS (T1/T2) | 0.2351 | 0.54134 | 0.79689 | 1.0414 | 1.2377 | 1.4938 | 1.7085 | 1.9526 | 2.1813 | 2.405 | 2.6523 | 2.8515 | 3.0225 | 3.1535 | 3.2663 | 3.3327 | 3.3921 | 3.4489 | 3.5091 | 3.4731
Glendale TS (T3/T4) | 0.044493 | 0.10475 | 0.15585 | 0.20591 | 0.24875 | 0.30542 | 0.35568 | 0.41426 | 0.47203 | 0.53005 | 0.59543 | 0.65207 | 0.70397 | 0.74791 | 0.78867 | 0.81827 | 0.84611 | 0.87332 | 0.90152 | 0.89227
Kalar MTS | 0.39207 | 0.90174 | 1.3111 | 1.9057 | 2.4965 | 3.1939 | 3.714 | 4.2864 | 4.8014 | 5.2726 | 5.7716 | 6.1487 | 6.4708 | 6.7288 | 6.9212 | 7.0008 | 7.0555 | 7.1065 | 7.1668 | 7.1685
Murray TS (T11/T12) | 0.83269 | 1.8891 | 2.622 | 3.2405 | 3.7359 | 4.5184 | 5.0938 | 5.6384 | 6.0447 | 6.5943 | 7.214 | 7.6483 | 8.0409 | 8.3785 | 8.7228 | 8.8496 | 8.9328 | 8.9993 | 9.0655 | 9.0097
Murray TS (T13/T14) | 0.26063 | 0.59127 | 0.8205 | 1.0139 | 1.1687 | 1.4135 | 1.5933 | 1.7633 | 1.8899 | 2.0617 | 2.2554 | 2.3912 | 2.5139 | 2.6195 | 2.7274 | 2.7672 | 2.7933 | 2.8142 | 2.8349 | 2.8174
Niagara West MTS | 0.32756 | 0.74329 | 1.0734 | 1.3705 | 1.6353 | 1.9902 | 2.3072 | 2.6605 | 2.9723 | 3.2994 | 3.6386 | 3.9097 | 4.1489 | 4.3541 | 4.4974 | 4.5787 | 4.6437 | 4.7097 | 4.7863 | 4.834
NOTL DS | 0.27135 | 0.63693 | 0.91342 | 1.1618 | 1.3505 | 1.6451 | 1.8778 | 2.1059 | 2.2813 | 2.5125 | 2.7644 | 2.9501 | 3.1231 | 3.2823 | 3.4272 | 3.4934 | 3.541 | 3.5846 | 3.6313 | 3.6366
NOTL York MTS | 0.12753 | 0.29065 | 0.40874 | 0.50956 | 0.61215 | 0.7648 | 0.89944 | 1.0177 | 1.1121 | 1.2285 | 1.3521 | 1.4454 | 1.5313 | 1.6098 | 1.6745 | 1.7052 | 1.7274 | 1.7485 | 1.7721 | 1.779
Port Colborne TS | 0.26182 | 0.59363 | 0.86976 | 1.1198 | 1.344 | 1.6229 | 1.893 | 2.2129 | 2.4929 | 2.763 | 3.0168 | 3.2183 | 3.3876 | 3.5218 | 3.5686 | 3.5852 | 3.5871 | 3.5945 | 3.6152 | 3.632
Stanley TS | 0.57131 | 1.2984 | 1.8446 | 2.3233 | 2.7224 | 3.2933 | 3.7641 | 4.2571 | 4.6624 | 5.1234 | 5.6098 | 5.9727 | 6.2911 | 6.5607 | 6.7668 | 6.8503 | 6.9042 | 6.954 | 7.0133 | 7.0117
Thorold TS | 0.22267 | 0.50729 | 0.72342 | 0.91032 | 1.0734 | 1.2996 | 1.5005 | 1.7177 | 1.8969 | 2.0915 | 2.2853 | 2.432 | 2.5595 | 2.6704 | 2.7336 | 2.7559 | 2.7651 | 2.7752 | 2.7921 | 2.7933
Vansickle TS | 0.38815 | 0.88622 | 1.3052 | 1.7132 | 2.0385 | 2.4632 | 2.8213 | 3.2287 | 3.6041 | 3.9771 | 4.3889 | 4.7217 | 5.0072 | 5.2272 | 5.4104 | 5.5184 | 5.6154 | 5.7089 | 5.698 | 5.6396
Vineland DS | 0.11213 | 0.25566 | 0.37225 | 0.47966 | 0.56833 | 0.68584 | 0.81409 | 0.96068 | 1.0993 | 1.2095 | 1.3242 | 1.4126 | 1.4871 | 1.5459 | 1.585 | 1.6019 | 1.6137 | 1.6253 | 1.6396 | 1.6429
CNPI Station #17 MTS | 0.19653 | 0.44636 | 0.64958 | 0.83004 | 0.98971 | 1.1976 | 1.3928 | 1.6161 | 1.8152 | 2.0052 | 2.1853 | 2.3253 | 2.4519 | 2.5511 | 2.5863 | 2.6051 | 2.6033 | 2.6142 | 2.6245 | 2.629
CNPI Station #18 MTS | 0.26094 | 0.58983 | 0.86337 | 1.1085 | 1.3274 | 1.5984 | 1.8662 | 2.1756 | 2.4451 | 2.7006 | 2.9488 | 3.1448 | 3.3101 | 3.4504 | 3.4909 | 3.5086 | 3.5116 | 3.5194 | 3.5398 | 3.5544
Total Region | 7.8337 | 17.9189 | 25.8042 | 33.153 | 39.4291 | 48.0284 | 55.289 | 68.0699 | 69.8798 | 77.1103 | 84.6099 | 90.3501 | 95.3631 | 99.5173 | 102.4614 | 103.7273 | 104.5839 | 105.4015 | 106.2536 | 106.029
DRAFT