## _Cover
Dunsky Energy + Climate Advisors
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents
Date: November 10, 2021

## _Contents
Table of Contents
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Cover Sheet
Section and Sheet Titles
0.0.01 Definitions
1 Summary
1.0.01 Residential BTM Measures
1.0.02 Non-Residential BTM Measures
1.0.03 FTM Measures
1.0.04 Master Measure List
2 Measure List & Assessment
2.0.01 Measure Assessment
3 Measure Screening
3.0.01 Measure Screening
4 Detailed Approach
4.0.01 Detailed Approach

## Definitions
Definitions
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents
| Measure Assessment Metrics |  | Definition
| Enabling Device | Smart Device/Switch | Control functionality is enabled through an add-on smart device/switch
|  | Embedded | Control functionality is embedded into the equipment
| DR Strategy | Direct Controlled | Direct Controlled measures are those measures that the utility/ISO has a direct control over its operation and needs an opt out request from the customer if the measure needs to be put out of service for grid applications
|  | Scheduled | Resources that reduce load for personal benefit (e.g. bill management) or in response to a price signal or other behavioural stimulus (e.g. time-of-use pricing, critical peak pricing, price alerts)
| Service Provision Pathways | Direct Participant | Resources that are able to directly participate in the market to provide grid services
|  | Aggregate Participant | Resources that must go through an aggregated porfolio or a DER program to participate in providing grid services
|  | Not in the market/Other | Resources that are ineligible for service provision
|  | Multiple Pathways | Resources that are able to directly participate in the market, or join an aggregated porfolio of DERs to provide grid services
| Grid Services | Feasible & demonstrated | Technical feasible with demonstrated record of providing the service
|  | Technically feasible with operational constraints & limited demonstration | Technical and/or operational constraints limit opportunities
|  | Not feasible | Technical and/or operational constraints restrict service provision
| Dispatchable: | Yes | Controllable resources that can adhere to dispatch instructions within 5 minutes. Considers aggregate resources' ability to respond
|  | No | DERs that are not controllable and/or can not adhere to dispatch instructions within 5 minutes.
| Technology Maturity: | Mature | Wide-spread availability with proven track-record
|  | Commercially Available | Commercially available technologies with supply and/or performance limitations
|  | Emerging | Nascent or emerging technologies with limited availability and track-record
| Measure Screening Criteria |  | Definition
| Alignment with System Needs and Characteristics | Low | Not able to provide many of the grid services required to meet system needs.
|  | Mid | Able to provide some grid services to meet some system needs.
|  | High | Well suited to provide a range of grid services to meet system needs.
| Opportunity Size | Low | Small market size and limited growth within the study period.
|  | Mid | Medium market size, or small market size with moderate growth within the study period.
|  | High | Large market opportunity within the study period.
| Potential for delivering GHG reductions | Low | Measures that may increase greenhouse gas emissions.
|  | Mid | Measures that have the potential to slightly contribute towards emissions reductions.
|  | High | Measures that have the potential to substantially decrease emissions.
| Expected Cost-Effectiveness | Low | Not expected to be cost-effective within the study period.
|  | Mid | Expected to be cost-effective within the study period.
|  | High | Expected to be very cost-effective within the study period.
| Market readiness | Low | The technology has limited availability and/or demonstrated use.
|  | Mid | The technology is available but has some factors that would limit its adoption in the market, such as higher costs, limited availability, etc.
|  | High | The technology is widely available and demonstrated.
| Alignment with customer goals | Low | Measures do not meet customer needs and preferences, for example, do not reduce emissions, have the potential to increase rates and/or are a hassle for the customer's day-to-day.
|  | Mid | Measures generally align with customer needs and preferences, for example, energy efficiency and demand response measures.
|  | High | Measures align with cutomer needs and preferences for resiliency, rate reductions, etc.
| Relevance to Study Objectives/Scope | Low | Not well aligned with the study objectives and scope (determining the types and volumes of DERs that can be achieved in Ontario over the next decade and have the ability to provide wholesale electricity services).
|  | Mid | Somewhat aligned with the study objectives and scope (determining the types and volumes of DERs that can be achieved in Ontario over the next decade and have the ability to provide wholesale electricity services).
|  | High | Very aligned with the study objectives and scope (determining the types and volumes of DERs that can be achieved in Ontario over the next decade and have the ability to provide wholesale electricity services)
Note on E25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should be renamed "Alignment with / Capability to Meet System Needs" per the discussion in the stakeholder feedback doc.
Note on E43: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should be removed in this version.

## Summary_SC
Section 1
Summary
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents
Notes:

## Residential BTM Measures
Residential BTM Measures
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents
Sector: Residential Behind-the-Meter
| Technology/Measure | Recommended?
HVAC
| AC Thermostat | Yes
| ASHP/DMSHP Smart Thermostat | Yes
| Baseboard Heating Thermostat | No
| Dual-Fuel Space Heating Smart Thermostat | Yes
| Dual-Fuel Space Heating Smart Switch | Yes
| GSHP Smart Thermostat | No
Pools and Spas
| Electric Resistance Pool Heaters | No
| Heat Pump Pool Heaters | No
| Hot Tub/Spa | No
| Res. Pool Pumps | Yes
Smart Appliances
| Clothes Dryer Smart Switch | No
| Dehumidifers Smart Switch | No
| Dishwasher / Clothes Washer Smart Switch | No
| Fridge/Freezer Smart Switch | No
| Smart Clothes Dryer | Yes
| Smart Dishwasher / Clothes Washer | No
| Smart Fridge/Freezer | No
Storage
| BTM Battery Storage Residential | Yes
Thermal Storage
| Thermal Storage and Heat Pump | Yes
| Thermal Storage for Cooling | Yes
| Thermal Storage for Heating | Yes
Water Heating
| Dual-Fuel Water Heating | No
| Electric Resistance Water Heaters Smart Switch | Yes
| Heat Pump Water Heater Smart Switch | Yes
| Smart Electric Resistance Water Heaters | Yes
| Smart Heat Pump Water Heaters | Yes
Distributed Generation
| Other Micro Generation (Micro Wind, Micro Hydro, Micro CHP, etc.) | No
| Res. BTM Solar with Smart Inverters | Yes
Passenger EV Charging
| EV Charger Smart Switch | No
| Passenger EV Telematics | Yes
| Smart EV Chargers | Yes
| Vehicle-to-Grid (V2G) | Yes
Other Load Flexibility
| Other Behavioral-based Residential Flexibility | Yes
| Total | 19

## Non-Residential BTM Measures
Non-Residential BTM Measures
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents
Sector: Non-Residential Behind-the-Meter
| Technology/Measure | Recommended?
HVAC
| Large Commercial HVAC Control | Yes
| Small Commercial ASHP/DMSHP Smart Thermostat | Yes
| Small Commercial GSHP Smart Thermostat | No
| Small Commercial Smart Thermostat | Yes
Lighting Controls
| Lighting Controls | Yes
Pools and Spas
| Pool Heating | No
| Pool Pumps | No
| Spa/Hot Tubs | No
Storage
| BTM Battery Storage Non Residential | Yes
| Short-duration Storage (flywheel, Capacitor Bank, etc.) | No
Thermal Storage
| Commercial HVAC Thermal Storage | Yes
| Thermal Storage for Refrigeration Applications | Yes
Water Heating
| Large Commercial Dual-Fuel Water Heating | Yes
| Large Commercial Hot Water | Yes
| Small Commercial Dual-Fuel Water Heating | No
| Small Commercial Hot Water | Yes
Distributed Generation
| Back-up Generation | Yes
| Biomass/Biogas | No
| BTM Solar with Smart Inverters | Yes
| CHP | No
| Hydrogen Fuel Cell | No
| Natural Gas Fuel Cell | No
EV Fleet Charging
| Buses: EV Smart Charging | Yes
| Buses: Vehicle-to-Grid (V2G) | Yes
| HDV Fleet EV Smart Chargers | Yes
| HDV Fleet Vehicle-to-Grid (V2G) | Yes
| LDV Fleet EV Charger Smart Switch | No
| LDV Fleet EV Smart Chargers | Yes
| LDV Fleet EV Telematics | Yes
| LDV Fleet Vehicle-to-Grid (V2G) | Yes
| MDV Fleet EV Smart Chargers | Yes
| MDV Fleet Vehicle-to-Grid (V2G) | Yes
| Off Road EVs Smart Chargers | Yes
Other Load Flexibility
| District Cooling/Heating Flexibility | Yes
| Greenhouses: Grow Lights | Yes
| Irrigation Pump Controls | Yes
| Industrial Flexibility | Yes
| Other Commercial Flexibility | Yes
| Refrigeration Controls | Yes
| Total | 28

## FTM Measures
FTM Measures
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents
Sector: Front-of-the-Meter
| Technology/Measure | Recommended?
Storage
| CAES | No
| Electrothermal Storage | No
| Flywheel | No
| FTM Battery Storage | Yes
| Power-to-Gas (Hydrogen) | No
Distributed Generation
| FTM Biomass/Biogas | No
| FTM Small-scale Hydro | Yes
| FTM Small-scale Wind | No
| FTM Solar | Yes
| Total | 3

## Master Measure List
Master Measure List
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents
| Index | Technology/Measure | Description | Measure Group/Category | Sector
| 1 | FTM Biomass/Biogas | Biogas/biomass (e.g. landfill gas) used to offset all or a portion of local energy consumption or to support grid operations. | Distributed Generation | Front-of-the-Meter
| 2 | FTM Solar | FTM Solar includes utility scale and community/shared solar | Distributed Generation | Front-of-the-Meter
| 3 | FTM Small-scale Hydro | Small-scale hydro is a hydro-plant that is installed in small rivers, and typically is a run-of-the-river facility, meaning it does not have a forebay to store water. | Distributed Generation | Front-of-the-Meter
| 4 | FTM Small-scale Wind | Small scale wind (e.g., 50 to 300 kW) used to offset all or a portion of local energy consumption or to support grid operations. | Distributed Generation | Front-of-the-Meter
| 5 | CAES | Compressed Air Energy Storage | Storage | Front-of-the-Meter
| 6 | Power-to-Gas (Hydrogen) | Surplus energy can be converted to hydrogen gas. | Storage | Front-of-the-Meter
| 7 | Flywheel | Fast responding resource that uses intertia to provide frequency response | Storage | Front-of-the-Meter
| 8 | FTM Battery Storage | Battery storage (for example, li-ion or lead-acid) can be used to store energy during off-peak times for use on-peak. | Storage | Front-of-the-Meter
| 9 | Electrothermal Storage | Thermal Energy Storage is a technology that stores thermal energy by heating or cooling a storage medium. | Storage | Front-of-the-Meter
| 10 | Back-up Generation | Back-up generation powers a part or the entire facility's electrical system in case of a power outage or to reduce grid load. | Distributed Generation | Non-Residential Behind-the-Meter
| 11 | BTM Solar with Smart Inverters | Smart inverters help integrate solar energy and can provide grid support functions, such as voltage regulation, frequency support, etc. | Distributed Generation | Non-Residential Behind-the-Meter
| 12 | CHP | Combined Heat and Power at a non-residential facility used for space heating, cooling, domestic hot water, and other industrial processes, allowing for reduced use of grid energy during peak times. | Distributed Generation | Non-Residential Behind-the-Meter
| 13 | Hydrogen Fuel Cell | Fuel cells work similar to long-duration energy storage, but they do not run down or need recharging. They produce electricity and heat as long as fuel is supplied, providing long periods of load relief with minimal operational overhead. | Distributed Generation | Non-Residential Behind-the-Meter
| 14 | Biomass/Biogas | For example, on-farm biogas project or renewable biomass used to reduce electricity needs. | Distributed Generation | Non-Residential Behind-the-Meter
| 15 | LDV Fleet EV Smart Chargers | Level 2 smart chargers allow for controlled charging for light duty vehicles | EV Fleet Charging | Non-Residential Behind-the-Meter
| 16 | LDV Fleet EV Charger Smart Switch | Smart switch to control non-smart light duty fleet vehicle chargers | EV Fleet Charging | Non-Residential Behind-the-Meter
| 17 | LDV Fleet EV Telematics | Load control via on-board vehicle smart charging capabilities. | EV Fleet Charging | Non-Residential Behind-the-Meter
| 18 | LDV Fleet Vehicle-to-Grid (V2G) | Vehicle-to-Grid charging allows power to be pushed back to the grid from the battery of electric light duty fleet vehicles. | EV Fleet Charging | Non-Residential Behind-the-Meter
| 19 | MDV Fleet EV Smart Chargers | Level 2 smart chargers allow for controlled charging | EV Fleet Charging | Non-Residential Behind-the-Meter
| 20 | MDV Fleet Vehicle-to-Grid (V2G) | Vehicle-to-Grid charging allows power to be pushed back to the grid from the battery of electric medium and heavy duty fleet vehicles. | EV Fleet Charging | Non-Residential Behind-the-Meter
| 21 | HDV Fleet EV Smart Chargers | Level 2 smart chargers allow for controlled charging | EV Fleet Charging | Non-Residential Behind-the-Meter
| 22 | HDV Fleet Vehicle-to-Grid (V2G) | Vehicle-to-Grid charging allows power to be pushed back to the grid from the battery of electric medium and heavy duty fleet vehicles. | EV Fleet Charging | Non-Residential Behind-the-Meter
| 23 | Off Road EVs Smart Chargers | Level 2 smart chargers allow for controlled charging in off road vehicles (e.g. electric forklifts) | EV Fleet Charging | Non-Residential Behind-the-Meter
| 24 | Buses: EV Smart Charging | Level 2 smart chargers allow for controlled charging in buses | EV Fleet Charging | Non-Residential Behind-the-Meter
| 25 | Buses: Vehicle-to-Grid (V2G) | Vehicle-to-Grid charging allows power to be pushed back to the grid from the battery of buses. | EV Fleet Charging | Non-Residential Behind-the-Meter
| 26 | Large Commercial HVAC Control | Auto HVAC control for heating and cooling | HVAC | Non-Residential Behind-the-Meter
| 27 | Small Commercial Smart Thermostat | Smart thermostat or smart switch for heating and cooling setpoint control. | HVAC | Non-Residential Behind-the-Meter
| 28 | Lighting Controls | Lighting sensors and controls. | Lighting Controls | Non-Residential Behind-the-Meter
| 29 | District Cooling/Heating Flexibility | Pumps within system can act as a distributed energy resource. Includes geothermal. | Other Load Flexibility | Non-Residential Behind-the-Meter
| 30 | Other Commercial Flexibility | Curtailment of other commercial processes | Other Load Flexibility | Non-Residential Behind-the-Meter
| 31 | Irrigation Pump Controls | Irrigation systems have multiple pumps, which can be turned off to provide DR. | Other Load Flexibility | Non-Residential Behind-the-Meter
| 32 | Refrigeration Controls | Commercial refrigeration controls allowing refrigeration to cycle at reduced loads. | Other Load Flexibility | Non-Residential Behind-the-Meter
| 33 | Greenhouses: Grow Lights | Lighting sensors and controls for LED Grow Lights | Other Load Flexibility | Non-Residential Behind-the-Meter
| 34 | Pool Heating | Pool heaters can be turned off during peak demand times to offset load. | Pools and Spas | Non-Residential Behind-the-Meter
| 35 | Pool Pumps | Curtailment of pool pumps. | Pools and Spas | Non-Residential Behind-the-Meter
| 36 | Spa/Hot Tubs | Hot tubs and spas can be monitored during peak demand times to offset load. | Pools and Spas | Non-Residential Behind-the-Meter
| 37 | BTM Battery Storage Non Residential | Behind-the-meter storage can help non-residential facilities reduce demand charges by shifting loads. | Storage | Non-Residential Behind-the-Meter
| 38 | Short-duration Storage (flywheel, Capacitor Bank, etc.) | Super-short (<1 hour) duration storage that is able to provide fast frequency response. Example applications include providing energy during the time it takes for a UPS to come online. | Storage | Non-Residential Behind-the-Meter
| 39 | Commercial HVAC Thermal Storage | Thermal energy storage systems shift cooling energy use to non-peak times. | Thermal Storage | Non-Residential Behind-the-Meter
| 40 | Thermal Storage for Refrigeration Applications | Thermal storage for refrigeration applications provide cooling during peak times to reduce energy load. Some technologies (e.g. Viking Cold Solutions) claim to be able to deliver over 12 hours of load-shifting while improving refrigeration efficiency and average of 25%. | Thermal Storage | Non-Residential Behind-the-Meter
| 41 | Small Commercial Dual-Fuel Water Heating | A dual-fuel water heater uses both electricity and gas to provide water heating. A dual-fuel water heater system can provide curtailment by temporarily switching fuels from electric to some other fuel during times of grid need. | Water Heating | Non-Residential Behind-the-Meter
| 42 | Large Commercial Dual-Fuel Water Heating | A dual-fuel water heater uses both electricity and gas to provide water heating. A dual-fuel water heater system can provide curtailment by temporarily switching fuels from electric to some other fuel during times of grid need. | Water Heating | Non-Residential Behind-the-Meter
| 43 | Large Commercial Hot Water | Water heating setpoint control | Water Heating | Non-Residential Behind-the-Meter
| 44 | Small Commercial Hot Water | Water heating setpoint control | Water Heating | Non-Residential Behind-the-Meter
| 45 | Small Commercial GSHP Smart Thermostat | Cooling and heating setpoint control through smart thermostat or smart switch. | HVAC | Non-Residential Behind-the-Meter
| 46 | Small Commercial ASHP/DMSHP Smart Thermostat | Cooling and heating setpoint control through smart thermostat or smart switch. | HVAC | Non-Residential Behind-the-Meter
| 47 | Natural Gas Fuel Cell | Fuel cells can provide long periods of load relief with minimal operational overhead | Distributed Generation | Non-Residential Behind-the-Meter
| 48 | Industrial Flexibility | Curtailment of industrial load (processes, HVAC, lighting, etc.) | Other Load Flexibility | Non-Residential Behind-the-Meter
| 49 | Res. BTM Solar with Smart Inverters | Smart inverters help integrate solar energy and can provide grid support functions, such as voltage regulation, frequency support, etc. | Distributed Generation | Residential Behind-the-Meter
| 50 | Other Micro Generation (Micro Wind, Micro Hydro, Micro CHP, etc.) | Micro generation can enable homes to offset all or a portion of their electricity consumption. | Distributed Generation | Residential Behind-the-Meter
| 51 | AC Thermostat | Cooling setpoint control using a smart switch or smart thermostat. | HVAC | Residential Behind-the-Meter
| 52 | Baseboard Heating Thermostat | Heating setpoint control using a smart switch or smart thermostat. | HVAC | Residential Behind-the-Meter
| 53 | Dual-Fuel Space Heating Smart Thermostat | A dual-fuel space heater uses both electricity and gas to provide heating. A dual-fuel HVAC system can provide curtailment by temporarily switching fuels. | HVAC | Residential Behind-the-Meter
| 54 | Dual-Fuel Space Heating Smart Switch | A dual-fuel space heater uses both electricity and gas to provide heating. A dual-fuel HVAC system can provide curtailment by temporarily switching fuels. | HVAC | Residential Behind-the-Meter
| 55 | GSHP Smart Thermostat | Cooling and heating setpoint control through smart thermostat or smart switch. | HVAC | Residential Behind-the-Meter
| 56 | Other Behavioral-based Residential Flexibility | Behavioural demand response is where people are encouraged to reduce energy during peak event days. No technology enablement is used. | Other Load Flexibility | Residential Behind-the-Meter
| 57 | Smart EV Chargers | Level 2 smart chargers allow for controlled charging | Passenger EV Charging | Residential Behind-the-Meter
| 58 | EV Charger Smart Switch | Smart switches allow control on or off of vehicle charging | Passenger EV Charging | Residential Behind-the-Meter
| 59 | Passenger EV Telematics | On-board smart charging capacibilities | Passenger EV Charging | Residential Behind-the-Meter
| 60 | Vehicle-to-Grid (V2G) | Vehicle-to-Grid charging allows power to be pushed back to the grid from the battery of electric vehicles. | Passenger EV Charging | Residential Behind-the-Meter
| 61 | Electric Resistance Pool Heaters | Pool heaters can be turned off during peak demand times to offset load. | Pools and Spas | Residential Behind-the-Meter
| 62 | Heat Pump Pool Heaters | Pool heaters can be turned off during peak demand times to offset load. | Pools and Spas | Residential Behind-the-Meter
| 63 | Hot Tub/Spa | Hot tubs and spas can be monitored during peak demand times to offset load. | Pools and Spas | Residential Behind-the-Meter
| 64 | Clothes Dryer Smart Switch | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter
| 65 | Dehumidifers Smart Switch | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter
| 66 | Dishwasher / Clothes Washer Smart Switch | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter
| 67 | Fridge/Freezer Smart Switch | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter
| 68 | Smart Clothes Dryer | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter
| 69 | Smart Dishwasher / Clothes Washer | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter
| 70 | Smart Fridge/Freezer | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter
| 71 | BTM Battery Storage Residential | Energy can be stored in batteries during off-peak times to be used during peak times. | Storage | Residential Behind-the-Meter
| 72 | Thermal Storage for Heating | Electric thermal storage that converts off-peak electricity to heat and store it in heating elements contained in high-density ceramic bricks. | Thermal Storage | Residential Behind-the-Meter
| 73 | Thermal Storage for Cooling | Thermal energy storage systems shift cooling energy use to non-peak times. | Thermal Storage | Residential Behind-the-Meter
| 74 | Thermal Storage and Heat Pump | Electric Thermal Storage (ceramic brick) paired with a Heat Pump | Thermal Storage | Residential Behind-the-Meter
| 75 | Dual-Fuel Water Heating | A dual-fuel water heater uses both electricity and gas to provide water heating. A dual-fuel water heater system can provide curtailment by temporarily switching fuels from electric to some other fuel during times of grid need. | Water Heating | Residential Behind-the-Meter
| 76 | Electric Resistance Water Heaters Smart Switch | Water heating setpoint control through smart switch. | Water Heating | Residential Behind-the-Meter
| 77 | Heat Pump Water Heater Smart Switch | Water heating setpoint control through smart switch. | Water Heating | Residential Behind-the-Meter
| 78 | Smart Electric Resistance Water Heaters | Water heating setpoint control. | Water Heating | Residential Behind-the-Meter
| 79 | Smart Heat Pump Water Heaters | Water heating setpoint control. | Water Heating | Residential Behind-the-Meter
| 80 | ASHP/DMSHP Smart Thermostat | Cooling and heating setpoint control through smart thermostat or smart switch. | HVAC | Residential Behind-the-Meter
| 81 | Res. Pool Pumps | Curtailment of pool pumps. | Pools and Spas | Residential Behind-the-Meter

## Measure Assessment_SC
Section 2
Measure List & Assessment
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents

## Measure Assessment
Measure Assessment
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents
| Overview | [5 empty] | Operational Parameters |  |  | Grid Services | [5 empty] | Technology Considerations
| Index | Technology/Measure | Description | Measure Group/Category | Sector | Enabling Device | Device Control Strategy | Dispatchable | Service Provision Pathway | Electricity - Inject | Energy - Arbitrage | Energy - Avoid Curtailment (i.e. SBG) | Capacity | Operating Reserve | Frequency Regulation | Technology Maturity | Cost Enhancements Expected by End of Study | Performance Enhancements Expected by End of Study | Demonstrated Use in ON and/or other markets
| 1 | FTM Biomass/Biogas | Biogas/biomass (e.g. landfill gas) used to offset all or a portion of local energy consumption or to support grid operations. | Distributed Generation | Front-of-the-Meter | Embedded | Not Applicable | Yes | Both | Feasible & demonstrated | Not feasible | Not feasible | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No | Yes
| 2 | FTM Solar | FTM Solar includes utility scale and community/shared solar | Distributed Generation | Front-of-the-Meter | Embedded | Not Applicable | No | Both | Feasible & demonstrated | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | Maybe | Maybe | Yes
| 3 | FTM Small-scale Hydro | Small-scale hydro is a hydro-plant that is installed in small rivers, and typically is a run-of-the-river facility, meaning it does not have a forebay to store water. | Distributed Generation | Front-of-the-Meter | Embedded | Not Applicable | No | Both | Feasible & demonstrated | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No | Yes
| 4 | FTM Small-scale Wind | Small scale wind (e.g., 50 to 300 kW) used to offset all or a portion of local energy consumption or to support grid operations. | Distributed Generation | Front-of-the-Meter | Embedded | Not Applicable | No | Both | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Maybe | Maybe | Yes
| 5 | CAES | Compressed Air Energy Storage | Storage | Front-of-the-Meter | Embedded | Direct Controlled | Yes | Direct Participant | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Commercially Available | Maybe | Maybe | Yes
| 6 | Power-to-Gas (Hydrogen) | Surplus energy can be converted to hydrogen gas. | Storage | Front-of-the-Meter | Embedded | Direct Controlled | Yes | Direct Participant | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Emerging | Yes | Maybe | Yes
| 7 | Flywheel | Fast responding resource that uses intertia to provide frequency response | Storage | Front-of-the-Meter | Embedded | Direct Controlled | Yes | Both | Not feasible | Not feasible | Not feasible | Not feasible | Not feasible | Feasible & demonstrated | Emerging | No | No | Yes
| 8 | FTM Battery Storage | Battery storage (for example, li-ion or lead-acid) can be used to store energy during off-peak times for use on-peak. | Storage | Front-of-the-Meter | Embedded | Direct Controlled | Yes | Direct Participant | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Commercially Available | Yes | Maybe | Yes
| 9 | Electrothermal Storage | Thermal Energy Storage is a technology that stores thermal energy by heating or cooling a storage medium. | Storage | Front-of-the-Meter | Embedded | Direct Controlled | Yes | Both | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Mature | Maybe | Maybe
| 10 | Back-up Generation | Back-up generation powers a part or the entire facility's electrical system in case of a power outage or to reduce grid load. | Distributed Generation | Non-Residential Behind-the-Meter | None/Manual | Scheduled | No | Both | Feasible & demonstrated | Not feasible | Not feasible | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Mature | No | No | Yes
| 11 | BTM Solar with Smart Inverters | Smart inverters help integrate solar energy and can provide grid support functions, such as voltage regulation, frequency support, etc. | Distributed Generation | Non-Residential Behind-the-Meter | Smart Switch/Device | Direct Controlled | No | Both | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | Maybe | Maybe
| 12 | CHP | Combined Heat and Power at a non-residential facility used for space heating, cooling, domestic hot water, and other industrial processes, allowing for reduced use of grid energy during peak times. | Distributed Generation | Non-Residential Behind-the-Meter | None/Manual | Scheduled | No | Both | Feasible & demonstrated | Not feasible | Not feasible | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | Maybe | Yes
| 13 | Hydrogen Fuel Cell | Fuel cells work similar to long-duration energy storage, but they do not run down or need recharging. They produce electricity and heat as long as fuel is supplied, providing long periods of load relief with minimal operational overhead. | Distributed Generation | Non-Residential Behind-the-Meter | Embedded | Direct Controlled | Yes | Both | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Emerging | Yes | Yes
| 14 | Biomass/Biogas | For example, on-farm biogas project or renewable biomass used to reduce electricity needs. | Distributed Generation | Non-Residential Behind-the-Meter | Embedded | Direct Controlled | Yes | Both | Feasible & demonstrated | Not feasible | Not feasible | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No | Yes
| 15 | LDV Fleet EV Smart Chargers | Level 2 smart chargers allow for controlled charging for light duty vehicles | EV Fleet Charging | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Yes | Yes | Yes
| 16 | LDV Fleet EV Charger Smart Switch | Smart switch to control non-smart light duty fleet vehicle chargers | EV Fleet Charging | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Yes | Yes | Yes
| 17 | LDV Fleet EV Telematics | Load control via on-board vehicle smart charging capabilities. | EV Fleet Charging | Non-Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Yes | Yes | Yes
| 18 | LDV Fleet Vehicle-to-Grid (V2G) | Vehicle-to-Grid charging allows power to be pushed back to the grid from the battery of electric light duty fleet vehicles. | EV Fleet Charging | Non-Residential Behind-the-Meter | Embedded | Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Emerging | Yes | Yes | Yes
| 19 | MDV Fleet EV Smart Chargers | Level 2 smart chargers allow for controlled charging | EV Fleet Charging | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Yes | Yes
| 20 | MDV Fleet Vehicle-to-Grid (V2G) | Vehicle-to-Grid charging allows power to be pushed back to the grid from the battery of electric medium and heavy duty fleet vehicles. | EV Fleet Charging | Non-Residential Behind-the-Meter | Embedded | Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Emerging | Yes | Yes
| 21 | HDV Fleet EV Smart Chargers | Level 2 smart chargers allow for controlled charging | EV Fleet Charging | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Yes | Yes
| 22 | HDV Fleet Vehicle-to-Grid (V2G) | Vehicle-to-Grid charging allows power to be pushed back to the grid from the battery of electric medium and heavy duty fleet vehicles. | EV Fleet Charging | Non-Residential Behind-the-Meter | Embedded | Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Emerging | Yes | Yes
| 23 | Off Road EVs Smart Chargers | Level 2 smart chargers allow for controlled charging in off road vehicles (e.g. electric forklifts) | EV Fleet Charging | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Yes | Yes
| 24 | Buses: EV Smart Charging | Level 2 smart chargers allow for controlled charging in buses | EV Fleet Charging | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Yes | Yes | Yes
| 25 | Buses: Vehicle-to-Grid (V2G) | Vehicle-to-Grid charging allows power to be pushed back to the grid from the battery of buses. | EV Fleet Charging | Non-Residential Behind-the-Meter | Embedded | Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Emerging | Yes | Yes | Yes
| 26 | Large Commercial HVAC Control | Auto HVAC control for heating and cooling | HVAC | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No | Yes
| 27 | Small Commercial Smart Thermostat | Smart thermostat or smart switch for heating and cooling setpoint control. | HVAC | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No
| 28 | Lighting Controls | Lighting sensors and controls. | Lighting Controls | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Not feasible | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Mature | No | No
| 29 | District Cooling/Heating Flexibility | Pumps within system can act as a distributed energy resource. Includes geothermal. | Other Load Flexibility | Non-Residential Behind-the-Meter | None/Manual | Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Mature | No | No | Yes
| 30 | Other Commercial Flexibility | Curtailment of other commercial processes | Other Load Flexibility | Non-Residential Behind-the-Meter | None/Manual | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Not feasible | Feasible & demonstrated | Not feasible | Not feasible | Mature | No | No | Yes
| 31 | Irrigation Pump Controls | Irrigation systems have multiple pumps, which can be turned off to provide DR. | Other Load Flexibility | Non-Residential Behind-the-Meter | None/Manual | Scheduled or Direct Controlled | No | Aggregate Participant | Not feasible | Not feasible | Not feasible | Feasible & demonstrated | Not feasible | Not feasible | Mature | No | No
| 32 | Refrigeration Controls | Commercial refrigeration controls allowing refrigeration to cycle at reduced loads. | Other Load Flexibility | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Mature | No | No
| 33 | Greenhouses: Grow Lights | Lighting sensors and controls for LED Grow Lights | Other Load Flexibility | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Mature | Maybe | Maybe
| 34 | Pool Heating | Pool heaters can be turned off during peak demand times to offset load. | Pools and Spas | Non-Residential Behind-the-Meter | None/Manual | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Not feasible | Mature | No | No
| 35 | Pool Pumps | Curtailment of pool pumps. | Pools and Spas | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | No | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Mature | No | No | Yes
| 36 | Spa/Hot Tubs | Hot tubs and spas can be monitored during peak demand times to offset load. | Pools and Spas | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Mature | No | No
| 37 | BTM Battery Storage Non Residential | Behind-the-meter storage can help non-residential facilities reduce demand charges by shifting loads. | Storage | Non-Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Both | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Commercially Available | Yes | Maybe | Yes
| 38 | Short-duration Storage (flywheel, Capacitor Bank, etc.) | Super-short (<1 hour) duration storage that is able to provide fast frequency response. Example applications include providing energy during the time it takes for a UPS to come online. | Storage | Non-Residential Behind-the-Meter | Embedded | Direct Controlled | Yes | Both | Not feasible | Not feasible | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Emerging | Maybe | Maybe | Maybe
| 39 | Commercial HVAC Thermal Storage | Thermal energy storage systems shift cooling energy use to non-peak times. | Thermal Storage | Non-Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No
| 40 | Thermal Storage for Refrigeration Applications | Thermal storage for refrigeration applications provide cooling during peak times to reduce energy load. Some technologies (e.g. Viking Cold Solutions) claim to be able to deliver over 12 hours of load-shifting while improving refrigeration efficiency and average of 25%. | Thermal Storage | Non-Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | No | No
| 41 | Small Commercial Dual-Fuel Water Heating | A dual-fuel water heater uses both electricity and gas to provide water heating. A dual-fuel water heater system can provide curtailment by temporarily switching fuels from electric to some other fuel during times of grid need. | Water Heating | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Not feasible | Not feasible | Mature | No | No
| 42 | Large Commercial Dual-Fuel Water Heating | A dual-fuel water heater uses both electricity and gas to provide water heating. A dual-fuel water heater system can provide curtailment by temporarily switching fuels from electric to some other fuel during times of grid need. | Water Heating | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Not feasible | Not feasible | Mature | No | No
| 43 | Large Commercial Hot Water | Water heating setpoint control | Water Heating | Non-Residential Behind-the-Meter | Smart Switch/Device | Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Mature | No | No | Yes
| 44 | Small Commercial Hot Water | Water heating setpoint control | Water Heating | Non-Residential Behind-the-Meter | Smart Switch/Device | Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Mature | No | No
| 45 | Small Commercial GSHP Smart Thermostat | Cooling and heating setpoint control through smart thermostat or smart switch. | HVAC | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No
| 46 | Small Commercial ASHP/DMSHP Smart Thermostat | Cooling and heating setpoint control through smart thermostat or smart switch. | HVAC | Non-Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No
| 47 | Natural Gas Fuel Cell | Fuel cells can provide long periods of load relief with minimal operational overhead | Distributed Generation | Non-Residential Behind-the-Meter | Embedded | Direct Controlled | Yes | Both | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Commercially Available | Yes | Yes
| 48 | Industrial Flexibility | Curtailment of industrial load (processes, HVAC, lighting, etc.) | Other Load Flexibility | Non-Residential Behind-the-Meter | None/Manual | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Not feasible | Feasible & demonstrated | Not feasible | Not feasible | Mature | No | No | Yes
| 49 | Res. BTM Solar with Smart Inverters | Smart inverters help integrate solar energy and can provide grid support functions, such as voltage regulation, frequency support, etc. | Distributed Generation | Residential Behind-the-Meter | Smart Switch/Device | Direct Controlled | No | Both | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | Yes | No | Yes
| 50 | Other Micro Generation (Micro Wind, Micro Hydro, Micro CHP, etc.) | Micro generation can enable homes to offset all or a portion of their electricity consumption. | Distributed Generation | Residential Behind-the-Meter | None/Manual | Direct Controlled | No | Both | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | No | No | Yes
| 51 | AC Thermostat | Cooling setpoint control using a smart switch or smart thermostat. | HVAC | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No | Yes
| 52 | Baseboard Heating Thermostat | Heating setpoint control using a smart switch or smart thermostat. | HVAC | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | No | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No
| 53 | Dual-Fuel Space Heating Smart Thermostat | A dual-fuel space heater uses both electricity and gas to provide heating. A dual-fuel HVAC system can provide curtailment by temporarily switching fuels. | HVAC | Residential Behind-the-Meter | None/Manual | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Not feasible | Not feasible | Mature | No | No
| 54 | Dual-Fuel Space Heating Smart Switch | A dual-fuel space heater uses both electricity and gas to provide heating. A dual-fuel HVAC system can provide curtailment by temporarily switching fuels. | HVAC | Residential Behind-the-Meter | Smart Switch/Device | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Not feasible | Not feasible | Mature | No | No
| 55 | GSHP Smart Thermostat | Cooling and heating setpoint control through smart thermostat or smart switch. | HVAC | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No | Yes
| 56 | Other Behavioral-based Residential Flexibility | Behavioural demand response is where people are encouraged to reduce energy during peak event days. No technology enablement is used. | Other Load Flexibility | Residential Behind-the-Meter | None/Manual | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Not feasible | Feasible & demonstrated | Not feasible | Not feasible | Mature | No | No
| 57 | Smart EV Chargers | Level 2 smart chargers allow for controlled charging | Passenger EV Charging | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Yes | Yes | Yes
| 58 | EV Charger Smart Switch | Smart switches allow control on or off of vehicle charging | Passenger EV Charging | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Yes | Yes | Yes
| 59 | Passenger EV Telematics | On-board smart charging capacibilities | Passenger EV Charging | Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Commercially Available | Yes | Yes | Yes
| 60 | Vehicle-to-Grid (V2G) | Vehicle-to-Grid charging allows power to be pushed back to the grid from the battery of electric vehicles. | Passenger EV Charging | Residential Behind-the-Meter | Embedded | Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Emerging | Yes | Yes | Yes
| 61 | Electric Resistance Pool Heaters | Pool heaters can be turned off during peak demand times to offset load. | Pools and Spas | Residential Behind-the-Meter | Smart Switch/Device | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Not feasible | Mature | No | No
| 62 | Heat Pump Pool Heaters | Pool heaters can be turned off during peak demand times to offset load. | Pools and Spas | Residential Behind-the-Meter | Smart Switch/Device | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Not feasible | Mature | No | No
| 63 | Hot Tub/Spa | Hot tubs and spas can be monitored during peak demand times to offset load. | Pools and Spas | Residential Behind-the-Meter | Smart Switch/Device | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Mature | No | No
| 64 | Clothes Dryer Smart Switch | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Mature | No | No
| 65 | Dehumidifers Smart Switch | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter | Smart Switch/Device | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Mature | No | No
| 66 | Dishwasher / Clothes Washer Smart Switch | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Mature | No | No
| 67 | Fridge/Freezer Smart Switch | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Emerging | No | No
| 68 | Smart Clothes Dryer | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Commercially Available | Maybe | No
| 69 | Smart Dishwasher / Clothes Washer | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Commercially Available | Maybe | No
| 70 | Smart Fridge/Freezer | Smart appliances and appliances with smart switches can be used to provide demand response. | Smart Appliances | Residential Behind-the-Meter | Embedded | Scheduled | No | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Emerging | Maybe | No
| 71 | BTM Battery Storage Residential | Energy can be stored in batteries during off-peak times to be used during peak times. | Storage | Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Both | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Commercially Available | Yes | Maybe | Yes
| 72 | Thermal Storage for Heating | Electric thermal storage that converts off-peak electricity to heat and store it in heating elements contained in high-density ceramic bricks. | Thermal Storage | Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No | Yes
| 73 | Thermal Storage for Cooling | Thermal energy storage systems shift cooling energy use to non-peak times. | Thermal Storage | Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Emerging | Maybe | Maybe | Yes
| 74 | Thermal Storage and Heat Pump | Electric Thermal Storage (ceramic brick) paired with a Heat Pump | Thermal Storage | Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No
| 75 | Dual-Fuel Water Heating | A dual-fuel water heater uses both electricity and gas to provide water heating. A dual-fuel water heater system can provide curtailment by temporarily switching fuels from electric to some other fuel during times of grid need. | Water Heating | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Not feasible | Not feasible | Mature | No | No
| 76 | Electric Resistance Water Heaters Smart Switch | Water heating setpoint control through smart switch. | Water Heating | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Mature | No | No | Yes
| 77 | Heat Pump Water Heater Smart Switch | Water heating setpoint control through smart switch. | Water Heating | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Commercially Available | No | No | Yes
| 78 | Smart Electric Resistance Water Heaters | Water heating setpoint control. | Water Heating | Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Feasible & demonstrated | Mature | Yes | No | Yes
| 79 | Smart Heat Pump Water Heaters | Water heating setpoint control. | Water Heating | Residential Behind-the-Meter | Embedded | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Mature | Yes | No | Yes
| 80 | ASHP/DMSHP Smart Thermostat | Cooling and heating setpoint control through smart thermostat or smart switch. | HVAC | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | Yes | Aggregate Participant | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Feasible & demonstrated | Technically feasible with operational constraints &/or limited demonstration | Technically feasible with operational constraints &/or limited demonstration | Mature | No | No
| 81 | Res. Pool Pumps | Curtailment of pool pumps. | Pools and Spas | Residential Behind-the-Meter | Smart Switch/Device | Scheduled or Direct Controlled | No | Aggregate Participant | Not feasible | Not feasible | Not feasible | Technically feasible with operational constraints &/or limited demonstration | Not feasible | Not feasible | Mature | No | No | Yes

## Screening_SC
Section 3
Measure Screening
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents

## Measure Screening
Measure Screening
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents
| Overview |  |  |  | Criteria
| Index | Technology/Measure | Sector | Measure Group/Category | Alignment with / capability to meet system needs | Opportunity Size | Potential for delivering GHG reductions | Expected Cost-Effectiveness | Market readiness | Alignment with customer goals | Recommended DERs | Rationale
| 1 | FTM Biomass/Biogas | Front-of-the-Meter | Distributed Generation | Mid | Low | High | Low | High | Mid | No | Limited expected cost-effectiveness and market opportunities given the competition for biomass feedstock.
| 2 | FTM Solar | Front-of-the-Meter | Distributed Generation | Mid | Mid | High | Mid | High | Mid | Yes | Solar is a market ready technology that can provide energy and some capacity at a relatively low cost.
| 3 | FTM Small-scale Hydro | Front-of-the-Meter | Distributed Generation | Mid | Mid | High | Low | High | Mid | Yes | Existing small hydro resources can provide cost-effective grid services
| 4 | FTM Small-scale Wind | Front-of-the-Meter | Distributed Generation | Mid | Low | High | Low | High | Mid | No | Limited market opportunity given the small market size
| 5 | CAES | Front-of-the-Meter | Storage | High | Low | Mid | Low | Low | Mid | No | Typically deployed as a transmission connected asset to leverage economies for scale.
| 6 | Power-to-Gas (Hydrogen) | Front-of-the-Meter | Storage | Mid | Low | Mid | Low | Low | Mid | No | Market readiness is limited and is not expected to be commercially mature by the end of the study period. Cost-effectiveness is limited as well.
| 7 | Flywheel | Front-of-the-Meter | Storage | Low | Low | Low | Low | Mid | Mid | No | Limited ability to contribute to system needs and minimal cost-effectiveness compared to other storage measures
| 8 | FTM Battery Storage | Front-of-the-Meter | Storage | High | High | High | Mid | High | Mid | Yes | FTM standalone storage is a flexible resource for grid services, with expected cost reductions, leading to cost-efficient deployment over the study period.
| 9 | Electrothermal Storage | Front-of-the-Meter | Storage | Mid | Low | Mid | Low | Mid | Mid | No | Typically deployed in larger transmission-connected set-ups to leverage economies for scale
| 10 | Back-up Generation | Non-Residential Behind-the-Meter | Distributed Generation | Mid | Mid | Low | Mid | High | High | Yes | Backup generation is an available resource that can be tapped into with minimal costs
| 11 | BTM Solar with Smart Inverters | Non-Residential Behind-the-Meter | Distributed Generation | Mid | Mid | High | Mid | High | Mid | Yes | Solar with storage is a market ready technology, that provides significant grid flexibility, is aligned with system needs, and is expected to be cost effective for both the customer and the system
| 12 | CHP | Non-Residential Behind-the-Meter | Distributed Generation | Mid | Mid | Low | Low | High | Mid | No | Limited future opportunities expected to emerge given the limited potential for grid service provisions, GHG savings and cost-effectiveness relative to other measures
| 13 | Hydrogen Fuel Cell | Non-Residential Behind-the-Meter | Distributed Generation | Mid | Low | Mid | Low | Low | Mid | No | Market readiness is limited and cost-effectiveness is limited.
| 14 | Biomass/Biogas | Non-Residential Behind-the-Meter | Distributed Generation | Mid | Low | Mid | Low | High | Mid | No | Offers mid-level benefits, with low market opportunities & cost-effectiveness
| 15 | LDV Fleet EV Smart Chargers | Non-Residential Behind-the-Meter | EV Fleet Charging | High | Mid | Mid | High | High | Mid | Yes | EV smart chargers are expected to growth significantly as the share of EV vehicles increase over the study period, while being cost-effective.
| 16 | LDV Fleet EV Charger Smart Switch | Non-Residential Behind-the-Meter | EV Fleet Charging | High | Low | Mid | Mid | High | Mid | No | Prevalence of smart charging as well as in-vehicle charging capabilities likely to limit market for “dumb” EV chargers
| 17 | LDV Fleet EV Telematics | Non-Residential Behind-the-Meter | EV Fleet Charging | High | Low | Mid | Mid | Low | Mid | Yes | Limited market opportunity over the study period
| 18 | LDV Fleet Vehicle-to-Grid (V2G) | Non-Residential Behind-the-Meter | EV Fleet Charging | Mid | Mid | Mid | High | Low | Mid | Yes | V2G can provide valuable services to the grid. Over the study period, market readiness and opportunity size are expected to grow and deliver cost-effective services.
| 19 | MDV Fleet EV Smart Chargers | Non-Residential Behind-the-Meter | EV Fleet Charging | Mid | Mid | Mid | High | Mid | Mid | Yes | EV smart chargers are expected to growth significantly as the share of EV vehicles increase over the study period, while being cost-effective.
| 20 | MDV Fleet Vehicle-to-Grid (V2G) | Non-Residential Behind-the-Meter | EV Fleet Charging | Mid | Mid | Mid | High | Low | Mid | Yes | V2G can provide valuable services to the grid. Over the study period, market readiness and opportunity size are expected to grow and deliver cost-effective services.
| 21 | HDV Fleet EV Smart Chargers | Non-Residential Behind-the-Meter | EV Fleet Charging | Mid | Mid | Mid | High | Mid | Mid | Yes | EV smart chargers are expected to growth significantly as the share of EV vehicles increase over the study period, while being cost-effective.
| 22 | HDV Fleet Vehicle-to-Grid (V2G) | Non-Residential Behind-the-Meter | EV Fleet Charging | Mid | Mid | Mid | High | Low | Mid | Yes | V2G can provide valuable services to the grid. Over the study period, market readiness and opportunity size are expected to grow and deliver cost-effective services.
| 23 | Off Road EVs Smart Chargers | Non-Residential Behind-the-Meter | EV Fleet Charging | Mid | Mid | Mid | High | Mid | Mid | Yes | EV smart chargers are expected to growth significantly as the share of EV vehicles increase over the study period, while being cost-effective.
| 24 | Buses: EV Smart Charging | Non-Residential Behind-the-Meter | EV Fleet Charging | High | High | Mid | High | Mid | Mid | Yes | EV smart chargers are expected to growth significantly as the share of EV vehicles increase over the study period, while being cost-effective.
| 25 | Buses: Vehicle-to-Grid (V2G) | Non-Residential Behind-the-Meter | EV Fleet Charging | Mid | Mid | Mid | High | Low | Mid | Yes | V2G can provide valuable services to the grid. Over the study period, market readiness and opportunity size are expected to grow and deliver cost-effective services.
| 26 | Large Commercial HVAC Control | Non-Residential Behind-the-Meter | HVAC | High | High | Mid | High | High | Low | Yes | Commercial curtailment, including HVAC is, generally speaking, the amongst the most cost-effective DER measure & with large opportunities.
| 27 | Small Commercial Smart Thermostat | Non-Residential Behind-the-Meter | HVAC | High | Mid | Mid | Mid | High | Low | Yes | Smart thermostat control is a staple of DER, with high opportunities and cost-effectiveness
| 28 | Lighting Controls | Non-Residential Behind-the-Meter | Lighting Controls | Mid | High | Mid | High | High | Low | Yes | Commercial curtailment, including lighting is, generally speaking, the amongst the most cost-effective DER measure & with large opportunities.
| 29 | District Cooling/Heating Flexibility | Non-Residential Behind-the-Meter | Other Load Flexibility | Low | Low | Mid | High | Mid | Low | Yes | Limited ability to contribute to system needs and limited market opportunities
| 30 | Other Commercial Flexibility | Non-Residential Behind-the-Meter | Other Load Flexibility | Mid | High | Mid | High | High | Mid | Yes | Commercial curtailment, including process curtailment is, generally speaking, the amongst the most cost-effective DER measure & with large opportunities.
| 31 | Irrigation Pump Controls | Non-Residential Behind-the-Meter | Other Load Flexibility | Mid | Low | Mid | Mid | High | Mid | Yes | Offers mid-level benefits, with low market opportunities
| 32 | Refrigeration Controls | Non-Residential Behind-the-Meter | Other Load Flexibility | Low | Mid | Mid | Mid | High | Mid | Yes | Cost-effective measure, potential is mainly limited to the food sale and warehouse segments.
| 33 | Greenhouses: Grow Lights | Non-Residential Behind-the-Meter | Other Load Flexibility | Low | Mid | Mid | Mid | Mid | Mid | Yes | Growing market, and expected to be cost-effective.
| 34 | Pool Heating | Non-Residential Behind-the-Meter | Pools and Spas | Low | Low | Mid | High | High | Low | No | Limited market opportunity given the small market size
| 35 | Pool Pumps | Non-Residential Behind-the-Meter | Pools and Spas | Low | Mid | Mid | High | High | Low | No | Limited ability to contribute to system needs
| 36 | Spa/Hot Tubs | Non-Residential Behind-the-Meter | Pools and Spas | Mid | Low | Mid | Mid | High | Mid | No | Offers mid-level benefits, with low market opportunities
| 37 | BTM Battery Storage Non Residential | Non-Residential Behind-the-Meter | Storage | High | High | High | Mid | High | Mid | Yes | BTM standalone storage is a flexible resource for grid services, with expected cost reductions, leading to cost-efficient deployment over the study period.
| 38 | Short-duration Storage (flywheel, Capacitor Bank, etc.) | Non-Residential Behind-the-Meter | Storage | Low | Low | Low | Low | Mid | Mid | No | Expensive technology and limited applicability (regulation)
| 39 | Commercial HVAC Thermal Storage | Non-Residential Behind-the-Meter | Thermal Storage | High | High | Mid | High | High | Mid | Yes | Thermal storage has been around for decades, and is expected to deliver cost-effective savings in the commercial sector.
| 40 | Thermal Storage for Refrigeration Applications | Non-Residential Behind-the-Meter | Thermal Storage | Mid | Mid | Mid | High | Mid | Mid | Yes | Thermal storage has been around for decades, and is expected to deliver cost-effective savings in the commercial sector.
| 41 | Small Commercial Dual-Fuel Water Heating | Non-Residential Behind-the-Meter | Water Heating | Low | Mid | Low | Low | Mid | Mid | No | Limited market opportunity and GHG reductions
| 42 | Large Commercial Dual-Fuel Water Heating | Non-Residential Behind-the-Meter | Water Heating | Low | Mid | Low | Low | Mid | Mid | Yes | Limited market opportunity and GHG reductions
| 43 | Large Commercial Hot Water | Non-Residential Behind-the-Meter | Water Heating | High | High | Mid | High | Mid | Mid | Yes | Commercial curtailment, including hot water is, generally speaking, the amongst the most cost-effective DER measure & with large opportunities.
| 44 | Small Commercial Hot Water | Non-Residential Behind-the-Meter | Water Heating | High | Mid | Mid | Low | Mid | Mid | Yes | Electric water heaters can provide high value services to the grid, while being cost-effectiveness.
| 45 | Small Commercial GSHP Smart Thermostat | Non-Residential Behind-the-Meter | HVAC | High | Low | Mid | High | High | Low | No | Limited market opportunity given the small market size. Will be blended with ASHP.
| 46 | Small Commercial ASHP/DMSHP Smart Thermostat | Non-Residential Behind-the-Meter | HVAC | High | High | Mid | High | High | Mid | Yes | Smart thermostat control is a staple of DER, with high opportunities and cost-effectiveness
| 47 | Natural Gas Fuel Cell | Non-Residential Behind-the-Meter | Distributed Generation | Mid | Mid | Low | Mid | Mid | Mid | No | Low GHG reduction compared to other DER.
| 48 | Industrial Flexibility | Non-Residential Behind-the-Meter | Other Load Flexibility | Mid | High | Mid | High | High | Mid | Yes | Industrial curtailment, including process curtailment is, generally speaking, the amongst the most cost-effective DER measure & with large opportunities.
| 49 | Res. BTM Solar with Smart Inverters | Residential Behind-the-Meter | Distributed Generation | Mid | Mid | High | High | High | High | Yes | Solar with battery is a market ready technology, that provides significant grid flexibility, is aligned with system needs, and is expected to be cost-effective for both the customer and the system
| 50 | Other Micro Generation (Micro Wind, Micro Hydro, Micro CHP, etc.) | Residential Behind-the-Meter | Distributed Generation | Mid | Low | Mid | Low | Mid | High | No | Limited market opportunity given the small market size
| 51 | AC Thermostat | Residential Behind-the-Meter | HVAC | High | High | Mid | High | High | Low | Yes | Smart thermostat control is a staple of DER, with high opportunities and cost-effectiveness
| 52 | Baseboard Heating Thermostat | Residential Behind-the-Meter | HVAC | Mid | Low | Mid | Mid | High | Low | No | Limited ability to contribute to emerging system needs and small opportunity size
| 53 | Dual-Fuel Space Heating Smart Thermostat | Residential Behind-the-Meter | HVAC | Low | Mid | Low | Mid | High | Low | Yes | Limited market opportunity and GHG reductions
| 54 | Dual-Fuel Space Heating Smart Switch | Residential Behind-the-Meter | HVAC | Low | Mid | Low | Low | High | Low | Yes | Limited market opportunity and GHG reductions
| 55 | GSHP Smart Thermostat | Residential Behind-the-Meter | HVAC | High | Low | Mid | High | High | Low | No | Limited market opportunity given the small market size. Will be blended with ASHP.
| 56 | Other Behavioral-based Residential Flexibility | Residential Behind-the-Meter | Other Load Flexibility | Mid | High | Mid | High | High | Mid | Yes | Although difficult to quantify, behavior-based residential curtailment is generally highly cost-effective
| 57 | Smart EV Chargers | Residential Behind-the-Meter | Passenger EV Charging | High | Mid | Mid | High | High | Mid | Yes | EV smart chargers are expected to growth significantly as the share of EV vehicle increase over the study period, while being cost-effective.
| 58 | EV Charger Smart Switch | Residential Behind-the-Meter | Passenger EV Charging | High | Low | Mid | Mid | High | Mid | No | Prevalence of smart charging as well as in-vehicle charging capabilities likely to limit market for “dumb” EV chargers
| 59 | Passenger EV Telematics | Residential Behind-the-Meter | Passenger EV Charging | High | Low | Mid | Mid | Low | Mid | Yes | Limited market opportunity over the study period
| 60 | Vehicle-to-Grid (V2G) | Residential Behind-the-Meter | Passenger EV Charging | Mid | Mid | Mid | High | Low | Mid | Yes | V2G can provide valuable services to the grid. Over the study period, market readiness and opportunity size are expected to grow and deliver cost-effective services.
| 61 | Electric Resistance Pool Heaters | Residential Behind-the-Meter | Pools and Spas | Low | Low | Mid | High | High | Low | No | Limited market opportunity given the small market size
| 62 | Heat Pump Pool Heaters | Residential Behind-the-Meter | Pools and Spas | Low | Low | Mid | High | High | Low | No | Limited market opportunity given the small market size
| 63 | Hot Tub/Spa | Residential Behind-the-Meter | Pools and Spas | Mid | Low | Mid | Mid | High | Low | No | Limited ability to contribute to system needs & low opportunity size
| 64 | Clothes Dryer Smart Switch | Residential Behind-the-Meter | Smart Appliances | Low | Mid | Mid | Mid | Mid | Low | No | Measure typically not found to be cost-effective
| 65 | Dehumidifers Smart Switch | Residential Behind-the-Meter | Smart Appliances | Low | Mid | Mid | Mid | Mid | Low | No | Measure typically not found to be cost-effective
| 66 | Dishwasher / Clothes Washer Smart Switch | Residential Behind-the-Meter | Smart Appliances | Low | Low | Mid | Low | Mid | Low | No | Measure typically not found to be cost-effective
| 67 | Fridge/Freezer Smart Switch | Residential Behind-the-Meter | Smart Appliances | Low | Low | Mid | Low | Mid | Low | No | Measure typically not found to be cost-effective
| 68 | Smart Clothes Dryer | Residential Behind-the-Meter | Smart Appliances | Low | Mid | Mid | High | Mid | Low | Yes | Often cost-effective, and good potential in the single family segment.
| 69 | Smart Dishwasher / Clothes Washer | Residential Behind-the-Meter | Smart Appliances | Low | Low | Mid | Mid | Mid | Low | No | Measure typically not found to be cost-effective
| 70 | Smart Fridge/Freezer | Residential Behind-the-Meter | Smart Appliances | Low | Low | Mid | Low | Mid | Low | No | Measure typically not found to be cost-effective
| 71 | BTM Battery Storage Residential | Residential Behind-the-Meter | Storage | High | Mid | Mid | Mid | High | High | Yes | BTM standalone storage is a flexible resource for grid services, with expected cost reductions, leading to cost-efficient deployment over the study period.
| 72 | Thermal Storage for Heating | Residential Behind-the-Meter | Thermal Storage | Mid | Low | Mid | Mid | Mid | Mid | Yes | Residential thermal storage has large opportunity and is market ready. However cost-effectiveness is not always achieved.
| 73 | Thermal Storage for Cooling | Residential Behind-the-Meter | Thermal Storage | High | Mid | Mid | Mid | Mid | Mid | Yes | Residential thermal storage has large opportunity and is market ready. However cost-effectiveness is not always achieved.
| 74 | Thermal Storage and Heat Pump | Residential Behind-the-Meter | Thermal Storage | Mid | Mid | Mid | Mid | Mid | Mid | Yes | Residential thermal storage has large opportunity and is market ready. However cost-effectiveness is not always achieved.
| 75 | Dual-Fuel Water Heating | Residential Behind-the-Meter | Water Heating | Low | Mid | Low | Low | Mid | Mid | No | Limited market opportunity and GHG reductions
| 76 | Electric Resistance Water Heaters Smart Switch | Residential Behind-the-Meter | Water Heating | High | Mid | Mid | Mid | High | Mid | Yes | Electric water heaters can provide high value services to the grid, while being cost-effectiveness.
| 77 | Heat Pump Water Heater Smart Switch | Residential Behind-the-Meter | Water Heating | High | Mid | Mid | Mid | Mid | Mid | Yes | Electric water heaters can provide high value services to the grid, while being cost-effectiveness. Heat Pump water heater penetration is expected to grow over the duration of the study.
| 78 | Smart Electric Resistance Water Heaters | Residential Behind-the-Meter | Water Heating | High | Mid | Mid | High | High | Mid | Yes | Electric water heaters can provide high value services to the grid, while being cost-effectiveness.
| 79 | Smart Heat Pump Water Heaters | Residential Behind-the-Meter | Water Heating | High | Mid | Mid | High | Mid | Mid | Yes | Electric water heaters can provide high value services to the grid, while being cost-effectiveness. Heat Pump water heater penetration is expected to grow over the duration of the study.
| 80 | ASHP/DMSHP Smart Thermostat | Residential Behind-the-Meter | HVAC | High | High | Mid | High | High | Mid | Yes | Smart thermostat control is a staple of DER, with high opportunities and cost-effectiveness
| 81 | Res. Pool Pumps | Residential Behind-the-Meter | Pools and Spas | Low | Mid | Mid | High | High | Mid | Yes | Limited ability to contribute to system needs, but usually highly cost-effective.

## Approach_SC
Section 4
Detailed Approach
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents

## Approach
Detailed Approach
IESO DER Potential Study - Measure List, Pre-Assessment & Approach
Go to Table of Contents
[6 empty] | Technical Potential | [7 empty] | Achievable Potential |  |  |  | Grid Services |  |  |  |  | Costs | [5 empty] | Other
|  |  | Measure Details |  |  | Technical Market Sizing |  | Market Growth |  | Measure Sizing |  | Baseline Load Shape |  | Achievable Potential Adoption Approach |  | Measure Sizing Adjusted [Achievable] |  | Capacity | Operating Reserve | Frequency Regulation | Energy/Arbitrage/SBG | Ability to capture 5-minute benefits (derating factor) | Measure Up-front Costs |  | Measure O&M Costs |  | Cost Projections |  | Lifetime |  | Baseline Market |  | Measure Variation
| Pre-assessment Index | Study Index | Technology/Measure | Sector | Measure Group/Category | Approach/Value | Source | Approach/Value | Source | Approach/Value | Source | Approach/Value | Source | Approach/Value | Source | Approach/Value | Source | Approach/Value | Approach/Value | Approach/Value | Approach/Value | Approach/Value | Approach/Value | Source | Approach/Value | Source | Approach/Value | Source | Approach/Value | Source | Approach/Value | Source | Measure Variation
| 2 | 1 | FTM Solar | Front-of-the-Meter | Distributed Generation | The technical potential for FTM solar is determined by the capacity of the resource it most likely can displace from the generation stack. The annual technical potential will be subject to changes in the market conditions such as capacity retirements and natural gas additions and technical challenges such as interconnection constraints and land unavailability. | IESO Reports | IESO capacity needs, natural gas additions and retirements, and interconnection and land constraints | IESO Reports Wholesale Markets | N/A (see technical market sizing) | IESO Reports | PVWatts Generation Profile Data | PVWatts, DNV-GL | Detailed market adoption modeling for each scenario | Detailed adoption modelling | N/A | N/A | Median of the daily average generation during summer capacity hours | N/A | N/A | Hourly Generation x Hourly Avoided Energy Costs | Yes | Ultility Scale Solar and BOS System costs | NREL ATB Baseline Study | Typical system maintenace costs (% of CAPEX) and inverter replacement | NREL ATB Baseline Study | Costs are expected to decrease | NREL ATB Projections | EUL of Utility Scale Solar: 30 | NREL | Consider only groundmount PV systems: 1437 MW | IESO’s Active Contracted Generation List, Ground Mounted Systems
| 3 | 2 | FTM Small-scale Hydro | Front-of-the-Meter | Distributed Generation | Technical potential limited by Natural Gas that can be displaced by small hydro, hydro-potential of rivers in Ontario, ecological constraints | Ontario’s Waterpower Potential study | IESO capacity needs, natural gas additions and retirements, and interconnection and land constraints | IESO Reports Wholesale Markets | N/A (see technical market sizing) | IESO Reports | Run-of-river hydro profiles | Canada Hydrological Database | Detailed market adoption modeling for each scenario | Detailed adoption modelling | N/A | N/A | Median of the daily average generation during summer capacity hours | Reserve 10% headroom for flexible OR. Generation is assumed to be derated to 90%. | Reserve 10% headroom for flexible FR. Generation is assumed to be derated to 90%. | Hourly Generation x Hourly Avoided Energy Costs | Yes | Upfront Capex Costs | Ontario’s Waterpower Potential study | Typical O&M Costs | Ontario’s Waterpower Potential study | N/A | Gas Generator Market Reports | EUL of Small Hydro: 50 | Ontario’s Waterpower Potential study | Consider exisiting small hydro capacity (306 MW) | IESO’s Active Contracted Generation List
| 8 | 3 | FTM Battery Storage | Front-of-the-Meter | Storage | The technical potential for FTM storage is the capacity that can support 100% peak demand reduction capability (PDRC). The drop in the PDRC values would mean that for 1 MW of storage added to the system the corresponding drop in the system load is less that 1 MW. This technical potential can be estimated through iterations of different FTM Storage Capacity (Total) | IESO Reports System Load Profile | IESO Capacity Needs, Changes in the System Load Factor, Natural Gas Additions and Retirements, interconnection constraints and land unavailability, | IESO Reports Wholesale Markets | FTM Energy Storage would be characterised as a single measure. | TBD | N/A | N/A | Detailed market adoption modeling for each scenario | Detailed adoption modelling | Sized to typical system sizing practices | TBD | Sustained capacity reduction during peak hours as per dispatch instructions | Average capacity reserved for OR provision as per dispatch instructions | Ramp up/down provision based on min(headroom/footroom) | Peak to Off-Peak shifting and charge during SBG hours as per dispatch instructions. Derated by charging and discharging losses. | Yes | Energy Storage System and BOS System Costs | ES Cost Projections (NRCAN, BNEF) | Typical system maintenace (% of CAPEX) | NREL ATB Baseline Study | Costs are expected to decrease | BNEF. NREL ATB | EUL of Utility Scale Energy Storage: 10 | NRCAN, NREL Reports | Current capacity contracted with IESO (50 MW) | IESO
| 10 | 4 | Back-up Generation | Non-Residential Behind-the-Meter | Distributed Generation | Number of Commercial Customers with Natural Gas Back up Generation Systems. | CEUS and APO | Follows segment/population growth. | Population growth - APO. | Sized to power rating of average back up generator. | IESO's DERs Survey | N/A | N/A | Estimated penetration of back-up generation based on market data and trends | TBD | N/A | N/A | Capacity of natural gas gensets | 70% of Equipment Power Rating limted to 500 hours a year | N/A | Hourly Generation x Hourly Avoided Energy Costs | Yes | Incremental compliance and Fuel Costs | Gas Generator Market Reports | Maintainence Costs, Fuel Costs, Compliance Cost | Gas Generator Market Reports | N/A | N/A | EUL of generators: 9 | Internal Dunsky Measure Database | Existing share of back up generators | CEUS Data IESO | All commercial segments
| 11 | 5 | BTM Solar with Smart Inverters | Non-Residential Behind-the-Meter | Distributed Generation | Number of buildings with a rooftop suitable for solar deployment | IESO Solar PV Potential Study | Rate of growth / new construction by segment | Population growth - APO. | Maximum size of system that can be theoretically deployed based on roof size and typical panel footprint | IESO Solar APS Study | Ontario-Average Generation Profile | IESO Solar APS Study | Detailed market adoption modeling for each scenario | Detailed adoption modelling | Sized to typical system sizing practices | Net-metering interconnection data | Median of the daily average generation during summer capacity hours | N/A | N/A | Hourly Generation x Hourly Avoided Energy Costs | Yes | BTM Solar Upfront Costs | OEB DER Impact Study | Typical system maintenace costs (% of CAPEX) and inverter replacement | NREL ATB Baseline Study | Costs are expected to decrease | NREL ATB Baseline Study | EUL of BTM solar: 30 | Typical Industry Assumption | Current Baseline 480 MW. MicroFIT and Net Metering Data were used for determining capacity and number of installs in the baseline year. | IESO’s Active Contracted Generation List. Rooftop systems | All commercial segments
| 15 | 6 | LDV Fleet EV Smart Chargers | Non-Residential Behind-the-Meter | EV Fleet Charging | Number of electric light-duty fleet vehicles | Number of EVs - APO's EV adoption forecast. Share of fleet EV LDV vehicle -Dunsky assumption | Forecasted electric light-duty fleet adoption | APO with scenario adjustments | Nameplate capacity of the charger. 10 kW. | Plug'N Drive, EV Batteries Value Proposition for Ontario's Electricity Grid and EV Owners, July 2020 | Average LDV non-residential EV load profile | Final 2020 Transportation Electrification Forecast, ISO-NE, April 2020. | Estimated penetration of smart EV chargers based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging during peak hours. Provide up to 6 hours of curtailable load during the evening peak. | Vehicle to stop charging to provide demand reduction when called upon. Assuming vehicle is plugged in and available 18 hours/day. | V1G is able to provide regulation down services by charging the battery. Batteries can respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | EVs can be scheduled to absorb SBG when it is the highest. Can provide up to 6 hours of load absorption. Assume vehicle is plugged in 18 hours a day. | Yes | Incremental equipment cost from upgrading a dumb charger to a smart charger | Internal Dunsky Measure Database | No incremental maintenance. | Typical Industry Assumption | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | Number of EVs in jurisdiction x % fleet LDV EVs x % with smart charging capabilities | Number of EVs - APO's EV adoption forecast. Share of fleet EV LDV vehicle - Internal Dunsky Database. Penetration of EV smart chargers - Internal Dunsky Database. | All commercial segments
| 18 | 7 | LDV Fleet Vehicle-to-Grid (V2G) | Non-Residential Behind-the-Meter | EV Fleet Charging | Number of electric light-duty fleet vehicles | Number of EVs - APO's EV adoption forecast. Share of fleet EV LDV vehicle -Dunsky assumption | Forecasted electric light-duty fleet adoption | APO with scenario adjustments | Nameplate capacity of the charger. 10 kW. | Elson Advocacy, Vehicle-to-Building/Grid Presentation for Ontario Energy Board Framework for Energy Innovation Working Group, July 2021 | Average LDV non-residential EV load profile | Final 2020 Transportation Electrification Forecast, ISO-NE, April 2020. | Estimated penetration of V2G based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging or discharge battery during peak hours. Provide upto 6 hours of curtailable load during the evening peak. | Vehicle to stop charging to provide demand reduction when called upon, or discharge battery to provide stand-by power to respond to OR signal. Assuming vehicle is plugged in and available 18 hours/day. | V2G acts as a battery, and therefore is able to provide frequency regulation services to the grid. Able to provide both regulation up and regulation down services. Batteries are able to respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | Can provide energy arbitrage, absorbing SBG and discharging back to the grid when energy is needed. Bidirectional control. Can provide up to 6 hours of load absorbtion. Assume discharge duration of 4 hours, and round trip efficiency of 85%. | Yes | Incremental equipment cost from upgrading to a bidirectional charger (from a dumb charger) | Internal Dunsky Measure Database | Additional O&M based on 5% of the hardware costs over the 10-year life of the charger | Plug'n Drive, EV Batteries and Ontario's Electric System Final Report July 2020 v2 | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | None | N/A | All commercial segments
| 19 | 8 | MDV Fleet EV Smart Chargers | Non-Residential Behind-the-Meter | EV Fleet Charging | Number of electric medium-duty fleet vehicles | Based on assumed market share projections (i.e. annual % sales) from other Canadian markets, applied to Ontario's vehicle fleet (NRCan CEUD - Transportation) | Forecasted electric medium-duty fleet adoption | APO with scenario adjustments | Nameplate capacity of the charger. 10 kW. | Elson Advocacy, Vehicle-to-Building/Grid Presentation for Ontario Energy Board Framework for Energy Innovation Working Group, July 2021 | Average MDV non-residential EV load profile | California Investor-Owned Utility Electricity Load Shapes, August 2020, with adjustments to reflect differences in weather patterns and corresponding seasonality impacts. | Estimated penetration of smart EV chargers based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging during peak hours. Provide up to 6 hours of interruption pushed later in the evening. | Vehicle to stop charging to provide demand reduction when called upon. Assuming vehicle is plugged in and available 18 hours/day. | V1G is able to provide regulation down services by charging the battery. Batteries can respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | EVs can be scheduled to absorb SBG when it is the highest. Can provide up to 6 hours of load absorption. Assume vehicle is plugged in 18 hours a day. | Yes | Incremental equipment cost from upgrading a dumb charger to a smart charger | Internal Dunsky Measure Database | No incremental O&M costs. | Typical Industry Assumption | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | Number of EVs in jurisdiction x % fleet MDV EVs x % with smart charging capabilities | Number of EVs - APO's EV adoption forecast. Share of fleet EV MDV vehicle - Internal Dunsky Database. Penetration of EV smart chargers - Internal Dunsky Database. | All large commercial segments
| 20 | 9 | MDV Fleet Vehicle-to-Grid (V2G) | Non-Residential Behind-the-Meter | EV Fleet Charging | Number of electric medium-duty fleet vehicles | Based on assumed market share projections (i.e. annual % sales) from other Canadian markets, applied to Ontario's vehicle fleet (NRCan CEUD - Transportation) | Forecasted electric medium-duty fleet adoption | APO with scenario adjustments | Nameplate capacity of the charger. 10 kW. | Elson Advocacy, Vehicle-to-Building/Grid Presentation for Ontario Energy Board Framework for Energy Innovation Working Group, July 2021 | Average MDV non-residential EV load profile | California Investor-Owned Utility Electricity Load Shapes, August 2020, with adjustments to reflect differences in weather patterns and corresponding seasonality impacts. | Estimated penetration of V2G based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging or discharge battery during peak hours. Provide upto 6 hours of curtailable load during the evening peak. | Vehicle to stop charging to provide demand reduction when called upon, or discharge battery to provide stand-by power to respond to OR signal. Assuming vehicle is plugged in and available 18 hours/day. | V2G acts as a battery, and therefore is able to provide frequency regulation services to the grid. Able to provide both regulation up and regulation down services. Batteries are able to respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | Can provide energy arbitrage, absorbing SBG and discharging back to the grid when energy is needed. Bidirectional control. Can provide up to 6 hours of load absorbtion. Assume discharge duration of 4 hours, and round trip efficiency of 85%. | Yes | Incremental equipment cost from upgrading to a bidirectional charger (from a dumb charger) | Internal Dunsky Measure Database | Additional O&M based on 5% of the hardware costs over the 10-year life of the charger | Plug'n Drive, EV Batteries and Ontario's Electric System Final Report July 2020 v2 | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | None | N/A | All large commercial segments
| 21 | 10 | HDV Fleet EV Smart Chargers | Non-Residential Behind-the-Meter | EV Fleet Charging | Number of electric heavy-duty fleet vehicles | Based on assumed market share projections (i.e. annual % sales) from other Canadian markets, applied to Ontario's vehicle fleet (NRCan CEUD - Transportation) | Forecasted electric heavy-duty fleet adoption | APO with scenario adjustments | Nameplate capacity of the charger. 50 kW. | Gladstein, Neandross & Associates (GNA), Electric Vehicle Charging Guidebook for Medium- and Heavy- Duty Commercial Fleets, 2019 | Average HDV non-residential EV load profile | California Investor-Owned Utility Electricity Load Shapes, August 2020, with adjustments to reflect differences in weather patterns and corresponding seasonality impacts. | Estimated penetration of smart EV chargers based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging during peak hours. Provide up to 6 hours of interruption pushed later in the evening. | Vehicle to stop charging to provide demand reduction when called upon. Assuming vehicle is plugged in and available 18 hours/day. | V1G is able to provide regulation down services by charging the battery. Batteries can respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | EVs can be scheduled to absorb SBG when it is the highest. Can provide up to 6 hours of load absorption. Assume vehicle is plugged in 18 hours a day. | Yes | Incremental equipment cost from upgrading a dumb charger to a smart charger | Internal Dunsky Measure Database | No incremental O&M costs. | Typical Industry Assumption | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | Number of EVs in jurisdiction x % fleet HDV EVs x % with smart charging capabilities | Number of EVs - APO's EV adoption forecast. Share of fleet EV HDV vehicle - Internal Dunsky Database. Penetration of EV smart chargers - Internal Dunsky Database. | All large commercial segments
| 22 | 11 | HDV Fleet Vehicle-to-Grid (V2G) | Non-Residential Behind-the-Meter | EV Fleet Charging | Number of electric heavy-duty fleet vehicles | Based on assumed market share projections (i.e. annual % sales) from other Canadian markets, applied to Ontario's vehicle fleet (NRCan CEUD - Transportation) | Forecasted electric heavy-duty fleet adoption | APO with scenario adjustments | Nameplate capacity of the charger. 50 kW. | Elson Advocacy, Vehicle-to-Building/Grid Presentation for Ontario Energy Board Framework for Energy Innovation Working Group, July 2021 | Average LDV non-residential EV load profile, adjusted to average HDV sizing | California Investor-Owned Utility Electricity Load Shapes, August 2020, with adjustments to reflect differences in weather patterns and corresponding seasonality impacts. | Estimated penetration of V2G based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging or discharge battery during peak hours. Provide upto 6 hours of curtailable load during the evening peak. | Vehicle to stop charging to provide demand reduction when called upon, or discharge battery to provide stand-by power to respond to OR signal. Assuming vehicle is plugged in and available 18 hours/day. | V2G acts as a battery, and therefore is able to provide frequency regulation services to the grid. Able to provide both regulation up and regulation down services. Batteries are able to respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | Can provide energy arbitrage, absorbing SBG and discharging back to the grid when energy is needed. Bidirectional control. Can provide up to 6 hours of load absorbtion. Assume discharge duration of 4 hours, and round trip efficiency of 85%. | Yes | Incremental equipment cost from upgrading to a bidirectional charger (from a dumb charger) | Internal Dunsky Measure Database | Charging facility annual maintenance cost (5% of equipment cost) | Ercan, T., M. Noori, Y. Zhao, and O. Tatari. 2016. “On the front lines of a sustainable transportation fleet: Applications of vehicle-to-grid technology for transit and school buses.” | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | None | N/A | All large commercial segments
| 23 | 12 | Off Road EVs Smart Chargers | Non-Residential Behind-the-Meter | EV Fleet Charging | Number of electric off-road vehicles | Based on assumed market share projections (i.e. annual % sales) from other Canadian markets, applied to Ontario's vehicle fleet (NRCan CEUD - Transportation) | Forecasted electric off-road vehicle adoption | APO with scenario adjustments | Nameplate capacity of the charger. 10 kW. | Gladstein, Neandross & Associates (GNA), Electric Vehicle Charging Guidebook for Medium- and Heavy- Duty Commercial Fleets, 2019 | Average LDV non-residential EV load profile, adjusted to average off-road EV sizing | Final 2020 Transportation Electrification Forecast, ISO-NE, April 2020. | Estimated penetration of smart EV chargers based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging during peak hours. Provide up to 6 hours of interruption pushed later in the evening. | Vehicle to stop charging to provide demand reduction when called upon. Assuming vehicle is plugged in and available 18 hours/day. | V1G is able to provide regulation down services by charging the battery. Batteries can respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | EVs can be scheduled to absorb SBG when it is the highest. Can provide up to 6 hours of load absorption. Assume vehicle is plugged in 18 hours a day. | Yes | Incremental equipment cost from upgrading a dumb charger to a smart charger | Internal Dunsky Measure Database | No incremental O&M costs. | Typical Industry Assumption | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | Number of EVs in jurisdiction x % off-road EVs x % with smart charging capabilities | Number of EVs - APO's EV adoption forecast. Share of off-road electric vehicle - Internal Dunsky Database. Penetration of EV smart chargers - Internal Dunsky Database. | All large commercial segments
| 24 | 13 | Buses: EV Smart Charging | Non-Residential Behind-the-Meter | EV Fleet Charging | Number of electric buses | Based on assumed market share projections (i.e. annual % sales) from other Canadian markets, applied to Ontario's vehicle fleet (NRCan CEUD - Transportation) | Forecasted electric bus adoption | APO with scenario adjustments | Nameplate capacity of the charger. 50 kW. | Gladstein, Neandross & Associates (GNA), Electric Vehicle Charging Guidebook for Medium- and Heavy- Duty Commercial Fleets, 2019 | Average bus EV load profile | California Investor-Owned Utility Electricity Load Shapes, August 2020 | Estimated penetration of smart EV chargers based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging during peak hours. Provide up to 6 hours of interruption pushed later in the evening. | Vehicle to stop charging to provide demand reduction when called upon. Assuming vehicle is plugged in and available 19.5 - 21 hours/day if school bus, 8 -12 hours if transit bus. | V1G is able to provide regulation down services by charging the battery. Batteries can respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 19.5 - 21 hours/day if school bus, 8 -12 hours if transit bus. | EVs can be scheduled to absorb SBG when it is the highest. Can provide up to 6 hours of load absorption. Assuming vehicle is plugged in and available 19.5 - 21 hours/day if school bus, 8 -12 hours if transit bus. | Yes | Incremental equipment cost from upgrading a dumb charger to a smart charger | Internal Dunsky Measure Database | No incremental O&M costs. | Typical Industry Assumption | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | Number of EVs in jurisdiction x % e-buses x % with smart charging capabilities | Number of EVs - APO's EV adoption forecast. Share of e-buses - Internal Dunsky Database. Penetration of EV smart chargers - Internal Dunsky Database. | Applicable customer segments (subject to data availability)
| 25 | 14 | Buses: Vehicle-to-Grid (V2G) | Non-Residential Behind-the-Meter | EV Fleet Charging | Number of electric buses | Based on assumed market share projections (i.e. annual % sales) from other Canadian markets, applied to Ontario's vehicle fleet (NRCan CEUD - Transportation) | Forecasted electric bus adoption | APO with scenario adjustments | Nameplate capacity of the charger. 50 kW. | Elson Advocacy, Vehicle-to-Building/Grid Presentation for Ontario Energy Board Framework for Energy Innovation Working Group, July 2021 | Average bus EV load profile | California Investor-Owned Utility Electricity Load Shapes, August 2020 | Estimated penetration of V2G based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging or discharge battery during peak hours. Provide upto 6 hours of curtailable load during the evening peak. | Vehicle to stop charging to provide demand reduction when called upon. Assuming vehicle is plugged in and available 19.5 - 21 hours/day if school bus, 8 -12 hours if transit bus. | V2G acts as a battery, and therefore is able to provide frequency regulation services to the grid. Able to provide both regulation up and regulation down services. Batteries are able to respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 19.5 - 21 hours/day if school bus, 8 -12 hours if transit bus | Can provide energy arbitrage, absorbing SBG and discharging back to the grid when energy is needed. Bidirectional control. Can provide up to 6 hours of load absorbtion. Assume discharge duration of 4 hours, and round trip efficiency of 85%. | Yes | Incremental equipment cost from upgrading to a bidirectional charger (from a dumb charger) | Internal Dunsky Measure Database | Charging facility annual maintenance cost (5% of equipment cost) | Ercan, T., M. Noori, Y. Zhao, and O. Tatari. 2016. “On the front lines of a sustainable transportation fleet: Applications of vehicle-to-grid technology for transit and school buses.” | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | None | N/A | Applicable customer segments (subject to data availability)
| 17 | 15 | LDV Fleet EV Telematics | Non-Residential Behind-the-Meter | EV Fleet Charging | Number of electric light-duty fleet vehicles with telematics | Number of EVs (APO's EV adoption forecast). Penetration of EVs with telematics (source TBD). Share of fleet EV LDV vehicle (Dunsky assumption) | Forecasted LDV fleet EV adoption with telematics | APO with scenario adjustments. Penetration of telematics control with EVs (TBD) | Nameplate capacity of the charger. 10 kW. | Plug'N Drive, EV Batteries Value Proposition for Ontario's Electricity Grid and EV Owners, July 2020 | Average LDV EV load profile | Final 2020 Transportation Electrification Forecast, ISO-NE, April 2020. | Estimated penetration of EV telematics based on market trends and high-level adoption model | Penetration of EVs with telematics - Berg Insight | N/A | N/A | Curtail charging during peak hours. Provide up to 6 hours of interruption pushed later in the evening. | Vehicle to stop charging to provide demand reduction when called upon. Assuming vehicle is plugged in and available 18 hours/day. | V1G is able to provide regulation down services by charging the battery. Batteries can respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | EVs can be scheduled to absorb SBG when it is the highest. Can provide up to 6 hours of load absorption. | Yes | No incremental costs. | N/A | No incremental O&M costs. | Typical Industry Assumption | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of vehicle (assumed to be 10 years) | Internal Dunsky Measure Database | None | Penetration of EVs with telematics, Berg Insight, assumed proportions of vehicle type from Dunsky Internal Database | All commercial segments
| 26 | 16 | Large Commercial HVAC Control | Non-Residential Behind-the-Meter | HVAC | Number of large Commercial buildings with a central AC system | Number of buildings per segment - APO. Penetration of central ACs - CEUS. | Follows population growth. | Population growth - APO. BAS control - APS. | Sized to cooling and pumps and ventilation load. Varies by segment. | APO end-use data | Direct use of the cooling and pumps & ventilation load for each segment | APO end-use data | Estimated penetration of HVAC controls in large Commercial based on market data and trends | High-level adoption modelling | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | The BAS system will reserve a portion of its load for dispatch into the OR market. The portion of the load reserved will be determined through a set point control or through reduction in cycles (50% or 100%). Since cycles last for 15 mins, a cycle curtailment can provide OR. | N/A | A certain % of pre cooling through set point control would shift a portion of the morning peak load to the hours when there is a surplus baseload generation. | No | Based on a BYOD approach. No installation cost. No incremental for new devices since customers will adopt BAS indepently of DR | N/A | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of the BAS system: 10 | Dunsky Internal Database | Number of large Commercial per segment X % with central air conditioning X % penetration of BAS | IESO CEUS and APO | All large commercial segments
| 27 | 17 | Small Commercial Smart Thermostat | Non-Residential Behind-the-Meter | HVAC | Number of small Commercial buildings with a central AC system | Number of buildings per segment - APO. Penetration of central ACs - CEUS. | Population growth with consideration of growth in AC adoption/penetration | AC growth - APO. Smart thermostat adoption - APS | Sized to cooling load. Varies by segment. | APO end-use data | Direct use of the cooling load each segment of the small Commercial sector | APO end-use data | Estimated penetration of smart thermostats in small Commercial based on market data and trends | Smart Thermostat Penetration from CEUS | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | The smart thermstat will reserve a portion of its load for dispatch into the OR market. The portion of the load reserved will be determined through a set point control or through reduction in cycles (50% or 100%). Since cycles last for 15 mins, a cycle curtailment can provide OR. | N/A | A certain % of pre cooling through set point control would shift a portion of the morning peak load to the hours when there is a surplus baseload generation. | Yes | Based on a BYOD approach. No installation cost. No incremental for new devices since customers are not buying smart thermostat for DR purposes (but for EE). | N/A | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of the smart thermostat: 10 | ACEEE, Smart Buildings: Using Smart Technology to Save Energy in Existing Buildings, February 2017 | Number of small Commercial per segment X % with central air conditioning X % penetration of smart thermostats | IESO CEUS and APO | All small commercial segments
| 46 | 18 | Small Commercial ASHP/DMSHP Smart Thermostat | Non-Residential Behind-the-Meter | HVAC | Number of small Commercial buildings with an ASHP/DMSHP | Number of buildings per segment - APO. Penetration of ASHP/DMSHP - CEUS. | Follows population growth. | Population growth - APO. | Sized to cooling load. Varies by segment. | APO end-use data | Cooling Load Profile | APO end-use data | Estimated penetration of ASHP/DMSHP with a smart thermostat in Commercial buildings based on market data and trends | Smart Thermostat Penetration - CEUS. Penetration of ASHP/DMSHP - CEUS. | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called no more than 12 times a year. | The smart thermstat will reserve a portion of its load for dispatch into the OR market. The portion of the load reserved will be determined through a set point control or through reduction in cycles (50% or 100%). Since cycles last for 15 mins, a cycle curtailment can provide OR. | N/A | A certain % of pre cooling through set point control would shift a portion of the morning peak load to the hours when there is a surplus baseload generation. | Yes | Based on a BYOD approach. No installation cost. No incremental for new devices since customers are not buying smart thermostat for DR purposes (but for EE). | N/A | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of the smart thermostat only: 10 | ACEEE - Smart Buildings: Using Smart Technology to Save Energy in Existing Buildings | Number of small Commercial per segment X % with ASHP/DMSHP | IESO CEUS and APO | All large commercial segments
| 28 | 19 | Lighting Controls | Non-Residential Behind-the-Meter | Lighting Controls | Number of non-residential buildings with lighting system | Number of buildings per segment - APO. | Follows population growth. | Population growth - APO. | Sized to lighting load. Varies by segment. | APO end-use data | Non-residential lighting loads | APO end-use data | Estimated penetration of lighting controls in non-residential buildings based on market data and trends | High-level adoption modelling | N/A | N/A | The lighting load is assumed to be dimmed by a set percentage (15%) during a capacity event. | 15% of hourly load reserved for OR | 8% of hourly load reserved for FR | N/A | Yes | Incremental costs for lighting controls | PacifiCorp, 2021 Integrated Resource Plan, Appendix H - Demand Response Detailed Assumptions | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | Lifespan of controls: 8 | California Municipal Utilities Association, Savings Estimation TRM 2017 | Number of non-residential buildings X % with BAS controls applied to lighting systems | IESO CEUS and APO | All commercial segments
| 30 | 20 | Other Commercial Flexibility | Non-Residential Behind-the-Meter | Other Load Flexibility | Number of Commercial facilities with processes and other curtailable loads | Number of buildings per segment - APO. Penetration of processes and other curtailable loads - CEUS | Follows population growth. | Population growth - APO. | Sized to commercial process/other loads. Varies by segment. | APO end-use data | Commercial load shape | APO end-use data | Estimated penetration of commercial facilities with process of curtailable loads that would participate in a demand response program based on market data and trends | High-level adoption modelling | N/A | N/A | Demand response action called upon during peak demand hours through notification or TOU rates | N/A | N/A | N/A | No | No incremental costs. | N/A | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | Program lifetime: 1 | Internal Dunsky Measure Database | Number of Commercial facilities x % with processes and other curtailable loads enrolled in a demand response program | IESO CEUS and APO | All industrial segments
| 31 | 21 | Irrigation Pump Controls | Non-Residential Behind-the-Meter | Other Load Flexibility | Number of farms with irrigation pumps | Number of farms - APO. Penetration of irrigating farms: Stats Canada. | Follows population growth. | Population growth - APO. | Sized to irrigtion pump load. | Regional Technical Forum - Northwest Power & Conservation Council, Demand Response for Irrigation Pumps, May 2019. 2020 Baseline DR Supply Curves - NPCC. | Irrigation load shape | APO end-use data | Estimated penetration of irrigation pump controls in agriculture based on market data and trends | High-level adoption modelling | N/A | N/A | Pumps turned off from 2-4 hours per event, total demand response is capped at 15 hours per week, and 60 per year. If peak of the season, only about 80% of the total potential irrigation load is actually on and available for DR at any given time. | N/A | N/A | N/A | No | Incremental cost for controls | Regional Technical Forum - Northwest Power & Conservation Council, Demand Response for Irrigation Pumps, May 2019 | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | Lifespan of controls: 10 | California Technical Forum, Agriculture / Pumping Subcommittee Meeting #1, August 2017 | Number of farms x % that irrigate x number of pumps per farm x % with controls | Number of farms - APO. Penetration of irrigating farms: Stats Canada. | Other commercial (agriculture)
| 29 | 22 | District Cooling/Heating Flexibility | Non-Residential Behind-the-Meter | Other Load Flexibility | Number of non-residential facilities connected to a district cooling/heating system | Number of buildings per segment - APO. Penetration of district heating/cooling - TBD | Follows population growth. | Population growth - APO. | Sized to non-residential cooling loads. Varies by segment. | APO end-use data | Non-residential cooling load | APO end-use data | Estimated penetration of district heating/cooling in non-residential buildings based on market data and trends | High-level adoption modelling | N/A | N/A | TBD | N/A | N/A | N/A | Yes | No incremental costs. | N/A | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | Lifespan of district heating/cooling system: 25 | The Opportunities Of Changing From Oil Heating To District Heating | Number of non-residential facilities connected to a district cooling/heating system | Number of buildings per segment - APO. Penetration of district heating/cooling - TBD | All commercial segments
| 32 | 23 | Refrigeration Controls | Non-Residential Behind-the-Meter | Other Load Flexibility | Number of non-residential buildings with refrigeration equipment | Number of buildings per segment - APO. Penetration of refrigeration equipment - CEUS. | Follows population growth. | Population growth - APO. | Sized to refrigeration loads. Varies by segment. | EPRI | EPRI Load shape, matched to refrigeration end-use. | EPRI | Estimated penetration of refrigeration controls in non-residential buildings based on market data and trends | High-level adoption modelling | N/A | N/A | Able to shed load of around 10 kW in the most effective DR tests | N/A | N/A | N/A | No | Incremental cost for refrigeration controls | Internal Dunsky Measure Database | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | Lifespan of controls: 9 | Internal Dunsky Measure Database | Existing share of controls applied to commercial refrigeration systems | IESO CEUS and APO | Food retail, Warehouse
| 33 | 24 | Greenhouses: Grow Lights | Non-Residential Behind-the-Meter | Other Load Flexibility | Number of greenhouses with growlights | Number of greenhouses - APO. Penetration of grow lights - CEUS. | Follows population growth. | Population growth - APO. | Sized to grow light loads. | DormGrow, How much will it cost to run LED grow lights? May 2021 | Average grow lights load profile | Greenhouse Energy Profile Study, IESO, September 2019. | Estimated penetration of grow light controls in greenhouses based on market data and trends | High-level adoption modelling | N/A | N/A | Shortened operation time/curtailed load | N/A | N/A | N/A | No | Incremental cost for controls | PacifiCorp, 2021 Integrated Resource Plan, Appendix H - Demand Response Detailed Assumptions | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | Lifespan of controls: 8 | California Municipal Utilities Association, Savings Estimation TRM 2017 | Average number of growlights in a greenhouse x % with controls x number of greenhouses | IESO CEUS and APO | Other commercial (greenhouses)
| 48 | 25 | Industrial Flexibility | Non-Residential Behind-the-Meter | Other Load Flexibility | Number of Industrial facilities with curtailable load | Number of buildings per segment - APO. Penetration of curtailable loads - DERs Industrial Survey | Follows population growth. | Population growth - APO. | Sized to total building loads. Varies by segment. | APO end-use data | Industrial load shapes | APO end-use data | Estimated penetration of industrial facilities with curtailable loads that would participate in a demand response program based on market data and trends | High-level adoption modelling | N/A | N/A | Demand response action called upon during peak demand hours through notification or TOU rates | N/A | N/A | N/A | No | No incremental costs. | N/A | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | Program lifetime: 1 | Internal Dunsky Measure Database | Number of Industrial facilities x % with curtailable loads enrolled in a demand response program | IESO CEUS and APO | All industrial segments
| 37 | 26 | BTM Battery Storage Non Residential | Non-Residential Behind-the-Meter | Storage | Number of Class A, Non-RPP Class B and Small Commercial Customers with space for a standalone energy storage system | Number of buildings per segment - APO. Share of building with sufficient space for standalone storage - ConEdison DER potential study. | Follows population growth. | Population growth - APO. | Analysis of publicly available data from storage vendors and the US DOE’s Global Energy Storage Database. Small Business customers: 5 kW/ 20 kWh Non-RPP Class B customers: 1 MW/ 4 MWh Class A customers: 2.5 MW/ 5 MWh. | OEB DER Impact Study Appendix C | N/A | N/A | Detailed market adoption modeling for each scenario | Detailed adoption modelling | Sized to typical system sizing practices | Net-metering interconnection data | Sustained capacity reduction during peak hours as per dispatch instructions | Average capacity reserved for OR provision as per dispatch instructions | Ramp up/down provision based on min(headroom/footroom) | Peak to Off-Peak shifting and charge during SBG hours as per dispatch instructions. Derated by charging and discharging losses. | Yes | Upfront Capex costs | OEB DER Impact Study | Typical system maintenace (% of CAPEX) | NREL ATB Baseline Study | Costs are expected to decrease | BNEF. NREL ATB | Warantied Life of BTM ES : 10 | Technical Specifications BTM Energy Storage Products | Current Baseline: 50 MW 10% of currently installed NEM storage capacity was assigned to the small business sector, 20% of the storage capacity currently enrolled in the IAM’s was assigned to non-RPP Class B customers, 80% of the storage capacity enrolled in the IAM’s and 400 MW of BTM storage capacity was assigned to Class A customers | OEB DER Impact Study | All commercial segments
| 39 | 27 | Commercial HVAC Thermal Storage | Non-Residential Behind-the-Meter | Thermal Storage | Number of Non-Residential Customers | Number of buildings per segment - APO. | Follows population growth. | Population growth - APO. | Sized to cooling load. Varies by segment. | Cooling Load Profile | Cooling Load Profile | APO end-use data | Estimated penetration of HVAC thermal storage in commercial facilities based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | 6 hours of peak demand to off-peak. On-peak demand reductions of up to 14 kW. | OR Provision will be sized to the electrical component that can be shed | N/A | Peak to Off-Peak shifting and charge during SBG hours as per dispatch instructions | Yes | Cost of TES | NREL, Space Conditioning Tech Team Webinar: Thermal Energy Storage, the lowest cost storage. | Minimal O&M | Typical Industry Assumption | Costs are expected to decrease | NREL ATB Projections | Warantied Life of Thermal ES systems: 10 | Internal Dunsky Measure Database | Number of commercial buildings x % with thermal storage for HVAC | IESO CEUS and APO | All large commercial segments
| 40 | 28 | Thermal Storage for Refrigeration Applications | Non-Residential Behind-the-Meter | Thermal Storage | Number of non-residential buildings with refrigeration systems | Number of buildings per segment - APO. Penetration of refrigeration equipment - CEUS. | Follows population growth. | Population growth - APO. | Power Rating of refrigeration appliance. Varies by segment. | Technical Reference Manuals - Ontario | Refrigeration Load Profile | APO end-use data | Estimated penetration of thermal storage for refrigeration applications in commercial facilities based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Shift 85% of load up to 6.5 hours | OR Provision will be sized to the electrical component that can be shed | FR Provision is Min ( FR Footroom, FR Headroom) FR Footroom: Available hourly dispatchable energy minus 10% of the device power rating. FR Headroom: 90% Device Power Rating minus (baseload consumption) | Pre-cooling thermal storage during SBG hours | Yes | Cost of TES | Viking Cold Energy Storage Solutions | Minimal O&M | Typical Industry Assumption | Costs are expected to decrease | NREL ATB Projections | Warantied Life of Thermal ES systems: 10 | Internal Dunsky Measure Database | Number of non-residential buildings X % with thermal storage for refrigeration applications | IESO CEUS and APO | Food retail, Warehouse
| 42 | 29 | Large Commercial Dual-Fuel Water Heating | Non-Residential Behind-the-Meter | Water Heating | Number of large Commercial buildings with dual-fuel water heating | Number of buildings per segment - APO. Penetration of dual-fuel water heating - CEUS. | Follows population growth. | Population growth - APO. | Power Rating of a Large Commercial DFWH. Varies by segment. | Technical Reference Manuals - Ontario | Average Large Commercial WH Load Profile | APO end-use data | Estimated penetration of dual-fuel water heating in large Commercial buildings based on market data and trends | High-level adoption modelling | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | N/A | N/A | Shift a portion of the morning peak load to SBG hours by preheating system | Yes | Incremental Cost of Controls, Compliance and Fuel Costs | TBD | Maintainence Costs, Fuel Costs | Typical Industry Assumption | N/A | N/A | EUL of DFWH: 5 | Internal Dunsky Measure Database | Number of Large Commercial Customers X % penetration of dual fuel water heaters | IESO's CEUS IpSOS for penetration and saturation of electric water heater. | All large commercial segments
| 43 | 30 | Large Commercial Hot Water | Non-Residential Behind-the-Meter | Water Heating | Number of large Commercial buildings with an electric hot water system | Number of buildings per segment - APO. Penetration of electric hot water system - CEUS. | Follows population growth. | Population growth - APO. | Power Rating of a Large Commercial WH. Varies by segment. | Technical Reference Manuals - Ontario | Average Large Commercial WH Load Profile | APO end-use data | Estimated penetration of controls for hot water heating in large Commercial buildings based on market data and trends | High-level adoption modelling | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | Footroom that will be reserved for OR: Available hourly dispatchable energy minus 10% of the device power rating. This is to ensure that the device has sufficient energy available for OR. | FR Provision is Min ( FR Footroom, FR Headroom). FR Footroom: Available hourly dispatchable energy minus 10% of the device power rating. FR Headroom: 90% Device Power Rating minus (baseload consumption) | Shift a portion of the morning peak load to SBG hours by preheating system | Yes | Incremental Cost of Smart Switch | PacifiCorp, 2021 Integrated Resource Plan, Appendix H - Demand Response Detailed Assumptions | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of ERWH: 5 | Internal Dunsky Measure Database | Number of Large Commercial Customers X % penetration of electric water heaters | IESO's CEUS IpSOS for penetration and saturation of electric water heater. | All large commercial segments
| 44 | 31 | Small Commercial Hot Water | Non-Residential Behind-the-Meter | Water Heating | Number of small Commercial buildings with an electric hot water system | Number of buildings per segment - APO. Penetration of electric hot water system - CEUS. | Follows population growth. | Population growth - APO. | Power Rating of a Small Commercial WH. Varies by segment. | Technical Reference Manuals - Ontario | Average Small Commercial WH Load Profile | APO end-use data | Estimated penetration of small Commercial electric hot water based on market data and trends | High-level adoption modelling | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | Footroom that will be reserved for OR: Available hourly dispatchable energy minus 10% of the device power rating. This is to ensure that the device has sufficient energy available for OR. | FR Provision is Min ( FR Footroom, FR Headroom). FR Footroom: Available hourly dispatchable energy minus 10% of the device power rating. FR Headroom: 90% Device Power Rating minus (baseload consumption) | Shift a portion of the morning peak load to SBG hours by preheating system | Yes | Incremental Cost of Set Point Controls | PacifiCorp, 2021 Integrated Resource Plan, Appendix H - Demand Response Detailed Assumptions | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of ERWH: 5 | Internal Dunsky Measure Database | Number of Small Commercial Customers X % penetration of electric water heaters | IESO's CEUS IpSOS for penetration and saturation of electric water heater. | All small commercial segments
| 49 | 32 | Res. BTM Solar with Smart Inverters | Residential Behind-the-Meter | Distributed Generation | Number of buildings with a rooftop suitable for solar deployment | IESO Solar PV Potential Study | Rate of growth / new construction by segment | Population growth - APO. | Maximum size of system that can be theoretically deployed based on roof size and typical panel footprint | IESO Solar APS Study | Ontario-Average Generation Profile | IESO Solar APS Study | Detailed market adoption modeling for each scenario | Detailed adoption modelling | Sized to typical system sizing practices | Net-metering interconnection data | Median of the daily average generation during summer capacity hours | N/A | N/A | Hourly Generation x Hourly Avoided Energy Costs | Yes | BTM Solar Upfront Costs | OEB DER Impact Study | Maintainence and Inverter Replacement Costs for Solar will be gathered from reports | NREL ATB Baseline Study | Costs are expected to decrease | NREL ATB Baseline Study | EUL of BTM solar: 30 | Typical Industry Assumption | Current Baseline: 234.6MW Distributed solar FIT as well as Net Metering were used for determining the capacity and number of installs in the baseline year. | OEB DER Impact Study Appendix C | Single Family Home, Rowhouse
| 51 | 33 | AC Thermostat | Residential Behind-the-Meter | HVAC | Number of residential buildings with a central AC system | Number of buildings per segment - APO. Penetration of central ACs - REUS. | Population growth with consideration of growth in AC adoption/penetration | AC growth - APO. Smart thermostat adoption - APS | Sized to cooling and pumps and ventilation load. Varies by segment. | APO end-use data | Direct use of the cooling and pumps & ventilation load for each segment | APO end-use data | Estimated penetration of smart thermostats in residential buildings with central AC based on market data and trends | Smart Thermostat Penetration from REUS | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | The smart thermstat will reserve a portion of its load for dispatch into the OR market. The portion of the load reserved will be determined through a set point control or through reduction in cycles (50% or 100%). Since cycles last for 15 mins, a cycle curtailment can provide OR. | N/A | A certain % of pre cooling through set point control would shift a portion of the morning peak load to the hours when there is a surplus baseload generation. | Yes | Based on a BYOD approach. No installation cost. No incremental for new devices since customers are not buying smart thermostat for DR purposes (but for EE). | N/A | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of the smart thermostat only: 10 | ACEEE - Smart Buildings: Using Smart Technology to Save Energy in Existing Buildings | Number of households X % with central air conditioning X % penetration of smart thermostats | IESO REUS and APO | Applies to all residential segments
| 53 | 34 | Dual-Fuel Space Heating Smart Thermostat | Residential Behind-the-Meter | HVAC | Number of residential buildings with dual-fuel space heating systems (natural gas and electric) | Number of buildings per segment - APO. Penetration of dual-fuel space heating systems - REUS. | TBD | TBD | Sized to electric heating load. Varies by segment. | APO end-use data | Direct use of electric heating load each segment of residential sector | APO end-use data | Estimated penetration of smart thermostats for dual-fuel heating systems in residential buildings based on market data and trends | High-level adoption modelling | N/A | N/A | Called 4 hours max, shut off and rely on gas heat. Called not more than 12 times a year. | N/A | N/A | N/A | No | Based on a BYOD approach. No installation cost. No incremental for new devices since customers are not buying smart thermostat for DR purposes (but for EE). | N/A | Maintainence Costs, Fuel Costs | Typical Industry Assumption | N/A | N/A | EUL of the smart thermostat: 5 | Internal Dunsky Measure Database | Households with dual-fuel space heating systems (natural gas and electric) x penetration of smart thermostats | IESO REUS and APO | All residential segments
| 54 | 35 | Dual-Fuel Space Heating Smart Switch | Residential Behind-the-Meter | HVAC | Number of residential buildings with dual-fuel space heating systems (natural gas and electric) | Number of buildings per segment - APO. Penetration of dual-fuel space heating systems - REUS. | TBD | TBD | Sized to electric heating load. Varies by segment. | APO end-use data | Direct use of electric heating load each segment of residential sector | APO end-use data | Estimated penetration of smart switches for dual-fuel heating systems in residential buildings based on market data and trends | High-level adoption modelling | N/A | N/A | Called 4 hours max, shut off and rely on gas heat. Called not more than 12 times a year. | N/A | N/A | N/A | No | Cost of smart switch, Compliance and Fuel Costs | Internal Dunsky Measure Database | Maintainence Costs, Fuel Costs | Typical Industry Assumption | N/A | N/A | EUL of the smart switch: 5 | Internal Dunsky Measure Database | Households with dual-fuel space heating systems (natural gas and electric) x penetration of smart switches | IESO REUS and APO | All residential segments
| 80 | 36 | ASHP/DMSHP Smart Thermostat | Residential Behind-the-Meter | HVAC | Number of residential homes per segment with ASHP/DMSHP | Number of buildings per segment - APO. Penetration of ASHP/DMSHP - REUS. | Follows population growth. | APO with scenario adjustments | Sized to cooling load. Varies by segment. | APO end-use data | Cooling Load Profile | APO end-use data | Estimated penetration of ASHP/DMSHP with a smart thermostat in residential buildings based on market data and trends | Smart Thermostat Penetration - REUS. Penetration of ASHP/DMSHP - REUS. | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | The smart thermstat will reserve a portion of its load for dispatch into the OR market. The portion of the load reserved will be determined through a set point control or through reduction in cycles (50% or 100%). Since cycles last for 15 mins, a cycle curtailment can provide OR. | N/A | A certain % of pre cooling through set point control would shift a portion of the morning peak load to the hours when there is a surplus baseload generation. | Yes | Based on a BYOD approach. No installation cost. No incremental for new devices since customers are not buying smart thermostat for DR purposes (but for EE). | N/A | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of the smart thermostat only: 10 | ACEEE - Smart Buildings: Using Smart Technology to Save Energy in Existing Buildings | Number of Residential homes per segment X % with ASHP/DMSHP | IESO REUS and APO | All residential segments
| 56 | 37 | Other Behavioral-based Residential Flexibility | Residential Behind-the-Meter | Other Load Flexibility | Number of residential buildings | Number of buildings per segment - APO. | Follows population growth. | Population growth - APO. | Sized to residential plug loads. Varies by segment. | APO end-use data | SF home load shape | APO end-use data | Estimated penetration of residential facilities that would participate in a demand response program based on market data and trends | N/A | N/A | N/A | Demand response action called upon during peak demand hours through notification or TOU rates | N/A | N/A | Shift to SBG hours by delaying (or moving to an earlier time) the load. | No | No incremental costs. | N/A | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | Program lifetime: 1 | Internal Dunsky Measure Database | Existing residential buildings enrolled in demand response program | IESO REUS and APO | All residential segments
| 57 | 38 | Smart EV Chargers | Residential Behind-the-Meter | Passenger EV Charging | Number of electric passenger vehicles | Number of EVs - APO's EV adoption forecast. Share of passenger electric vehicle (Dunsky Assumption) | Forecasted passenger EV adoption | APO with scenario adjustments | Nameplate capacity of the charger. 6.6 kW. | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Average passenger EV load profile | Final 2020 Transportation Electrification Forecast, ISO-NE, April 2020. | Estimated penetration of smart EV chargers based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging during peak hours. Provide up to 6 hours of interruption pushed later in the evening. | Vehicle to stop charging to provide demand reduction when called upon. Assuming vehicle is plugged in and available 18 hours/day. | V1G is able to provide regulation down services by charging the battery. Batteries can respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | EVs can be scheduled to absorb SBG when it is the highest. Can provide up to 6 hours of load absorption. Assume vehicle is plugged in 18 hours a day. | Yes | Incremental equipment cost from upgrading a dumb charger to a smart charger | Internal Dunsky Measure Database | No incremental O&M costs. | Typical Industry Assumption | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | Number of EVs in jurisdiction x % passenger EVs x percentage of EVs with smart chargers | Number of EVs - APO's EV adoption forecast. Share of passenger vehicle - Internal Dunsky Database. Penetration of EV smart chargers - Internal Dunsky Database. | Single Family Home, Rowhouse
| 60 | 39 | Vehicle-to-Grid (V2G) | Residential Behind-the-Meter | Passenger EV Charging | Number of electric passenger vehicles | Number of EVs - APO's EV adoption forecast. Share of passenger electric vehicle (Dunsky Assumption) | Forecasted passenger EV adoption | APO with scenario adjustments | Nameplate capacity of the charger. 6.6 kW. | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Average passenger EV load profile | Final 2020 Transportation Electrification Forecast, ISO-NE, April 2020. | Estimated penetration of V2G based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Curtail charging or discharge battery during peak hours. Provide upto 6 hours of curtailable load during the evening peak. | Vehicle to stop charging to provide demand reduction when called upon, or discharge battery to provide stand-by power to respond to OR signal. Assuming vehicle is plugged in and available 18 hours/day. | V2G acts as a battery, and therefore is able to provide frequency regulation services to the grid. Able to provide both regulation up and regulation down services. Batteries are able to respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | Can provide energy arbitrage, absorbing SBG and discharging back to the grid when energy is needed. Bidirectional control. Can provide up to 6 hours of load absorbtion. Assume discharge duration of 4 hours, and round trip efficiency of 85%. | Yes | Incremental equipment cost from upgrading to a bidirectional charger (from a dumb charger) | Internal Dunsky Measure Database | Additional O&M based on 5% of the hardware costs over the 10-year life of the charger | Plug'n Drive, EV Batteries and Ontario's Electric System Final Report July 2020 v2 | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of EV charger: 10 | Internal Dunsky Measure Database | None | N/A | Single Family Home, Rowhouse
| 59 | 40 | Passenger EV Telematics | Residential Behind-the-Meter | Passenger EV Charging | Number of electric passenger vehicles with telematics | Number of EVs (APO's EV adoption forecast). Penetration of EVs with telematics (source TBD). Share of fleet EV LDV vehicle (Dunsky assumption) | Forecasted passenger EV adoption with telematics. | APO with scenario adjustments. Penetration of telematics control with EVs (TBD) | Nameplate capacity of the charger. 6.6 kW. | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Average passenger EV load profile | Final 2020 Transportation Electrification Forecast, ISO-NE, April 2020. | Estimated penetration of EV telematics based on market trends and high-level adoption model | Penetration of EVs with telematics - Berg Insight | N/A | N/A | Curtail charging during peak hours. Provide up to 6 hours of interruption pushed later in the evening. | Vehicle to stop charging to provide demand reduction when called upon. Assuming vehicle is plugged in and available 18 hours/day. | V1G is able to provide regulation down services by charging the battery. Batteries can respond to signals from the grid almost instantaneously. Assuming vehicle is plugged in and available 18 hours/day | EVs can be scheduled to absorb SBG when it is the highest. Can provide up to 6 hours of load absorption. | Yes | No incremental costs. | N/A | No incremental O&M costs. | Typical Industry Assumption | Costs are expected to decrease | The International Council on Clean Transportation, Estimating Electric Vehicle Charging Infrastructure Costs across Major U.S. Metropolitan Areas, August 2019 | Lifespan of vehicle (assumed to be 10 years) | Internal Dunsky Measure Database | None | Penetration of EVs with telematics, Berg Insight, assumed proportions of vehicle type from Dunsky Internal Database | Single Family Home, Rowhouse
| 81 | 41 | Res. Pool Pumps | Residential Behind-the-Meter | Pools and Spas | Number of residential homes with a pool pump | Number of buildings per segment - APO. Penetration of electric pool pumps - REUS. | Follows population growth. | Population growth - APO. | Power Rating of a Residential Pool Pump 1 to 1.5 kW. | Technical Reference Manuals - Ontario | Pool Pump Load Profile | APO end-use data | Estimated penetration of pool pumps in residential facilities based on market data and trends | High-level adoption modelling | N/A | N/A | Average hourly dispatchable load that is sustained within the capacity hours | N/A | N/A | N/A | No | Incremental Cost of Smart Controls | Internal Dunsky Measure Database | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | Lifespan of controls: 5 | Internal Dunsky Measure Database | Number of Residential homes per segment X % penetration of pool pumps | IESO REUS and APO | All residential segments
| 68 | 42 | Smart Clothes Dryer | Residential Behind-the-Meter | Smart Appliances | Number of residential buildings with a clothes dryer | Number of buildings per segment - APO. Penetration of clothes dryers - REUS. | Forecasted smart clothes dryer adoption. | Population growth - APO. Smart appliance growth - Statista, Smart Appliances, United States. | Clothes dryer load. | APO end use data | Average clothes dryer load profile | APO end use data | Estimated penetration of smart clothes dryers based on market data and trends | Smart Device Penetration from REUS | N/A | N/A | Reduce energy through control strategies. 100% of load curtailed. | N/A | N/A | Shift to SBG hours by delaying (or moving to an earlier time) the load. | Yes | Based on a BYOD approach. No installation cost. No incremental for new devices since customers are not buying smart clothes dryers for DR purposes. | N/A | No incremental O&M costs. | Typical Industry Assumption | Costs are expected to decrease | IEA, A Call to Action on Efficient and Smart Appliances, October 2021 | Lifespan of smart clothes dryer: 14 | NYSERDA, Appendix P: Effective Useful Life Tables, December 2019 | Number of residential buildings with an internet enabled clothes dryer | IESO REUS and APO | All residential segments
| 71 | 43 | BTM Battery Storage Residential | Residential Behind-the-Meter | Storage | Number of residential buildings with space for a standalone energy storage system | Number of buildings per segment - APO. Share of building with sufficient space for standalone storage - ConEdison DER potential study. | Follows population growth. | Population growth - APO. | Analysis of publicly available data from storage vendors and the US DOE’s Global Energy Storage Database. 5 kW. | OEB DER Impact Study Appendix C | N/A | N/A | Detailed market adoption modeling for each scenario | Detailed adoption modelling | Sized to typical system sizing practices | Net-metering interconnection data | Sustained capacity reduction during peak hours as per dispatch instructions | Average capacity reserved for OR provision as per dispatch instructions | Ramp up/down provision based on min(headroom/footroom) | Peak to Off-Peak shifting and charge during SBG hours as per dispatch instructions. Derated by charging and discharging losses. | Yes | Upfront Capex costs | OEB DER Impact Study | Typical system maintenace (% of CAPEX) | NREL ATB Baseline Study | Costs are expected to decrease | BNEF. NREL ATB | Warantied Life of BTM ES : 10 | Technical Specifications BTM Energy Storage Products | Current Baseline: 5 MW 90% of currently installed NEM storage capacity was assigned to the residential sector | OEB DER Impact Study | All residential segments
| 73 | 44 | Thermal Storage for Cooling | Residential Behind-the-Meter | Thermal Storage | Number of residential buildings with central air conditionning | Number of buildings per segment - APO. Penetration of central ACs - REUS. | Population growth with consideration of growth in AC adoption/penetration | Population growth - APO. | Power Rating of Air Conditioner | Cooling Load Profile | Cooling Load Profile | APO end-use data | Estimated penetration of thermal storage for cooling in residential facilities based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Complete Cooling Load Dispatch During Capacity Hours | OR Provision will be sized to the electrical component that can be shed | FR Provision is Min ( FR Footroom, FR Headroom) FR Footroom: Available hourly dispatchable energy minus 10% of the device power rating. FR Headroom: 90% Device Power Rating minus (baseload consumption) | Pre-cooling thermal storage during SBG hours | Yes | Cost of TES | Internal Dunsky Measure Database | Minimal O&M | Typical Industry Assumption | Costs are expected to decrease | NREL ATB Projections | Warantied Life of Thermal ES systems: 10 | Internal Dunsky Measure Database | Existing share of thermal storage for cooling applications (remove heat pumps) | IESO REUS and APO | All residential segments
| 74 | 45 | Thermal Storage and Heat Pump | Residential Behind-the-Meter | Thermal Storage | Number of residential buildings centrally cooled without a heat pump | Number of buildings per segment - APO. Penetration of central-ducted heat pumps: REUS. | Follows population growth. | Population growth - APO. | Power Rating of Heat Pump | Cooling Load Profile | Cooling Load Profile | APO end-use data | Estimated penetration of thermal storage and heat pump in residential facilities based on market trends and high-level adoption model | High-level adoption modelling | Sized to typical system sizing practices | TBD | Complete Cooling Load Dispatch During Capacity Hours | OR Provision will be sized to the electrical component that can be shed | FR Provision is Min ( FR Footroom, FR Headroom) FR Footroom: Available hourly dispatchable energy minus 10% of the device power rating. FR Headroom: 90% Device Power Rating minus (baseload consumption) | Pre-cooling thermal storage during SBG hours | Yes | Cost of TES | Stash Energy | Minimal O&M | Typical Industry Assumption | Costs are expected to decrease | NREL ATB Projections | Warantied Life of Thermal ES systems: 10 | Internal Dunsky Measure Database | Existing share of thermal storage and heat pump systems | IESO REUS and APO | All residential segments
| 72 | 46 | Thermal Storage for Heating | Residential Behind-the-Meter | Thermal Storage | Number of residential buildings with central heating | Number of buildings per segment - APO. Penetration of central-heating: REUS. | Follows population growth. | Population growth - APO. | Power Rating of Heat System | Heating Load Profile | Heating Load Profile | APO end-use data | Estimated penetration of thermal storage for heating in residential facilities based on market trends and high-level adoption model | High-level adoption modelling | N/A | N/A | Complete Heating Load Dispatch During Capacity Hours | OR Provision will be sized to the electrical component that can be shed | FR Provision is Min ( FR Footroom, FR Headroom) FR Footroom: Available hourly dispatchable energy minus 10% of the device power rating. FR Headroom: 90% Device Power Rating minus (baseload consumption) | Pre-heating thermal storage during SBG hours | Yes | Cost of TES | TBD | Minimal O&M | Typical Industry Assumption | Costs are expected to decrease | NREL ATB Projections | Warantied Life of Thermal ES systems: 10 | Internal Dunsky Measure Database | Existing share of thermal storage and central heating systems | IESO REUS and APO | All residential segments
| 76 | 47 | Electric Resistance Water Heaters Smart Switch | Residential Behind-the-Meter | Water Heating | Number of residential buildings with an electric resistance water heater | Number of buildings per segment - APO. Penetration of electric resistance water heaters - REUS. | Follows population growth. | Population growth - APO. | Power Rating of a Residential ERWH. | Technical Reference Manuals - Ontario | Average Residential ERWH Load Profile | APO end-use data | Estimated penetration of electric resistance water heaters with a smart switch based on market data and trends | High-level adoption modelling | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | Footroom that will be reserved for OR: Available hourly dispatchable energy minus 10% of the device power rating. This is to ensure that the device has sufficient energy available for OR. | FR Provision is Min ( FR Footroom, FR Headroom). FR Footroom: Available hourly dispatchable energy minus 10% of the device power rating. FR Headroom: 90% Device Power Rating minus (baseload consumption) | Shift a portion of the morning peak load to SBG hours by preheating system | Yes | Incremental Cost of Smart Switch | PacifiCorp, 2021 Integrated Resource Plan, Appendix H - Demand Response Detailed Assumptions | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of Smart Switch: 9 | Internal Dunsky Measure Database | Number of Residential homes per segment X % penetration of Electric resistance water heaters X (1- % internet enabled) | IESO's REUS for penetration and saturation of electric water heater. APO for # of building per segment. | All residential segments
| 77 | 48 | Heat Pump Water Heater Smart Switch | Residential Behind-the-Meter | Water Heating | Number of residential buildings with a heat pump water heater | Number of buildings per segment - APO. Penetration of heat pump water heaters - REUS. | Follows population growth. | Population growth - APO. | Power Rating of a Residential HPWH. | Technical Reference Manuals - Ontario | Average Residential HPWH Load Profile | APO end-use data | Estimated penetration of heat pump water heaters with a smart switch based on market data and trends | High-level adoption modelling | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | N/A | N/A | Shift a portion of the morning peak load to SBG hours by preheating system | Yes | Incremental Cost of Smart Switch | PacifiCorp, 2021 Integrated Resource Plan, Appendix H - Demand Response Detailed Assumptions | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of Smart Switch: 9 | Internal Dunsky Measure Database | Number of Residential homes per segment X % penetration of heat pump water heaters X (1- % internet enabled) | IESO's REUS for penetration and saturation of heat pump water heater. APO for # of building per segment. | All residential segments
| 78 | 49 | Smart Electric Resistance Water Heaters | Residential Behind-the-Meter | Water Heating | Number of residential buildings with a electric resistance water heater | Number of buildings per segment - APO. Penetration of smart electric resistance water heaters - REUS. | Follows population growth. | Population growth - APO. | Power Rating of a Residential ERWH. | Technical Reference Manuals - Ontario | Average Residential ERWH Load Profile | APO end-use data | Estimated penetration of smart electric resistance water heaters based on market data and high-level adoption modelling | High-level adoption modelling | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | Footroom that will be reserved for OR: Available hourly dispatchable energy minus 10% of the device power rating. This is to ensure that the device has sufficient energy available for OR. | FR Provision is Min ( FR Footroom, FR Headroom). FR Footroom: Available hourly dispatchable energy minus 10% of the device power rating. FR Headroom: 90% Device Power Rating minus (baseload consumption) | Shift a portion of the morning peak load to SBG hours by preheating system | Yes | Incremental Cost of Smart Appliance over conventional device | PacifiCorp, 2021 Integrated Resource Plan, Appendix H - Demand Response Detailed Assumptions | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of ERWH: 5 | Internal Dunsky Measure Database | Number of Residential homes per segment X % penetration of eletric resistance water heaters X % internet enabled | IESO's REUS for penetration and saturation of electric water heater. | All residential segments
| 79 | 50 | Smart Heat Pump Water Heaters | Residential Behind-the-Meter | Water Heating | Number of residential buildings with a smart heat pump water heater | Number of buildings per segment - APO. Penetration of heat pump water heater - REUS. | Forecasted heat pump water heater adoption. | APO with scenario adjustments. Penetration of telematics control with EVs (TBD) | Sized to the domestic hot water load. Varies by segment. | APO end-use data | Direct use of the domestic hot water load for each segment | APO end-use data | Estimated penetration of smart heat pump water heaters based on market data and trends | High-level adoption modelling | N/A | N/A | Called 4 hours max, with Precooling and rebound. Called not more than 12 times a year. | N/A | N/A | Shift a portion of the morning peak load to SBG hours by preheating system | Yes | Incremental Cost of Smart Appliance over conventional device | PacifiCorp, 2021 Integrated Resource Plan, Appendix H - Demand Response Detailed Assumptions | No incremental O&M costs. | Typical Industry Assumption | N/A | N/A | EUL of HPWH: 5 | Internal Dunsky Measure Database | Number of Residential Customers with HPWH that are internet enabled | IESO's REUS for penetration and saturation of heat pump water heater. APO for # of building per segment. | All residential segments