## Read Me
Load Shift Measure Input Assumptions
The following tabs contain load shift measures measures organized by sector and application.
Thermal Energy Storage (TES) Measures Include:
Sector | TES Type/Application | Load Shift Impact
Residential | Thermal Water Storage Heat Pump | Summer and Winter
Commercial | Thermal PCM Ice-water Storage HVAC Cooling | Summer
Commercial | Thermal PCM Saltwater-Ice Storage Refrigeration | Summer
Industrial | Thermal PCM Ice-water Storage HVAC Cooling | Summer
Industrial | Thermal Sensible Storage Process Heat | Summer and Winter
PCM = Phase Change Material

## Residential Thermal HP
Product: | Thermal Water Storage
Sector: | Residential
Description/Eligibility | Air-to-Water Heat Pump (Heating and Cooling) System
Measure Assumptions | [5 empty] | Application Assumptions
Parameter Group | Parameter | Unit Definition | Value | Source/Note | Stakeholder Feedback | Application | End Use | Load Shift | Participation Assumption | Stakeholder Feedback
End Use Savings | Summer Demand Savings (Peak Load Shift) | % kW reduction | 49% | Metered pilot project. Load shift 28% to 66% summer end-use load over 2- to 4- hour period. Based on Technical Evaluation of Air-to-Water Heat Pumps with Thermal Storage, CALNEXT report ET22SWE0050. Prepared by VEIC April 2025. Benchmarked saving of 25% total demand building load (~50% end-use load) "Role of Thermal Energy Storage in Reducing Peak Load from Building Electrification" Navius 2025 report for Natural Resources Canada. |  | Residential sector and segments | Air-to-water heat pump | Summer and winter season: remove load from peak periods. Shift space heating and cooling load to off-peak hours. Shifted load is redistributed to off peak hours of that day. | Program participation (a participant can opt at the time of equipment replacement) that has the eligible equipment. Considered as emerging technology adoption rate (slow). Adoption dependent on incentive costs to overcome high upfront costs. Benchmark utilities frequently pair rebates with participation in time of use programs.
End Use Savings | Winter Demand Savings (Peak Load Shift) | % kW reduction | 54.75% | Load shift 17% to 82% winter load over 2- to 4- hour period. Based on Technical Evaluation of Air-to-Water Heat Pumps with Thermal Storage, CALNEXT report ET22SWE0050. Prepared by VEIC April 2025.
End Use Savings | Energy Savings | % kWh savings | 0% | Assume no energy savings. Based on Technical Evaluation of Air-to-Water Heat Pumps with Thermal Storage, CALNEXT report ET22SWE0050. Prepared by VEIC April 2025.
Measure Life | Measure Life | EUL | 15 | Based on Technical Evaluation of Air-to-Water Heat Pumps with Thermal Storage, CALNEXT report ET22SWE0050. Prepared by VEIC April 2025.
Customer Incremental Cost | Equipment Cost (Incremental cost) | $/kW | 2774.6336 | Assume 5 kW system. Based on Technical Evaluation of Air-to-Water Heat Pumps with Thermal Storage, CALNEXT report ET22SWE0050. Prepared by VEIC April 2025. Assumes equipment and labor (80% equipment/20% labor). |  |  |  |  | 0
Customer Incremental Cost | Labor Cost (Incremental cost) | $/kW | 693.6584 | Assume 5 kW system. Based on Technical Evaluation of Air-to-Water Heat Pumps with Thermal Storage, CALNEXT report ET22SWE0050. Prepared by VEIC April 2025. Assumes equipment and labor (80% equipment/20% labor).
Customer Incentive | Incentive | $/kW | 3468.292 | Assume that significantly more incentive is needed to move the market, assume 100% of incremental cost consistent with the IESO energy efficiency program APO modeling.
Program Administration Cost | Program Admin | % of incentive | 20% | Estimated

## Commercial Thermal Cool
Product: | Thermal Storage (Ice-water phase change storage)
Sector: | Commercial
Description/Eligibility | Cooling
Measure Assumptions | [5 empty] | Application Assumptions
Parameter Group | Parameter | Unit Definition | Value | Source/Note | Stakeholder Feedback | Application | End Use | Load Shift | Participation Assumption | Stakeholder Feedback
End Use Savings | Demand Savings (Peak Load Shift) | % kW reduction | 75% | Inferred from NLR building simulations and research. NLR, Space Conditioning Tech Team Webinar: Thermal Energy Storage, the lowest cost storage. |  | Commercial sector and segments | Cooling | Summer seasons: Load-shifting measure; transferring cooling system energy use from afternoon peak hours to night-time operation using cooler outside air and store within ice/water system. Provides both energy and demand savings. | Program participation typically installed during equipment replace cycles. Considered as commercially available systems with a low adoption rate. Adoption dependent on incentive costs to overcome high upfront costs. Benchmark utilities frequently pair rebates with participation in time of use programs.
End Use Savings | Energy Savings | % kWh savings | 20% | Based on NLR building simulations and research. NLR, Space Conditioning Tech Team Webinar: Thermal Energy Storage, the lowest cost storage.
Measure Life | Measure Life | EUL | 20 | Assume consistent EUL as baseline equipment (Chiller IESO MSS)
Customer Incremental Cost | Equipment Cost (Incremental cost) | $/kW | 1184 | Inferred from NLR building simulations and research. NLR, Space Conditioning Tech Team Webinar: Thermal Energy Storage, the lowest cost storage. Cost per $1660/kW or $275/kWh (full system). Assumes equipment and labor (80% equipment/20% labor). Base equipment (Chillers > 300 tons (centrifugal) ~$180/kW (Northeast Energy Efficiency Partnerships. Incremental Cost Study Phase Two Final Report)
Customer Incremental Cost | Labor Cost (Incremental cost) | $/kW | 296 | Inferred from NLR building simulations and research. NLR, Space Conditioning Tech Team Webinar: Thermal Energy Storage, the lowest cost storage. Cost per $1660/kW or $275/kWh (full system). Assumes equipment and labor (80% equipment/20% labor). Base equipment (Chillers > 300 tons (centrifugal) ~$180/kW (Northeast Energy Efficiency Partnerships. Incremental Cost Study Phase Two Final Report)
Customer Incentive | Incentive | $/kW | 1480 | Assume 100% of incremental cost consistent with the IESO energy efficiency program APO modeling. Other programs provide 10% of project total costs.
Program Administration Cost | Program Admin | % of incentive | 20% | Estimated

## Commercial Thermal Refrig
Product: | Thermal Storage (Salt-water ice phase change storage)
Sector: | Commercial
Description/Eligibility | Refrigeration
Measure Assumptions | [5 empty] | Application Assumptions
Parameter Group | Parameter | Unit Definition | Value | Source/Note | Stakeholder Feedback | Application | End Use | Load Shift | Participation Assumption | Stakeholder Feedback
End Use Savings | Demand Savings (Peak Load Shift) | % kW reduction | 9.636% | SDGE Grocery Store Thermal Energy Storage Retrofit Study, 2021 EM&V report. Emerging Technologies Program. Prepared by: Tsosie Reyhner, PE kW Engineering. Internal project number DR16SDGE0002 |  | Commercial sector and segments (grocery) | Refrigeration | Summer and winter seasons: Load-shifting measure; transferring refrigation system energy use from afternoon peak hours to night time operation using cooler outside air and store within ice/salt water system. | Considered as commercial available systems with a low adoption rate. Installation can occur as a retorfit application or add-on to new equipment replacement. Adoption dependent on incentive costs to overcome high upfront costs. Benchmark utilities frequently pair rebates with participation in time of use programs.
End Use Savings | Energy Savings | % kWh savings | -2.027% | SDGE Grocery Store Thermal Energy Storage Retrofit Study, 2021 EM&V report. Emerging Technologies Program. Prepared by: Tsosie Reyhner, PE kW Engineering. Internal project number DR16SDGE0002
Measure Life | Measure Life | EUL | 20 | Assume consistent EUL as baseline equipment (Chiller IESO MSS)
Customer Incremental Cost | Equipment Cost (Full replacement cost) | $/kW | 72 | SDGE Grocery Store Thermal Energy Storage Retrofit Study, 2021 EM&V report. Emerging Technologies Program. Prepared by: Tsosie Reyhner, PE kW Engineering. Internal project number DR16SDGE0002. Assumes full cost of equipment and labor (80% equipment/20% labor). Refrigeration system size 250kW.
Customer Incremental Cost | Labor Cost (Full replacement cost) | $/kW | 18 | SDGE Grocery Store Thermal Energy Storage Retrofit Study, 2021 EM&V report. Emerging Technologies Program. Prepared by: Tsosie Reyhner, PE kW Engineering. Internal project number DR16SDGE0002. Assumes full cost of equipment and labor (80% equipment/20% labor). Refrigeration system size 250kW.
Customer Incentive | Incentive | $/kW | 360 | Assumes 100% of incremental cost.
Program Administration Cost | Program Admin | % of incentive | 20% | Estimated

## Industrial Thermal Cool
Product: | Thermal Storage (Ice-water phase change storage)
Sector: | Industrial
Description/Eligibility | Cooling/Refrigeration
Measure Assumptions | [5 empty] | Application Assumptions
Parameter Group | Parameter | Unit Definition | Value | Source/Note | Stakeholder Feedback | Application | End Use | Load Shift | Participation Assumption | Stakeholder Feedback
End Use Savings | Demand Savings (Peak Load Shift) | % kW reduction | 75% | Inferred from NLR building simulations and research. NLR, Space Conditioning Tech Team Webinar: Thermal Energy Storage, the lowest cost storage. |  | Industrial sector and segments | Cooling/Refrigeration | Summer seasons: Load-shifting measure; transferring cooling system energy use from afternoon peak hours to night time operation using cooler outside air and store within ice/water system. Provides both energy and demand savings. | Program participation typically installed during equipment replace cycles. Considered as commercial available systems with a low adoption rate. Adoption dependent on incentive costs to overcome high upfront costs. Benchmark utilities frequently pair rebates with participation in time of use programs.
End Use Savings | Energy Savings | % kWh savings | 20% | Based on NLR building simulations and research. NLR, Space Conditioning Tech Team Webinar: Thermal Energy Storage, the lowest cost storage.
Measure Life | Measure Life | EUL | 20 | Assume consistent EUL as baseline equipment (Chiller IESO MSS)
Customer Incremental Cost | Equipment Cost (Incremental cost) | $/kW | 1184 | Inferred from NLR building simulations and research. NLR, Space Conditioning Tech Team Webinar: Thermal Energy Storage, the lowest cost storage. Cost per $1660/kW or $275/kWh (full system). Assumes equipment and labor (80% equipment/20% labor). Base equipment (Chillers > 300 tons (centrifugal) ~$180/kW (Northeast Energy Efficiency Partnerships. Incremental Cost Study Phase Two Final Report)
Customer Incremental Cost | Labor Cost (Incremental cost) | $/kW | 296 | Inferred from NLR building simulations and research. NLR, Space Conditioning Tech Team Webinar: Thermal Energy Storage, the lowest cost storage. Cost per $1660/kW or $275/kWh (full system). Assumes equipment and labor (80% equipment/20% labor). Base equipment (Chillers > 300 tons (centrifugal) ~$180/kW (Northeast Energy Efficiency Partnerships. Incremental Cost Study Phase Two Final Report)
Customer Incentive | Incentive | $/kW | 1480 | Assume 100% of incremental cost consistent with the IESO energy efficiency program APO modeling. Other programs provide 10% of project total costs.
Program Administration Cost | Program Admin | % of incentive | 20% | Estimated

## Industrial Thermal Process Heat
Product: | Thermal Sensible Storage (solid or liquid material)
Sector: | Industrial
Description/Eligibility | Sensible Heat Storage System for Industrial Electric Boilers and Other Process Heating Devices
Measure Assumptions | [5 empty] | Application Assumptions
Parameter Group | Parameter | Unit Definition | Value | Source/Note | Stakeholder Feedback | Application | End Use | Load Shift | Participation Assumption | Stakeholder Feedback
End Use Savings | Demand Savings (Peak Load Shift) | % kW reduction | 40% | Industrial scale. 2022 Industrial Thermal Energy Storage report by European Energy Research Alliance (Energy Efficiency in Industrial Processes) |  | Industrial Sector | Current industrial heating processes using electricity | Summer and winter seasons: Shift process heating load to off-peak hours. Shifted load is redistributed to off peak hours of that day (pre-heating). | Barriers remain for high temperature applications. Assume Sensible Heat Thermal Energy Storage for low to med temperature applications (least costly). Program participation (a participant can opt into a program at any time) that has the eligible equipment. Considered as emerging technology adoption rate (slow). Adoption dependent on incentive costs to overcome high upfront costs. Benchmark utilities frequently pair rebates with a minimum reduction during on peak hours, and provide a rebate incentive to customers.
End Use Savings | Energy Savings | % kWh savings | -50% | Requires energy for the storage process. Varies sources range from 60% to 40% in round-trip efficiency. Assume an efficiency value in the middle of this range.
Measure Life | Measure Life | EUL | 25 | Assumed consistent with molten salt thermal energy storage system, deployed at scale.
Customer Incremental Cost | Equipment Cost (Full replacement cost) | $/kWh (delivered) | 12.8 | Average sensible TES costs - range from less than $1.6 to $35 per kWh delivered. 2022 Industrial Thermal Energy Storage report by European Energy Research Alliance (Energy Efficiency in Industrial Processes). Assumes equipment and labor (80% equipment/20% labor). Benchmarked with Development of Energy Storage: Cost models 2021 (Argonne National Laboratory)
Customer Incremental Cost | Labor Cost (Full replacement cost) | $/kWh (delivered) | 3.2 | Average sensible TES costs - range from less than $1.6 to $35 per kWh delivered. 2022 Industrial Thermal Energy Storage report by European Energy Research Alliance (Energy Efficiency in Industrial Processes). Assumes equipment and labor (80% equipment/20% labor). Benchmarked with Development of Energy Storage: Cost models 2021 (Argonne National Laboratory)
Customer Incentive | Incentive | $/kWh (delivered) | 16 | Assume 100% of incremental cost consistent with maximum potential approach. (Not proposed program design)
Program Administration Cost | Program Admin | % of incentive | 20% | Estimated