## Menu
Annual Planning Outlook
Supply, Adequacy and Energy Outlook Module Data
December 2022
Chapter 1: Supply Outlook
Figure 1: 2023 Installed Capacity
Figure 2: Summer and Winter Capacity Contribution
Chapter 2: Capacity Adequacy Outlook
Figure 3: Planning Reserve for Nuclear Refurbishment, Summer
Figure 4: Planning Reserve for Nuclear Refurbishment, Winter
Table 1: Summer LOLE Allocation
Table 2: Winter LOLE Allocation
Figure 5: Impact of 2022 APO LOLE allocation vs. Long-Run Assumption, Summer
Figure 6: Impact of 2022 APO LOLE allocation vs. Long-Run Assumption, Winter
Table 3: Incremental Summer Zonal Constraints, Scenario 1 without the 2022 AAR forward guidance CA targets (MW)
Table 4: Incremental Winter Zonal Constraints, Scenario 1 without the 2022 AAR forward guidance CA targets (MW)
Table 5: Zones and Defining Interfaces
Table 6: Transmission Transfer Capabilities (2024-2043)
Chapter 3: Energy Adequacy Outlook
Table 7: Henry Hub, Dawn Natural Gas Prices and Exchange Rate

## Figure 1
Back to main menu
Figure 1: 2023 Installed Capacity (MW)
Category | Installed Capacity
Transmission Connected Resources | 37425
Distribution Connected Resources | 3729
Back to main menu

## Figure 3
Back to main menu
Figure 3: Planning Reserve for Nuclear Refurbishment, Summer (MW)
Scenario | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043
2022 APO | 184 | 179 | 101 | 131 | 124 | 64 | 66 | 829 | 68 | 30 | 68 | 30 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
Back to main menu

## Figure 2
Back to main menu
Figure 2: Summer and Winter Capacity Contribution (%)
Fuel Type | Summer Capacity Contribution Factor | Winter Capacity Contribution Factor
Nuclear | 95% | 95%
Hydroelectric | 70% | 77%
Wind | 13% | 30%
Solar | 27% | 0%
Bioenergy | 95% | 95%
Gas/Oil | 95% | 95%
Demand Response | 69% | 78%
Dispatchable Load | 56% | 95%
Back to main menu

## Figure 4
Back to main menu
Figure 4: Planning Reserve for Nuclear Refurbishment, Winter (MW)
Scenario | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2031/2032 | 2032/2033 | 2033/2034 | 2034/2035 | 2035/2036 | 2036/2037 | 2037/2038 | 2038/2039 | 2039/2040 | 2040/2041 | 2041/2042 | 2042/2043
2022 APO | 113 | 120 | 153 | 841 | 86 | 91 | 48 | 68 | 30 | 68 | 30 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
Back to main menu

## Table 1
Back to main menu
Table 1: Summer LOLE Allocation (days/year)
Scenario | 2024 | 2025 | 2026 | 2027-2043
Target LOLE | 0.09 | 0.09 | 0.09 | 0.06
Back to main menu

## Table 2
Back to main menu
Table 1: Winter LOLE Allocation (days/year)
Scenario | 2024/2025 | 2025/2026 | 2026/2027 | 2027/2028 - 2042/2043
Target LOLE | 0.01 | 0.01 | 0.01 | 0.04
Back to main menu

## Figure 5
Back to main menu
Figure 5: Impact of 2022 APO LOLE allocation vs. Long-Run Assumption, Summer (MW)
Scenario | 2024 | 2025 | 2026
2022 APO - 0.09 | 878 | 669 | -1023
2022 APO - 0.06 | 613 | 477 | -1238
Back to main menu

## Figure 6
Back to main menu
Figure 6: Impact of 2022 APO LOLE allocation vs. Long-Run Assumption, Winter (MW)
Scenario | 2024/2025 | 2025/2026 | 2026/2027
2022 APO - 0.01 | 2038 | 130 | -910
2022 APO - 0.04 | 2415 | 472 | -451
Back to main menu

## Table 3
Back to main menu
Table 3: Incremental Summer Zonal Constraints, Scenario 1 without the 2022 AAR forward guidance CA targets (MW)
| 2024 |  | 2025 |  | 2026
Zone | Min | Max | Min | Max | Min | Max
Bruce | 0 | N/A | 0 | N/A | 0 | N/A
East | 0 | N/A | 0 | N/A | 0 | N/A
Essa | 0 | N/A | 0 | N/A | 0 | N/A
Niagara | 0 | 1000 | 0 | 1050 | 0 | 1100
Northeast | 0 | 50 | 0 | 50 | 0 | 50
Northwest | 0 | 50 | 0 | 50 | 0 | 50
Ottawa | 0 | N/A | 0 | N/A | 0 | N/A
Southwest | 0 | N/A | 0 | 2300 | 0 | 1800
Toronto | 0 | N/A | 0 | N/A | 0 | N/A
West | 0 | 600 | 0 | 750 | 0 | 450
Toronto+Essa+East+Ottawa | 0 | N/A | 0 | N/A | 0 | N/A
Northeast+Northwest | 0 | 50 | 0 | 50 | 0 | 50
Back to main menu

## Table 4
Back to main menu
Table 4: Incremental Winter Zonal Constraints, Scenario 1 without the 2022 AAR forward guidance CA targets (MW)
| 2024-25 |  | 2025-26
Zone | Min | Max | Min | Max
Bruce | 0 | N/A | 0 | N/A
East | 0 | N/A | 0 | N/A
Essa | 0 | N/A | 0 | N/A
Niagara | 0 | 900 | 0 | 850
Northeast | 0 | 250 | 0 | 100
Northwest | 0 | 250 | 0 | 250
Ottawa | 0 | N/A | 0 | N/A
Southwest | 0 | 500 | 0 | N/A
Toronto | 0 | N/A | 0 | N/A
West | 0 | 600 | 0 | 750
Toronto+Essa+East+Ottawa | 0 | N/A | 0 | N/A
Northeast+Northwest | 0 | 250 | 0 | 100
Back to main menu

## Table 5
Back to main menu
Table 5: Zones and Defining Interfaces
Area | Interface
Bruce | FABC
Niagara | QFW
Northwest | E-W
West | BLIP
Toronto+Essa+East+Ottawa | FETT, FN/FS
Northeast+Northwest | E-W, FN/FS
Back to main menu

## Table 6
Back to main menu
Table 6: Transmission Transfer Capabilities (2024-2043)
Interface | Positive Direction Interface Transfer Capability (MW) | Negative Direction Interface Transfer Capability (MW)
E-W | 500 | 350
FABC | 9999 | 9999
BLIP | Ranges from 2,020 to 3,700 | Ranges from 570 to 1,550
QFW | 2400 | 9999
FETT | Ranges from 4,700 to 7,350 | 9999
TEC | 9999 | 9999
FIO | 2950 | 9999
FN/FS | 1850 | 1750
CLAN | 9999 | 9999
Back to main menu

## Table 7
Back to main menu
Table 7: Henry Hub, Dawn Natural Gas Prices and Exchange Rate
Year | Henry Hub ($USD/MMBtu) | USD/CAD Exchange Rate | Dawn ($CAD/MMbtu)
2024 and onward | 3.12 | 0.8 | 3.75
Back to main menu