## Menu
Reliability Outlook - Tables
2026-03-18
2026 Q1 Outlook
From April 2026 – September 2027
1.0 Demand Forecast: First 18 Months
Table 1.1 Firm: Historical and Forecast Energy Summary
Table 1.1 Planned: Historical and Forecast Energy Summary
Table 1.1.1 Firm: Monthly Peak and Energy Demand
Table 1.1.1 Planned: Monthly Peak and Energy Demand | NOTE(S):
Table 1.1.2 Firm: Weekly Coincident Peak Demand by Zone
Table 1.1.2 Planned: Weekly Coincident Peak Demand by Zone | 1. Demand Forecast, Supply Forecast, and Transmission Outlook Considerations
Table 1.1.3 Firm: Weekly Energy Demand by Zone | a) The demand models use actual demand, weather, and economic data through the end of December 2025. The latest business intelligence regarding large step loads was incorporated in mid‑February. Actual weather and demand data for January and February 2026, which were observed after demand modeling, are also included in the tables for informational purposes.
Table 1.1.3 Planned: Weekly Energy Demand by Zone
Table 1.2 Firm: Forecasted Seasonal Peaks
Table 1.2 Planned: Forecasted Seasonal Peaks | b) This Reliability Outlook includes planned generator outages over the 18‑month period, submitted by market participants to the IESO’s outage management system by early to mid‑March 2026.
Table 1.3: Large Step Load Impacts, Firm and Planned Demand
Table 1.4 Firm: Weekly Energy and Peak Demand Forecast | c) This Reliability Outlook includes planned transmission outages that were submitted to the IESO’s outage management system by February 2026.
Table 1.4 Planned: Weekly Energy and Peak Demand Forecast
Table 1.4.1: Weekly Weather and Demand History
Table 1.4.2: Monthly Weather and Demand History | 2. As of the Q4 2025 Reliability Outlook the section numbers have changed as shown below:
Table 1.4.3: Monthly Consumption by Market Participant Type
Table 1.4.4: Economic Assumptions | Pre-Q4 2025 -> Q4 2025 onwards
Table 1.4.5: Estimate of Contracted Embedded Generation Capacity (MW) | Section 3.0 -> Section 1.0
Section 4.0 -> Section 2.0
2.0 Resource Supply Forecast: First 18 Months | Section 5.0 and Appendix A -> Section 3.0
Table 2.1: Existing Grid-Connected Resource Capacity | Appendix B and Appendix C -> Section 4.0
Table 2.2: Committed Generation and Electricity Storage Resources Status over the 18-month Reliability Outlook Period
Table 2.3: Monthly Historical Hydroelectric Median Values for Expected Weather Conditions
Table 2.4: Monthly Wind Capacity Contribution Values
Table 2.5: Monthly Solar Capacity Contribution Values
Table 2.6: Monthly Off-Peak Wind Capacity Contribution Values
Table 2.7: Summary of Available Resources under Expected Weather
3.0 Resource Adequacy Assessment: First 18 Months
Table 3.1 Firm: Summary of Zonal Energy for Firm Scenario, Expected Weather
Table 3.2 Planned: Summary of Zonal Energy for Planned Scenario, Expected Weather
Table 3.3 Firm: Ontario Energy Production by Fuel Type for the Firm Scenario, Expected Weather
Table 3.4 Planned: Ontario Energy Production by Fuel Type for the Planned Scenario, Expected Weather
Table 3.5: Assessment of Resource Adequacy: Expected Weather, Firm Scenario
Table 3.6: Assessment of Resource Adequacy: Expected Weather, Planned Scenario
Table 3.7: Zonal Bottled Generation: Expected Weather, Both Scenarios
Table 3.8: Energy Production Capability Forecast
Table 3.9: Reductions by Fuel Type: Expected Weather, Firm Scenario
Table 3.10: Firm Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Table 3.11: Planned Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
4.0 Transmission
Table 4.1: Transmission Projects
Table 4.2: Interface Limits with All Elements in Service
Table 4.3: Interconnection Flow Limits
Table 4.4: Bruce Zone Transmission Outages
Table 4.5: East Zone Transmission Outages
Table 4.6: Essa Zone Transmission Outages
Table 4.7: Niagara Zone Transmission Outages
Table 4.8: Northeast Zone Transmission Outages
Table 4.9: Northwest Zone Transmission Outages
Table 4.10: Ottawa Zone Transmission Outages
Table 4.11: Southwest Zone Transmission Outages
Table 4.12: Toronto Zone Transmission Outages
Table 4.13: West Zone Transmission Outages
Table 4.14: External Interties Transmission Outages

## Table 1.1 Firm
Back to main menu
Table 1.1 Firm: Historical and Forecast Energy Summary
Year | Normal Weather Energy (TWh) | % Growth in Energy
2006 | 152.349 | -1.858%
2007 | 151.6029 | -0.4897%
2008 | 148.9203 | -1.769%
2009 | 140.59 | -5.594%
2010 | 141.7415 | 0.819%
2011 | 141.0103 | -0.5158%
2012 | 140.7232 | -0.2036%
2013 | 140.4483 | -0.1954%
2014 | 139.4864 | -0.6848%
2015 | 136.3504 | -2.248%
2016 | 135.9259 | -0.3113%
2017 | 132.1965 | -2.744%
2018 | 135.5109 | 2.507%
2019 | 134.6666 | -0.6231%
2020 | 131.9143 | -2.044%
2021 | 133.7042 | 1.357%
2022 | 136.6504 | 2.204%
2023 | 138.0378 | 1.015%
2024 | 141.0947 | 2.215%
2025 | 145.3951 | 3.048%
2026 (Forecast) | 146.7568 | 0.9366%
2027 (Forecast) | 148.1358 | 0.9396%
Back to main menu

## Table 1.1 Planned
Back to main menu
Table 1.1 Planned: Historical and Forecast Energy Summary
Year | Normal Weather Energy (TWh) | % Growth in Energy
2006 | 152.349 | -1.858%
2007 | 151.6029 | -0.4897%
2008 | 148.9203 | -1.769%
2009 | 140.59 | -5.594%
2010 | 141.7415 | 0.819%
2011 | 141.0103 | -0.5158%
2012 | 140.7232 | -0.2036%
2013 | 140.4483 | -0.1954%
2014 | 139.4864 | -0.6848%
2015 | 136.3504 | -2.248%
2016 | 135.9259 | -0.3113%
2017 | 132.1965 | -2.744%
2018 | 135.5109 | 2.507%
2019 | 134.6666 | -0.6231%
2020 | 131.9143 | -2.044%
2021 | 133.7042 | 1.357%
2022 | 136.6504 | 2.204%
2023 | 138.0378 | 1.015%
2024 | 141.0947 | 2.215%
2025 | 145.3951 | 3.048%
2026 (Forecast) | 146.7568 | 0.9366%
2027 (Forecast) | 148.777 | 1.377%
Back to main menu

## Table 1.1.1 Firm
Back to main menu
Table 1.1.1 Firm: Monthly Peak and Energy Demand
Forecasted Peak and Energy Demand
| Peak Demand (MW) |  |  | Energy Demand (GWh)
Month | Current Forecast | Previous Forecast | Weather Corrected Actual | Current Forecast | Previous Forecast | Weather Corrected Actual
2012-01-01 | 22160.0997 | 22160.0997 | 22084.7322 | 13280.0235 | 13280.0235 | 12932.2873
2012-02-01 | 21813.8691 | 21813.8691 | 20756.8677 | 12202.5791 | 12202.5791 | 11380.2015
2012-03-01 | 20708.9072 | 20708.9072 | 20595.0545 | 12264.8125 | 12264.8125 | 11726.1779
2012-04-01 | 18745.092 | 18745.092 | 19830.1533 | 10866.5786 | 10866.5786 | 10883.4994
2012-05-01 | 19038.2309 | 19038.2309 | 19736.9901 | 10943.6824 | 10943.6824 | 10838.5019
2012-06-01 | 22569.1521 | 22569.1521 | 22832.4909 | 11398.2442 | 11398.2442 | 11511.081
2012-07-01 | 23298.1422 | 23298.1422 | 23630.2664 | 12319.3311 | 12319.3311 | 13057.6199
2012-08-01 | 22956.5741 | 22956.5741 | 22726.501 | 12419.0386 | 12419.0386 | 12373.2613
2012-09-01 | 20506.0631 | 20506.0631 | 20370.1157 | 10811.3017 | 10811.3017 | 10900.4102
2012-10-01 | 18345.9037 | 18345.9037 | 18684.153 | 11199.8353 | 11199.8353 | 11149.8822
2012-11-01 | 20571.5606 | 20571.5606 | 20258.2258 | 11629.6439 | 11629.6439 | 11663.449
2012-12-01 | 21693.287 | 21693.287 | 20910.8981 | 12612.0073 | 12612.0073 | 12306.8289
2012 | 23298.1422 | 23298.1422 | 23630.2664 | 141947.0782 | 141947.0782 | 140723.2004
2013-01-31 | 22013.997 | 22013.997 | 22610 | 13314.3055 | 13314.3055 | 13061.0693
2013-02-28 | 21773.6201 | 21773.6201 | 21333.0082 | 11819.7381 | 11819.7381 | 11668.8474
2013-03-31 | 20634.9497 | 20634.9497 | 20784.4526 | 12283.0437 | 12283.0437 | 11869.9986
2013-04-30 | 18492.3312 | 18492.3312 | 19284.8182 | 11018.1303 | 11018.1303 | 11090.2932
2013-05-31 | 19100.9692 | 19100.9692 | 18341.9804 | 10932.3105 | 10932.3105 | 10533.5712
2013-06-30 | 22499.2459 | 22499.2459 | 22719.4401 | 11406.4319 | 11406.4319 | 11283.4325
2013-07-31 | 23212.9348 | 23212.9348 | 24352.1456 | 12479.5529 | 12479.5529 | 12736.3503
2013-08-31 | 22359.7987 | 22359.7987 | 23255.371 | 12227.7513 | 12227.7513 | 12084.9413
2013-09-30 | 20513.3592 | 20513.3592 | 20422.3176 | 11015.3041 | 11015.3041 | 10767.0057
2013-10-31 | 18388.3002 | 18388.3002 | 18981.007 | 11279.1846 | 11279.1846 | 11114.0467
2013-11-30 | 20326.4941 | 20326.4941 | 20034.8189 | 11686.9287 | 11686.9287 | 11709.7788
2013-12-31 | 21395.0558 | 21395.0558 | 21184.5386 | 12699.9803 | 12699.9803 | 12528.9266
2013 | 23212.9348 | 23212.9348 | 24352.1456 | 142162.6617 | 142162.6617 | 140448.2614
2014-01-31 | 22319.8106 | 22319.8106 | 22043.8439 | 13356.427 | 13356.427 | 13409.7767
2014-02-28 | 20964.0592 | 20964.0592 | 21218.2216 | 11748.3799 | 11748.3799 | 11812.9441
2014-03-31 | 19906 | 19906 | 20728.4579 | 12054.5719 | 12054.5719 | 12242.1563
2014-04-30 | 17649 | 17649 | 19249.9632 | 10731.1367 | 10731.1367 | 11038.5265
2014-05-31 | 18964 | 18964 | 18750.4605 | 10790.2174 | 10790.2174 | 10546.4252
2014-06-30 | 22469.55 | 22469.55 | 20705.1957 | 11346.2756 | 11346.2756 | 11140.5499
2014-07-31 | 22948.69 | 22948.69 | 22294.8035 | 12360.0815 | 12360.0815 | 12324.9268
2014-08-31 | 21403.44 | 21403.44 | 21644.3547 | 11992.5131 | 11992.5131 | 11819.2371
2014-09-30 | 19023.2704 | 19023.2704 | 19449.0766 | 10579.5258 | 10579.5258 | 10671.4853
2014-10-31 | 18638.7361 | 18638.7361 | 18447.2196 | 11126.7565 | 11126.7565 | 10814.1957
2014-11-30 | 20302.34 | 20302.34 | 19923.2587 | 11497.4835 | 11497.4835 | 11410.1121
2014-12-31 | 21237.74 | 21237.74 | 21582.6701 | 12769.4956 | 12769.4956 | 12256.0958
2014 | 22948.69 | 22948.69 | 22294.8035 | 140352.8643 | 140352.8643 | 139486.4317
2015-01-31 | 22293.59 | 22293.59 | 21503.4489 | 13068.9431 | 13068.9431 | 12937.1182
2015-02-28 | 21016.81 | 21016.81 | 19709.6284 | 11528.5197 | 11528.5197 | 11740.7311
2015-03-31 | 19840.93 | 19840.93 | 20109.8817 | 11856.8161 | 11856.8161 | 11748.227
2015-04-30 | 18121.2 | 18121.2 | 19362.8308 | 10542.0267 | 10542.0267 | 10624.618
2015-05-31 | 19370.33 | 19370.33 | 17881.7583 | 10635.9243 | 10635.9243 | 10231.5964
2015-06-30 | 22276.64 | 22276.64 | 20554.6293 | 11410.2692 | 11410.2692 | 10908.724
2015-07-31 | 22888.49 | 22888.49 | 22638.5319 | 12174.2184 | 12174.2184 | 12273.6405
2015-08-31 | 21463.69 | 21463.69 | 22383 | 11821.2763 | 11821.2763 | 11782.7212
2015-09-30 | 18485 | 18485 | 19299.6325 | 10512.648 | 10512.648 | 10718.9879
2015-10-31 | 18339 | 18339 | 18444.3181 | 11150.1256 | 11150.1256 | 10731.7474
2015-11-30 | 20306 | 20306 | 19631.9089 | 11595.0899 | 11595.0899 | 10867.5486
2015-12-31 | 21160.04 | 21160.04 | 20418.0801 | 12611.2501 | 12611.2501 | 11784.7123
2015 | 22888.49 | 22888.49 | 22638.5319 | 138907.1073 | 138907.1073 | 136350.3725
2016-01-31 | 22360.24 | 22360.24 | 21249.7402 | 12982.1466 | 12982.1466 | 12523.599
2016-02-28 | 20985.25 | 20985.25 | 20194.6163 | 11806.8997 | 11806.8997 | 11502.97
2016-03-31 | 20075.21 | 20075.21 | 20324.618 | 11758.7447 | 11758.7447 | 11445.7227
2016-04-30 | 17405.08 | 17405.08 | 18912.1728 | 10309.6515 | 10309.6515 | 10578.9099
2016-05-31 | 19235.65 | 19235.65 | 19707.6447 | 10530.0143 | 10530.0143 | 10115.8584
2016-06-30 | 22315.7305 | 22315.7305 | 21568.912 | 11378.6081 | 11378.6081 | 11141.3797
2016-07-31 | 22599.9414 | 22599.9414 | 22288.7672 | 11896.1402 | 11896.1402 | 12345.0421
2016-08-31 | 21440.3166 | 21440.3166 | 22375.997 | 11771.834 | 11771.834 | 12295.9028
2016-09-30 | 18289 | 18289 | 19712.7154 | 10401.8861 | 10401.8861 | 10659.2295
2016-10-31 | 18079 | 18079 | 18394.9922 | 10947.5325 | 10947.5325 | 10453.1463
2016-11-30 | 20296 | 20296 | 19544.7667 | 11524.026 | 11524.026 | 10913.6011
2016-12-31 | 20888 | 20888 | 20286.7849 | 12430.7427 | 12430.7427 | 11950.5536
2016 | 22599.9414 | 22599.9414 | 22375.997 | 137738.2263 | 137738.2263 | 135925.9151
2017-01-31 | 21913.73 | 21913.73 | 20965.9674 | 12818.8508 | 12818.8508 | 12369.7298
2017-02-28 | 20966.2287 | 20966.2287 | 20379.4501 | 11294.713 | 11294.713 | 10787.4931
2017-03-31 | 20137.3 | 20137.3 | 18692.3503 | 11824.0632 | 11824.0632 | 11413.3465
2017-04-30 | 17969.79 | 17969.79 | 18482.7844 | 10366.7129 | 10366.7129 | 10105.7565
2017-05-31 | 19193.19 | 19193.19 | 18260.3078 | 10576.9018 | 10576.9018 | 10012.8427
2017-06-30 | 22454.87 | 22454.87 | 21144.8187 | 11159.3312 | 11159.3312 | 10682.999
2017-07-31 | 22492.73 | 22492.73 | 22152.8524 | 11984.7355 | 11984.7355 | 11851.6211
2017-08-31 | 22376.43 | 22376.43 | 21323.3584 | 12105.5471 | 12105.5471 | 11513.597
2017-09-30 | 19490.21 | 19490.21 | 17821.4732 | 10494.2948 | 10494.2948 | 10155.927
2017-10-31 | 18030.62 | 18030.62 | 17407.7858 | 10942.7953 | 10942.7953 | 10260.3837
2017-11-30 | 20230.97 | 20230.97 | 19195.4397 | 11371.7451 | 11371.7451 | 10946.7668
2017-12-31 | 20901.44 | 20901.44 | 21439.6493 | 12303.6865 | 12303.6865 | 12096.0133
2017 | 22492.73 | 22492.73 | 22152.8524 | 137243.3774 | 137243.3774 | 132196.4765
2018-01-31 | 21618.93 | 21618.93 | 20177.5339 | 12685.9178 | 12685.9178 | 12679.8037
2018-02-28 | 20242.21 | 20242.21 | 20042.2165 | 11074.1738 | 11074.1738 | 11081.1365
2018-03-31 | 19551.97 | 19551.97 | 19330.8728 | 11423.555 | 11423.555 | 11267.3415
2018-04-30 | 17669.81 | 17669.81 | 18107.9593 | 10157.8502 | 10157.8502 | 10586.2978
2018-05-31 | 18817.47 | 18817.47 | 19262.1307 | 10289.6502 | 10289.6502 | 10081.137
2018-06-30 | 21890.0001 | 21890.0001 | 20626.9619 | 10863.4062 | 10863.4062 | 10980.4534
2018-07-31 | 22076.0001 | 22076.0001 | 22409.0792 | 11652.7714 | 11652.7714 | 12483.776
2018-08-31 | 21946.0001 | 21946.0001 | 21385.6483 | 11685.5744 | 11685.5744 | 12040.5393
2018-09-30 | 19019 | 19019 | 19505.5646 | 10189.9802 | 10189.9802 | 10579.1906
2018-10-31 | 17788 | 17788 | 17751.4152 | 10750.0648 | 10750.0648 | 10526.7735
2018-11-30 | 19828 | 19828 | 19266.3918 | 11170.7506 | 11170.7506 | 11184.9393
2018-12-31 | 20503 | 20503 | 20375.1864 | 12007.3958 | 12007.3958 | 12019.553
2018 | 22076.0001 | 22076.0001 | 22409.0792 | 133951.0905 | 133951.0905 | 135510.9416
2019-01-31 | 21506 | 21506 | 21058.2817 | 12973.2132 | 12973.2132 | 12688.8389
2019-02-28 | 20008 | 20008 | 20420.3692 | 11162.2057 | 11162.2057 | 11212.4836
2019-03-31 | 19457 | 19457 | 19573.6921 | 11522.1982 | 11522.1982 | 11458.0531
2019-04-30 | 17548 | 17548 | 18796.3299 | 10252.9314 | 10252.9314 | 10432.2785
2019-05-31 | 18663 | 18663 | 17977.0308 | 10412.0446 | 10412.0446 | 10218.7126
2019-06-30 | 21623 | 21623 | 21239.1838 | 10939.3571 | 10939.3571 | 10608.5215
2019-07-31 | 22061 | 22061 | 21120.5208 | 11763.9974 | 11763.9974 | 12446.1887
2019-08-31 | 21200 | 21200 | 22490.4547 | 11598.2109 | 11598.2109 | 11798.5843
2019-09-30 | 19469.84 | 19469.84 | 18958.9757 | 10564.4926 | 10564.4926 | 10167.6302
2019-10-31 | 17559 | 17559 | 18814.592 | 10788.0047 | 10788.0047 | 10446.8836
2019-11-30 | 19597 | 19597 | 19001.8635 | 11194.6524 | 11194.6524 | 11094.2081
2019-12-31 | 20307 | 20307 | 20974 | 12086.6766 | 12086.6766 | 12094.1802
2019 | 22061 | 22061 | 22490.4547 | 135257.9849 | 135257.9849 | 134666.5633
2020-01-31 | 21185.0004 | 21185.0004 | 21137.8728 | 12859.4588 | 12859.4588 | 12460.9405
2020-02-28 | 19917.0004 | 19917.0004 | 19776.0281 | 11586.6754 | 11586.6754 | 11253.1814
2020-03-31 | 19377.0004 | 19377.0004 | 19680.948 | 11522.322 | 11522.322 | 11058.3098
2020-04-30 | 17302.0004 | 17302.0004 | 16515.7848 | 10229.1483 | 10229.1483 | 9383.3554
2020-05-31 | 17426 | 17426 | 18761.2836 | 9434.378 | 9434.378 | 9306.4436
2020-06-30 | 20034 | 20034 | 20741.8718 | 10274.389 | 10274.389 | 10596.6512
2020-07-31 | 22364.4404 | 22364.4404 | 24057.7367 | 11731.6936 | 11731.6936 | 12529.7172
2020-08-31 | 21631.4406 | 21631.4406 | 25317.7535 | 11441.5908 | 11441.5908 | 12338.1938
2020-09-30 | 20312.4408 | 20312.4408 | 19254.2062 | 10356.1124 | 10356.1124 | 10011.2355
2020-10-31 | 17039.9727 | 17039.9727 | 17587.3164 | 10040.7873 | 10040.7873 | 10349.5982
2020-11-30 | 18891.9134 | 18891.9134 | 19416.1975 | 10531.6058 | 10531.6058 | 10693.8532
2020-12-31 | 19805.1651 | 19805.1651 | 20975.3455 | 11815.0887 | 11815.0887 | 11932.8039
2020 | 22364.4404 | 22364.4404 | 25317.7535 | 131823.25 | 131823.25 | 131914.2838
2021-01-31 | 21176.0005 | 21176.0005 | 20951.6431 | 12539.1611 | 12539.1611 | 12307.6071
2021-02-28 | 20760.0005 | 20760.0005 | 20175.4672 | 11073.4765 | 11073.4765 | 11144.3783
2021-03-31 | 19384.0005 | 19384.0005 | 19868.2566 | 11497.7125 | 11497.7125 | 11249.5616
2021-04-30 | 17070.0009 | 17070.0009 | 17618.7846 | 10244.8035 | 10244.8035 | 10097.7166
2021-05-31 | 18055.3342 | 18055.3342 | 18021.5172 | 10152.0681 | 10152.0681 | 9986.9371
2021-06-30 | 22162.0009 | 22162.0009 | 21528.4908 | 10747.5852 | 10747.5852 | 10840.8856
2021-07-31 | 22413.0005 | 22413.0005 | 22251.4821 | 11806.5074 | 11806.5074 | 11970.9832
2021-08-31 | 22235.0005 | 22235.0005 | 21854.4728 | 11706.2663 | 11706.2663 | 12072.0791
2021-09-30 | 21212.0005 | 21212.0005 | 18979.8917 | 10472.6839 | 10472.6839 | 10401.3058
2021-10-31 | 17270.7147 | 17270.7147 | 17606.8602 | 10365.0376 | 10365.0376 | 10429.4829
2021-11-30 | 19227.38 | 19227.38 | 19684.7166 | 10886.7659 | 10886.7659 | 11017.3258
2021-12-31 | 20088.8968 | 20088.8968 | 21331.5579 | 11984.4925 | 11984.4925 | 12185.9418
2021 | 22413.0005 | 22413.0005 | 22251.4821 | 133476.5604 | 133476.5604 | 133704.2048
2022-01-31 | 20983.6671 | 20983.6671 | 21334.1018 | 12536.9576 | 12536.9576 | 12928.5532
2022-02-28 | 20446.0004 | 20446.0004 | 20782.3287 | 11208.712 | 11208.712 | 11400.5165
2022-03-31 | 19401.3338 | 19401.3338 | 19941.2707 | 11617.5125 | 11617.5125 | 11793.6956
2022-04-30 | 17251.0005 | 17251.0005 | 17752.3935 | 10239.112 | 10239.112 | 10311.1592
2022-05-31 | 18269.0005 | 18269.0005 | 20136.0014 | 10372.2878 | 10372.2878 | 10137.6947
2022-06-30 | 22161.0005 | 22161.0005 | 22101.7092 | 10967.9836 | 10967.9836 | 11002.2267
2022-07-31 | 22542.0005 | 22542.0005 | 22484.9516 | 11893.9057 | 11893.9057 | 12411.016
2022-08-31 | 22430.0005 | 22430.0005 | 23477.9346 | 12028.3221 | 12028.3221 | 11998.9314
2022-09-30 | 21489.0005 | 21489.0005 | 20446.2276 | 10551.0851 | 10551.0851 | 10678.4907
2022-10-31 | 17559.0005 | 17559.0005 | 17724.6236 | 10603.0084 | 10603.0084 | 10447.0825
2022-11-30 | 19812.0005 | 19812.0005 | 19389.6575 | 11151.0711 | 11151.0711 | 11128.3255
2022-12-31 | 20241.0005 | 20241.0005 | 20584.5241 | 12191.9609 | 12191.9609 | 12412.7534
2022 | 22542.0005 | 22542.0005 | 23477.9346 | 135361.9188 | 135361.9188 | 136650.4453
2023-01-31 | 21170.3338 | 21170.3338 | 21435.1399 | 12663.6554 | 12663.6554 | 13052.768
2023-02-28 | 20892.3338 | 20892.3338 | 20433.0112 | 11375.0622 | 11375.0622 | 11325.8235
2023-03-31 | 19701.0485 | 19701.0485 | 19000.8853 | 11846.6528 | 11846.6528 | 11814.7494
2023-04-30 | 17785.9996 | 17785.9996 | 19103.3719 | 10349.2653 | 10349.2653 | 10374.8437
2023-05-31 | 18869.9996 | 18869.9996 | 18001.5877 | 10418.8057 | 10418.8057 | 10473.6584
2023-06-30 | 21884.9996 | 21884.9996 | 22417.4764 | 10652.496 | 10652.496 | 11230.6805
2023-07-31 | 22445.9996 | 22445.9996 | 23368.3724 | 11858.9002 | 11858.9002 | 12455.0186
2023-08-31 | 22396.9996 | 22396.9996 | 21865.1956 | 12249.9171 | 12249.9171 | 12005.3253
2023-09-30 | 21479.9996 | 21479.9996 | 21317.3942 | 10718.9739 | 10718.9739 | 10685.1004
2023-10-31 | 17668.0452 | 17668.0452 | 19208.5675 | 10593.967 | 10593.967 | 10757.1302
2023-11-30 | 19742.0453 | 19742.0453 | 20453.2108 | 11007.299 | 11007.299 | 11478.5016
2023-12-31 | 20346.0453 | 20346.0453 | 21211.1571 | 12018.94 | 12018.94 | 12384.2261
2023 | 22445.9996 | 22445.9996 | 23368.3724 | 135753.9345 | 135753.9345 | 138037.826
2024-01-31 | 21418.2553 | 21418.2553 | 21405.4347 | 12929.406 | 12929.406 | 13208.8176
2024-02-28 | 20987.7553 | 20987.7553 | 20022.691 | 11956.6273 | 11956.6273 | 11729.9509
2024-03-31 | 19645.2454 | 19645.2454 | 18939.8337 | 11836.2413 | 11836.2413 | 11632.2959
2024-04-30 | 17839.6154 | 17839.6154 | 18586.0743 | 10616.6408 | 10616.6408 | 10650.6806
2024-05-31 | 19148.7554 | 19148.7554 | 19498.7984 | 10660.6544 | 10660.6544 | 10640.585
2024-06-30 | 22502.1655 | 22502.1655 | 22585.2284 | 10892.6773 | 10892.6773 | 11334.1111
2024-07-31 | 22729.3704 | 22729.3704 | 23182.1746 | 12334.9116 | 12334.9116 | 12956.8035
2024-08-31 | 22592.9271 | 22592.9271 | 22518.533 | 12432.5962 | 12432.5962 | 12419.372
2024-09-30 | 21998.022 | 21998.022 | 21462.7165 | 11042.347 | 11042.347 | 10932.1478
2024-10-31 | 17976.8176 | 17976.8176 | 18603.2901 | 11073.6096 | 11073.6096 | 11048.6213
2024-11-30 | 20217.9361 | 20217.9361 | 19942.2233 | 11500.099 | 11500.099 | 11494.5336
2024-12-31 | 21036.6297 | 21036.6297 | 21342.8087 | 12626.6472 | 12626.6472 | 13046.7703
2024 | 22729.3704 | 22729.3704 | 23182.1746 | 139902.4576 | 139902.4576 | 141094.6899
2025-01-31 | 21835.8361 | 21835.8361 | 22379.5336 | 13253.9945 | 13253.9945 | 13661.657
2025-02-28 | 21259.4124 | 21259.4124 | 21116.0479 | 11671.9004 | 11671.9004 | 12130.7045
2025-03-31 | 20000.0174 | 20000.0174 | 19614.4739 | 12058.4394 | 12058.4394 | 12091.2745
2025-04-30 | 18154.8411 | 18154.8411 | 19246.3001 | 10619.601 | 10619.601 | 10891.1786
2025-05-31 | 19064.5516 | 19064.5516 | 18891.1849 | 10649.1943 | 10649.1943 | 10886.6628
2025-06-30 | 22279.0506 | 22279.0506 | 22678.4237 | 11223.7937 | 11223.7937 | 11544.6629
2025-07-31 | 23249.8525 | 23168.1551 | 23249.8525 | 13471.3387 | 12424.9641 | 13471.3387
2025-08-31 | 23530.1953 | 22782.3554 | 23530.1953 | 12734.6294 | 12363.8608 | 12734.6294
2025-09-30 | 21192.8937 | 21288.0486 | 21192.8937 | 11125.7506 | 11069.0052 | 11125.7506
2025-10-31 | 18572.3296 | 18320.7967 | 18572.3296 | 11323.7934 | 11076.979 | 11323.7934
2025-11-30 | 19963.3073 | 20153.1936 | 19963.3073 | 12004.1764 | 11562.3458 | 12004.1764
2025-12-31 | 21487.8851 | 21447.1157 | 21487.8851 | 13529.2595 | 12900.8568 | 13529.2595
2025 | 23530.1953 | 23168.1551 | 23530.1953 | 143665.8713 | 140874.935 | 145395.0883
2026-01-31 | 22160.5721 | 22550.57 | 22160.5721 | 13936.0376 | 13826.1993 | 13936.0376
2026-02-28 | 21428.1773 | 21686.2 | 21428.1773 | 12322.8763 | 12168.7162 | 12322.8763
2026-03-31 | 20345.7779 | 20412.11 |  | 12501.8912 | 12554.0826
2026-04-30 | 18337.2522 | 18400.67 |  | 10995.8665 | 11030.7881
2026-05-31 | 19510.8225 | 19575.53 |  | 11100.8529 | 11134.7582
2026-06-30 | 23042.9438 | 23020.85 |  | 11828.0828 | 11847.8574
2026-07-31 | 23973.6189 | 24088.97 |  | 13121.8125 | 13137.9106
2026-08-31 | 23293.3615 | 23311.36 |  | 12783.8086 | 12787.1598
2026-09-30 | 21815.8926 | 21817.77 |  | 11458.4665 | 11462.8698
2026-10-31 | 18879.1352 | 18885.8 |  | 11459.1403 | 11462.3764
2026-11-30 | 20971.9767 | 20991.85 |  | 11992.6391 | 11998.7174
2026-12-31 | 21888.7283 | 21905.25 |  | 13255.3489 | 13260.1717
2026 | 23973.6189 | 24088.97 | 22160.5721 | 146756.8233 | 146671.6073 | 26258.9139
2027-01-31 | 22630.4034 | 22657.43 |  | 13840.577 | 13864.5494
2027-02-28 | 21777.8129 | 21810.01 |  | 12202.647 | 12230.8066
2027-03-31 | 20561.0762 | 20587.2 |  | 12592.3294 | 12602.9506
2027-04-30 | 18611.4466 | 18594.14 |  | 11183.6297 | 11164.192
2027-05-31 | 19989.4873 | 20068.33 |  | 11204.398 | 11214.7123
2027-06-30 | 23256.858 | 23268.69 |  | 11967.6244 | 11971.5554
2027-07-31 | 24070.4954 |  |  | 13244.5826
2027-08-31 | 23573.6086 |  |  | 12981.5398
2027-09-30 | 19066.4769 |  |  | 11629.9325
Back to main menu

## Table 1.1.1 Planned
Back to main menu
Table 1.1.1 Planned: Monthly Peak and Energy Demand
Forecasted Peak and Energy Demand
| Peak Demand (MW) |  |  | Energy Demand (GWh)
Month | Current Forecast | Previous Forecast | Weather Corrected Actual | Current Forecast | Previous Forecast | Weather Corrected Actual
2012-01-01 | 22160.0997 | 22160.0997 | 22084.7322 | 13280.0235 | 13280.0235 | 12932.2873
2012-02-01 | 21813.8691 | 21813.8691 | 20756.8677 | 12202.5791 | 12202.5791 | 11380.2015
2012-03-01 | 20708.9072 | 20708.9072 | 20595.0545 | 12264.8125 | 12264.8125 | 11726.1779
2012-04-01 | 18745.092 | 18745.092 | 19830.1533 | 10866.5786 | 10866.5786 | 10883.4994
2012-05-01 | 19038.2309 | 19038.2309 | 19736.9901 | 10943.6824 | 10943.6824 | 10838.5019
2012-06-01 | 22569.1521 | 22569.1521 | 22832.4909 | 11398.2442 | 11398.2442 | 11511.081
2012-07-01 | 23298.1422 | 23298.1422 | 23630.2664 | 12319.3311 | 12319.3311 | 13057.6199
2012-08-01 | 22956.5741 | 22956.5741 | 22726.501 | 12419.0386 | 12419.0386 | 12373.2613
2012-09-01 | 20506.0631 | 20506.0631 | 20370.1157 | 10811.3017 | 10811.3017 | 10900.4102
2012-10-01 | 18345.9037 | 18345.9037 | 18684.153 | 11199.8353 | 11199.8353 | 11149.8822
2012-11-01 | 20571.5606 | 20571.5606 | 20258.2258 | 11629.6439 | 11629.6439 | 11663.449
2012-12-01 | 21693.287 | 21693.287 | 20910.8981 | 12612.0073 | 12612.0073 | 12306.8289
2012 | 23298.1422 | 23298.1422 | 23630.2664 | 141947.0782 | 141947.0782 | 140723.2004
2013-01-31 | 22013.997 | 22013.997 | 22610 | 13314.3055 | 13314.3055 | 13061.0693
2013-02-28 | 21773.6201 | 21773.6201 | 21333.0082 | 11819.7381 | 11819.7381 | 11668.8474
2013-03-31 | 20634.9497 | 20634.9497 | 20784.4526 | 12283.0437 | 12283.0437 | 11869.9986
2013-04-30 | 18492.3312 | 18492.3312 | 19284.8182 | 11018.1303 | 11018.1303 | 11090.2932
2013-05-31 | 19100.9692 | 19100.9692 | 18341.9804 | 10932.3105 | 10932.3105 | 10533.5712
2013-06-30 | 22499.2459 | 22499.2459 | 22719.4401 | 11406.4319 | 11406.4319 | 11283.4325
2013-07-31 | 23212.9348 | 23212.9348 | 24352.1456 | 12479.5529 | 12479.5529 | 12736.3503
2013-08-31 | 22359.7987 | 22359.7987 | 23255.371 | 12227.7513 | 12227.7513 | 12084.9413
2013-09-30 | 20513.3592 | 20513.3592 | 20422.3176 | 11015.3041 | 11015.3041 | 10767.0057
2013-10-31 | 18388.3002 | 18388.3002 | 18981.007 | 11279.1846 | 11279.1846 | 11114.0467
2013-11-30 | 20326.4941 | 20326.4941 | 20034.8189 | 11686.9287 | 11686.9287 | 11709.7788
2013-12-31 | 21395.0558 | 21395.0558 | 21184.5386 | 12699.9803 | 12699.9803 | 12528.9266
2013 | 23212.9348 | 23212.9348 | 24352.1456 | 142162.6617 | 142162.6617 | 140448.2614
2014-01-31 | 22319.8106 | 22319.8106 | 22043.8439 | 13356.427 | 13356.427 | 13409.7767
2014-02-28 | 20964.0592 | 20964.0592 | 21218.2216 | 11748.3799 | 11748.3799 | 11812.9441
2014-03-31 | 19906 | 19906 | 20728.4579 | 12054.5719 | 12054.5719 | 12242.1563
2014-04-30 | 17649 | 17649 | 19249.9632 | 10731.1367 | 10731.1367 | 11038.5265
2014-05-31 | 18964 | 18964 | 18750.4605 | 10790.2174 | 10790.2174 | 10546.4252
2014-06-30 | 22469.55 | 22469.55 | 20705.1957 | 11346.2756 | 11346.2756 | 11140.5499
2014-07-31 | 22948.69 | 22948.69 | 22294.8035 | 12360.0815 | 12360.0815 | 12324.9268
2014-08-31 | 21403.44 | 21403.44 | 21644.3547 | 11992.5131 | 11992.5131 | 11819.2371
2014-09-30 | 19023.2704 | 19023.2704 | 19449.0766 | 10579.5258 | 10579.5258 | 10671.4853
2014-10-31 | 18638.7361 | 18638.7361 | 18447.2196 | 11126.7565 | 11126.7565 | 10814.1957
2014-11-30 | 20302.34 | 20302.34 | 19923.2587 | 11497.4835 | 11497.4835 | 11410.1121
2014-12-31 | 21237.74 | 21237.74 | 21582.6701 | 12769.4956 | 12769.4956 | 12256.0958
2014 | 22948.69 | 22948.69 | 22294.8035 | 140352.8643 | 140352.8643 | 139486.4317
2015-01-31 | 22293.59 | 22293.59 | 21503.4489 | 13068.9431 | 13068.9431 | 12937.1182
2015-02-28 | 21016.81 | 21016.81 | 19709.6284 | 11528.5197 | 11528.5197 | 11740.7311
2015-03-31 | 19840.93 | 19840.93 | 20109.8817 | 11856.8161 | 11856.8161 | 11748.227
2015-04-30 | 18121.2 | 18121.2 | 19362.8308 | 10542.0267 | 10542.0267 | 10624.618
2015-05-31 | 19370.33 | 19370.33 | 17881.7583 | 10635.9243 | 10635.9243 | 10231.5964
2015-06-30 | 22276.64 | 22276.64 | 20554.6293 | 11410.2692 | 11410.2692 | 10908.724
2015-07-31 | 22888.49 | 22888.49 | 22638.5319 | 12174.2184 | 12174.2184 | 12273.6405
2015-08-31 | 21463.69 | 21463.69 | 22383 | 11821.2763 | 11821.2763 | 11782.7212
2015-09-30 | 18485 | 18485 | 19299.6325 | 10512.648 | 10512.648 | 10718.9879
2015-10-31 | 18339 | 18339 | 18444.3181 | 11150.1256 | 11150.1256 | 10731.7474
2015-11-30 | 20306 | 20306 | 19631.9089 | 11595.0899 | 11595.0899 | 10867.5486
2015-12-31 | 21160.04 | 21160.04 | 20418.0801 | 12611.2501 | 12611.2501 | 11784.7123
2015 | 22888.49 | 22888.49 | 22638.5319 | 138907.1073 | 138907.1073 | 136350.3725
2016-01-31 | 22360.24 | 22360.24 | 21249.7402 | 12982.1466 | 12982.1466 | 12523.599
2016-02-28 | 20985.25 | 20985.25 | 20194.6163 | 11806.8997 | 11806.8997 | 11502.97
2016-03-31 | 20075.21 | 20075.21 | 20324.618 | 11758.7447 | 11758.7447 | 11445.7227
2016-04-30 | 17405.08 | 17405.08 | 18912.1728 | 10309.6515 | 10309.6515 | 10578.9099
2016-05-31 | 19235.65 | 19235.65 | 19707.6447 | 10530.0143 | 10530.0143 | 10115.8584
2016-06-30 | 22315.7305 | 22315.7305 | 21568.912 | 11378.6081 | 11378.6081 | 11141.3797
2016-07-31 | 22599.9414 | 22599.9414 | 22288.7672 | 11896.1402 | 11896.1402 | 12345.0421
2016-08-31 | 21440.3166 | 21440.3166 | 22375.997 | 11771.834 | 11771.834 | 12295.9028
2016-09-30 | 18289 | 18289 | 19712.7154 | 10401.8861 | 10401.8861 | 10659.2295
2016-10-31 | 18079 | 18079 | 18394.9922 | 10947.5325 | 10947.5325 | 10453.1463
2016-11-30 | 20296 | 20296 | 19544.7667 | 11524.026 | 11524.026 | 10913.6011
2016-12-31 | 20888 | 20888 | 20286.7849 | 12430.7427 | 12430.7427 | 11950.5536
2016 | 22599.9414 | 22599.9414 | 22375.997 | 137738.2263 | 137738.2263 | 135925.9151
2017-01-31 | 21913.73 | 21913.73 | 20965.9674 | 12818.8508 | 12818.8508 | 12369.7298
2017-02-28 | 20966.2287 | 20966.2287 | 20379.4501 | 11294.713 | 11294.713 | 10787.4931
2017-03-31 | 20137.3 | 20137.3 | 18692.3503 | 11824.0632 | 11824.0632 | 11413.3465
2017-04-30 | 17969.79 | 17969.79 | 18482.7844 | 10366.7129 | 10366.7129 | 10105.7565
2017-05-31 | 19193.19 | 19193.19 | 18260.3078 | 10576.9018 | 10576.9018 | 10012.8427
2017-06-30 | 22454.87 | 22454.87 | 21144.8187 | 11159.3312 | 11159.3312 | 10682.999
2017-07-31 | 22492.73 | 22492.73 | 22152.8524 | 11984.7355 | 11984.7355 | 11851.6211
2017-08-31 | 22376.43 | 22376.43 | 21323.3584 | 12105.5471 | 12105.5471 | 11513.597
2017-09-30 | 19490.21 | 19490.21 | 17821.4732 | 10494.2948 | 10494.2948 | 10155.927
2017-10-31 | 18030.62 | 18030.62 | 17407.7858 | 10942.7953 | 10942.7953 | 10260.3837
2017-11-30 | 20230.97 | 20230.97 | 19195.4397 | 11371.7451 | 11371.7451 | 10946.7668
2017-12-31 | 20901.44 | 20901.44 | 21439.6493 | 12303.6865 | 12303.6865 | 12096.0133
2017 | 22492.73 | 22492.73 | 22152.8524 | 137243.3774 | 137243.3774 | 132196.4765
2018-01-31 | 21618.93 | 21618.93 | 20177.5339 | 12685.9178 | 12685.9178 | 12679.8037
2018-02-28 | 20242.21 | 20242.21 | 20042.2165 | 11074.1738 | 11074.1738 | 11081.1365
2018-03-31 | 19551.97 | 19551.97 | 19330.8728 | 11423.555 | 11423.555 | 11267.3415
2018-04-30 | 17669.81 | 17669.81 | 18107.9593 | 10157.8502 | 10157.8502 | 10586.2978
2018-05-31 | 18817.47 | 18817.47 | 19262.1307 | 10289.6502 | 10289.6502 | 10081.137
2018-06-30 | 21890.0001 | 21890.0001 | 20626.9619 | 10863.4062 | 10863.4062 | 10980.4534
2018-07-31 | 22076.0001 | 22076.0001 | 22409.0792 | 11652.7714 | 11652.7714 | 12483.776
2018-08-31 | 21946.0001 | 21946.0001 | 21385.6483 | 11685.5744 | 11685.5744 | 12040.5393
2018-09-30 | 19019 | 19019 | 19505.5646 | 10189.9802 | 10189.9802 | 10579.1906
2018-10-31 | 17788 | 17788 | 17751.4152 | 10750.0648 | 10750.0648 | 10526.7735
2018-11-30 | 19828 | 19828 | 19266.3918 | 11170.7506 | 11170.7506 | 11184.9393
2018-12-31 | 20503 | 20503 | 20375.1864 | 12007.3958 | 12007.3958 | 12019.553
2018 | 22076.0001 | 22076.0001 | 22409.0792 | 133951.0905 | 133951.0905 | 135510.9416
2019-01-31 | 21506 | 21506 | 21058.2817 | 12973.2132 | 12973.2132 | 12688.8389
2019-02-28 | 20008 | 20008 | 20420.3692 | 11162.2057 | 11162.2057 | 11212.4836
2019-03-31 | 19457 | 19457 | 19573.6921 | 11522.1982 | 11522.1982 | 11458.0531
2019-04-30 | 17548 | 17548 | 18796.3299 | 10252.9314 | 10252.9314 | 10432.2785
2019-05-31 | 18663 | 18663 | 17977.0308 | 10412.0446 | 10412.0446 | 10218.7126
2019-06-30 | 21623 | 21623 | 21239.1838 | 10939.3571 | 10939.3571 | 10608.5215
2019-07-31 | 22061 | 22061 | 21120.5208 | 11763.9974 | 11763.9974 | 12446.1887
2019-08-31 | 21200 | 21200 | 22490.4547 | 11598.2109 | 11598.2109 | 11798.5843
2019-09-30 | 19469.84 | 19469.84 | 18958.9757 | 10564.4926 | 10564.4926 | 10167.6302
2019-10-31 | 17559 | 17559 | 18814.592 | 10788.0047 | 10788.0047 | 10446.8836
2019-11-30 | 19597 | 19597 | 19001.8635 | 11194.6524 | 11194.6524 | 11094.2081
2019-12-31 | 20307 | 20307 | 20974 | 12086.6766 | 12086.6766 | 12094.1802
2019 | 22061 | 22061 | 22490.4547 | 135257.9849 | 135257.9849 | 134666.5633
2020-01-31 | 21185.0004 | 21185.0004 | 21137.8728 | 12859.4588 | 12859.4588 | 12460.9405
2020-02-28 | 19917.0004 | 19917.0004 | 19776.0281 | 11586.6754 | 11586.6754 | 11253.1814
2020-03-31 | 19377.0004 | 19377.0004 | 19680.948 | 11522.322 | 11522.322 | 11058.3098
2020-04-30 | 17302.0004 | 17302.0004 | 16515.7848 | 10229.1483 | 10229.1483 | 9383.3554
2020-05-31 | 17426 | 17426 | 18761.2836 | 9434.378 | 9434.378 | 9306.4436
2020-06-30 | 20034 | 20034 | 20741.8718 | 10274.389 | 10274.389 | 10596.6512
2020-07-31 | 22364.4404 | 22364.4404 | 24057.7367 | 11731.6936 | 11731.6936 | 12529.7172
2020-08-31 | 21631.4406 | 21631.4406 | 25317.7535 | 11441.5908 | 11441.5908 | 12338.1938
2020-09-30 | 20312.4408 | 20312.4408 | 19254.2062 | 10356.1124 | 10356.1124 | 10011.2355
2020-10-31 | 17039.9727 | 17039.9727 | 17587.3164 | 10040.7873 | 10040.7873 | 10349.5982
2020-11-30 | 18891.9134 | 18891.9134 | 19416.1975 | 10531.6058 | 10531.6058 | 10693.8532
2020-12-31 | 19805.1651 | 19805.1651 | 20975.3455 | 11815.0887 | 11815.0887 | 11932.8039
2020 | 22364.4404 | 22364.4404 | 25317.7535 | 131823.25 | 131823.25 | 131914.2838
2021-01-31 | 21176.0005 | 21176.0005 | 20951.6431 | 12539.1611 | 12539.1611 | 12307.6071
2021-02-28 | 20760.0005 | 20760.0005 | 20175.4672 | 11073.4765 | 11073.4765 | 11144.3783
2021-03-31 | 19384.0005 | 19384.0005 | 19868.2566 | 11497.7125 | 11497.7125 | 11249.5616
2021-04-30 | 17070.0009 | 17070.0009 | 17618.7846 | 10244.8035 | 10244.8035 | 10097.7166
2021-05-31 | 18055.3342 | 18055.3342 | 18021.5172 | 10152.0681 | 10152.0681 | 9986.9371
2021-06-30 | 22162.0009 | 22162.0009 | 21528.4908 | 10747.5852 | 10747.5852 | 10840.8856
2021-07-31 | 22413.0005 | 22413.0005 | 22251.4821 | 11806.5074 | 11806.5074 | 11970.9832
2021-08-31 | 22235.0005 | 22235.0005 | 21854.4728 | 11706.2663 | 11706.2663 | 12072.0791
2021-09-30 | 21212.0005 | 21212.0005 | 18979.8917 | 10472.6839 | 10472.6839 | 10401.3058
2021-10-31 | 17270.7147 | 17270.7147 | 17606.8602 | 10365.0376 | 10365.0376 | 10429.4829
2021-11-30 | 19227.38 | 19227.38 | 19684.7166 | 10886.7659 | 10886.7659 | 11017.3258
2021-12-31 | 20088.8968 | 20088.8968 | 21331.5579 | 11984.4925 | 11984.4925 | 12185.9418
2021 | 22413.0005 | 22413.0005 | 22251.4821 | 133476.5604 | 133476.5604 | 133704.2048
2022-01-31 | 20983.6671 | 20983.6671 | 21334.1018 | 12536.9576 | 12536.9576 | 12928.5532
2022-02-28 | 20446.0004 | 20446.0004 | 20782.3287 | 11208.712 | 11208.712 | 11400.5165
2022-03-31 | 19401.3338 | 19401.3338 | 19941.2707 | 11617.5125 | 11617.5125 | 11793.6956
2022-04-30 | 17251.0005 | 17251.0005 | 17752.3935 | 10239.112 | 10239.112 | 10311.1592
2022-05-31 | 18269.0005 | 18269.0005 | 20136.0014 | 10372.2878 | 10372.2878 | 10137.6947
2022-06-30 | 22161.0005 | 22161.0005 | 22101.7092 | 10967.9836 | 10967.9836 | 11002.2267
2022-07-31 | 22542.0005 | 22542.0005 | 22484.9516 | 11893.9057 | 11893.9057 | 12411.016
2022-08-31 | 22430.0005 | 22430.0005 | 23477.9346 | 12028.3221 | 12028.3221 | 11998.9314
2022-09-30 | 21489.0005 | 21489.0005 | 20446.2276 | 10551.0851 | 10551.0851 | 10678.4907
2022-10-31 | 17559.0005 | 17559.0005 | 17724.6236 | 10603.0084 | 10603.0084 | 10447.0825
2022-11-30 | 19812.0005 | 19812.0005 | 19389.6575 | 11151.0711 | 11151.0711 | 11128.3255
2022-12-31 | 20241.0005 | 20241.0005 | 20584.5241 | 12191.9609 | 12191.9609 | 12412.7534
2022 | 22542.0005 | 22542.0005 | 23477.9346 | 135361.9188 | 135361.9188 | 136650.4453
2023-01-31 | 21170.3338 | 21170.3338 | 21435.1399 | 12663.6554 | 12663.6554 | 13052.768
2023-02-28 | 20892.3338 | 20892.3338 | 20433.0112 | 11375.0622 | 11375.0622 | 11325.8235
2023-03-31 | 19701.0485 | 19701.0485 | 19000.8853 | 11846.6528 | 11846.6528 | 11814.7494
2023-04-30 | 17785.9996 | 17785.9996 | 19103.3719 | 10349.2653 | 10349.2653 | 10374.8437
2023-05-31 | 18869.9996 | 18869.9996 | 18001.5877 | 10418.8057 | 10418.8057 | 10473.6584
2023-06-30 | 21884.9996 | 21884.9996 | 22417.4764 | 10652.496 | 10652.496 | 11230.6805
2023-07-31 | 22445.9996 | 22445.9996 | 23368.3724 | 11858.9002 | 11858.9002 | 12455.0186
2023-08-31 | 22396.9996 | 22396.9996 | 21865.1956 | 12249.9171 | 12249.9171 | 12005.3253
2023-09-30 | 21479.9996 | 21479.9996 | 21317.3942 | 10718.9739 | 10718.9739 | 10685.1004
2023-10-31 | 17668.0452 | 17668.0452 | 19208.5675 | 10593.967 | 10593.967 | 10757.1302
2023-11-30 | 19742.0453 | 19742.0453 | 20453.2108 | 11007.299 | 11007.299 | 11478.5016
2023-12-31 | 20346.0453 | 20346.0453 | 21211.1571 | 12018.94 | 12018.94 | 12384.2261
2023 | 22445.9996 | 22445.9996 | 23368.3724 | 135753.9345 | 135753.9345 | 138037.826
2024-01-31 | 21418.2553 | 21418.2553 | 21405.4347 | 12929.406 | 12929.406 | 13208.8176
2024-02-28 | 20987.7553 | 20987.7553 | 20022.691 | 11956.6273 | 11956.6273 | 11729.9509
2024-03-31 | 19645.2454 | 19645.2454 | 18939.8337 | 11836.2413 | 11836.2413 | 11632.2959
2024-04-30 | 17839.6154 | 17839.6154 | 18586.0743 | 10616.6408 | 10616.6408 | 10650.6806
2024-05-31 | 19148.7554 | 19148.7554 | 19498.7984 | 10660.6544 | 10660.6544 | 10640.585
2024-06-30 | 22502.1655 | 22502.1655 | 22585.2284 | 10892.6773 | 10892.6773 | 11334.1111
2024-07-31 | 22729.3249 | 22729.3249 | 23182.1746 | 12334.9116 | 12334.9116 | 12956.8035
2024-08-31 | 22604.8475 | 22604.8475 | 22518.533 | 12446.9545 | 12446.9545 | 12419.372
2024-09-30 | 22015.6938 | 22015.6938 | 21462.7165 | 11057.7009 | 11057.7009 | 10932.1478
2024-10-31 | 17976.8176 | 17976.8176 | 18603.2901 | 11073.6096 | 11073.6096 | 11048.6213
2024-11-30 | 20217.9361 | 20217.9361 | 19942.2233 | 11500.099 | 11500.099 | 11494.5336
2024-12-31 | 21036.6297 | 21036.6297 | 21342.8087 | 12626.6472 | 12626.6472 | 13046.7703
2024 | 22729.3249 | 22729.3249 | 23182.1746 | 139932.1699 | 139932.1699 | 141094.6899
2025-01-31 | 21856.1165 | 21856.1165 | 22379.5336 | 13268.2621 | 13268.2621 | 13661.657
2025-02-28 | 21278.651 | 21278.651 | 21116.0479 | 11685.5171 | 11685.5171 | 12130.7045
2025-03-31 | 20023.5778 | 20023.5778 | 19614.4739 | 12075.4951 | 12075.4951 | 12091.2745
2025-04-30 | 18154.8411 | 18154.8411 | 19246.3001 | 10619.601 | 10619.601 | 10891.1786
2025-05-31 | 19064.5516 | 19064.5516 | 18891.1849 | 10649.1943 | 10649.1943 | 10886.6628
2025-06-30 | 22279.0506 | 22279.0506 | 22678.4237 | 11223.7937 | 11223.7937 | 11544.6629
2025-07-31 | 23249.8525 | 23171.0268 | 23249.8525 | 13471.3387 | 12427.0436 | 13471.3387
2025-08-31 | 23530.1953 | 22852.8201 | 23530.1953 | 12734.6294 | 12416.3112 | 12734.6294
2025-09-30 | 21192.8937 | 21301.525 | 21192.8937 | 11125.7506 | 11078.9473 | 11125.7506
2025-10-31 | 18572.3296 | 18359.0116 | 18572.3296 | 11323.7934 | 11105.4864 | 11323.7934
2025-11-30 | 19963.3073 | 20191.9546 | 19963.3073 | 12004.1764 | 11589.9091 | 12004.1764
2025-12-31 | 21487.8851 | 21485.0415 | 21487.8851 | 13529.2595 | 12929.668 | 13529.2595
2025 | 23530.1953 | 23171.0268 | 23530.1953 | 143710.8115 | 141069.229 | 145395.0883
2026-01-31 | 22160.5721 | 22588.04 | 22160.5721 | 13936.0376 | 13853.6597 | 13936.0376
2026-02-28 | 21428.1773 | 21723.91 | 21428.1773 | 12322.8763 | 12193.5192 | 12322.8763
2026-03-31 | 20345.7779 | 20449.45 |  | 12501.8912 | 12581.543
2026-04-30 | 18337.2522 | 18439.01 |  | 10995.8665 | 11057.3627
2026-05-31 | 19510.8225 | 19614.1 |  | 11100.8529 | 11162.2187
2026-06-30 | 23042.9438 | 23054.31 |  | 11828.0828 | 11874.4321
2026-07-31 | 23973.6189 | 24125.48 |  | 13121.8125 | 13165.3711
2026-08-31 | 23293.3615 | 23349.21 |  | 12783.8086 | 12814.6202
2026-09-30 | 21815.8926 | 21852.41 |  | 11458.4665 | 11488.0044
2026-10-31 | 18879.1352 | 18921.36 |  | 11459.1403 | 11488.3489
2026-11-30 | 20971.9767 | 21027.45 |  | 11992.6391 | 12023.8521
2026-12-31 | 21888.7283 | 21941.22 |  | 13255.3489 | 13286.1441
2026 | 23973.6189 | 24125.48 | 22160.5721 | 146756.8233 | 146989.0763 | 26258.9139
2027-01-31 | 22657.0485 | 22690.45 |  | 13860.0144 | 13889.1514
2027-02-28 | 21813.2523 | 21858.82 |  | 12225.9719 | 12263.9423
2027-03-31 | 20599.4645 | 20642.91 |  | 12620.3194 | 12642.9682
2027-04-30 | 18659.1268 | 18669.97 |  | 11217.2176 | 11216.288
2027-05-31 | 20045.1252 | 20149.53 |  | 11244.7035 | 11275.9709
2027-06-30 | 23324.881 | 23381.75 |  | 12015.991 | 12053.7601
2027-07-31 | 24148.4464 |  |  | 13302.6224
2027-08-31 | 23661.6362 |  |  | 13046.3313
2027-09-30 | 22143.7022 |  |  | 11703.1939
Back to main menu

## Table 1.1.2 Firm
Back to main menu
Table 1.1.2 Firm: Weekly Coincident Peak Demand by Zone
Week Ending | Firm Hourly Coincident Peak Demand (MW)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario | Load Forecast Uncertainty
2026-04-05 23:00 | 102.2505 | 1249.6563 | 1406.1832 | 612.8738 | 1455.2844 | 399.2154 | 1149.5201 | 3675.8824 | 6490.0854 | 1844.0341 | 18384.9856 | 565.9887
2026-04-12 23:00 | 95.5541 | 1223.7099 | 1376.5744 | 596.2665 | 1415.3901 | 392.2706 | 1120.3516 | 3635.3459 | 6256.1893 | 1842.4604 | 17954.1126 | 579.6748
2026-04-19 23:00 | 115.6608 | 1202.3195 | 1344.0219 | 567.9934 | 1368.597 | 405.9545 | 1083.5924 | 3504.1963 | 6297.0877 | 1815.0456 | 17704.4692 | 683.878
2026-04-26 23:00 | 103.8158 | 1149.9911 | 1301.8584 | 583.1681 | 1288.1051 | 364.1118 | 1058.2621 | 3536.8926 | 6172.8295 | 1882.3986 | 17441.4331 | 611.1489
2026-05-03 23:00 | 110.1593 | 1154.52 | 1299.7598 | 540.8302 | 1254.9904 | 380.9133 | 1052.8455 | 3476.2387 | 6165.0149 | 1790.9268 | 17226.1989 | 630.4626
2026-05-10 23:00 | 103.7122 | 953.8744 | 1195.2817 | 575.3732 | 1175.7706 | 385.211 | 1085.6468 | 3515.4548 | 6353.4737 | 1913.8533 | 17257.6517 | 756.5348
2026-05-17 23:00 | 95.6434 | 1054.2798 | 1243.79 | 582.3897 | 1217.8526 | 347.242 | 1163.1617 | 3520.5567 | 6469.2359 | 1655.0347 | 17349.1867 | 1058.1867
2026-05-24 23:00 | 92.1472 | 1129.8703 | 1299.1432 | 669.5468 | 1192.5431 | 347.0348 | 1060.0338 | 3580.3065 | 6730.2725 | 1853.3393 | 17954.2374 | 1424.7734
2026-05-31 23:00 | 90.3865 | 1060.4003 | 1305.4663 | 631.8289 | 1182.6587 | 339.26 | 1215.2401 | 3526.3012 | 7250.9683 | 1825.7475 | 18428.2577 | 2122.9778
2026-06-07 23:00 | 79.2151 | 1022.196 | 1310.2917 | 739.1315 | 1169.7418 | 361.5633 | 1212.7129 | 4073.723 | 7240.5268 | 2046.4559 | 19255.558 | 2228.7139
2026-06-14 23:00 | 80.2845 | 1164.801 | 1413.0329 | 709.1575 | 1154.6992 | 369.0142 | 1335.321 | 3933.4212 | 7443.2587 | 2115.2513 | 19718.2415 | 2187.4856
2026-06-21 23:00 | 76.2322 | 1301.9987 | 1684.4166 | 804.3733 | 1133.4906 | 333.0524 | 1251.2827 | 4145.6491 | 7945.0512 | 2159.9038 | 20835.4507 | 2004.776
2026-06-28 23:00 | 84.2032 | 1244.1168 | 1505.2487 | 825.5043 | 1138.5187 | 337.4458 | 1305.8656 | 4505.4215 | 8337.3732 | 2427.9364 | 21711.6342 | 1693.5311
2026-07-05 23:00 | 73.4955 | 1340.3384 | 1678.4992 | 830.1201 | 1118.1002 | 361.5829 | 1392.3561 | 4427.4286 | 8064.522 | 2398.1924 | 21684.6354 | 1705.7306
2026-07-12 23:00 | 81.6996 | 1248.7719 | 1611.2836 | 816.2186 | 1156.3749 | 366.0383 | 1539.2909 | 4525.68 | 8604.7853 | 2436.2528 | 22386.396 | 1777.0801
2026-07-19 23:00 | 77.9244 | 1345.6572 | 1639.8781 | 821.9772 | 1162.2605 | 371.1555 | 1562.5532 | 4762.5024 | 8268.822 | 2513.1483 | 22525.8787 | 1718.1777
2026-07-26 23:00 | 78.7833 | 1374.0198 | 1711.5826 | 832.2948 | 1157.8886 | 386.7568 | 1430.1091 | 4609.6465 | 8536.2297 | 2428.138 | 22545.4491 | 1705.3875
2026-08-02 23:00 | 93.5143 | 1491.6321 | 1820.2129 | 848.836 | 1293.6451 | 410.5224 | 1488.4342 | 4319.083 | 8183.6925 | 2344.8387 | 22294.4112 | 1632.1208
2026-08-09 23:00 | 96.3382 | 1331.5694 | 1600.9073 | 789.9741 | 1189.6705 | 366.4913 | 1455.8072 | 4395.0938 | 8279.5917 | 2259.7483 | 21765.1918 | 1794.5334
2026-08-16 23:00 | 90.9335 | 1313.5974 | 1612.9323 | 821.5231 | 1188.6508 | 402.2708 | 1256.9136 | 4400.5793 | 8417.6587 | 2312.0744 | 21817.1338 | 1615.1329
2026-08-23 23:00 | 90.399 | 1337.0664 | 1598.8705 | 807.6442 | 1223.2402 | 390.1953 | 1397.5187 | 4543.5593 | 7858.4185 | 2410.4486 | 21657.3607 | 1386.6259
2026-08-30 23:00 | 98.2143 | 1272.7701 | 1621.5888 | 771.0547 | 1226.1864 | 368.3782 | 1479.5493 | 4215.0557 | 8154.6582 | 2320.1135 | 21527.5692 | 1407.9515
2026-09-06 23:00 | 101.4204 | 1235.0959 | 1544.7451 | 762.1928 | 1191.2661 | 371.6998 | 1419.2818 | 4261.5693 | 7842.1233 | 2369.7725 | 21099.167 | 1785.5627
2026-09-13 23:00 | 93.5798 | 1122.5624 | 1329.0532 | 748.7948 | 1129.1196 | 347.1646 | 1096.9581 | 4234.9479 | 7440.2738 | 2359.9889 | 19902.443 | 1993.4029
2026-09-20 23:00 | 77.3766 | 1128.3833 | 1426.6528 | 709.4486 | 1213.8815 | 367.9159 | 1256.2589 | 3944.8925 | 7181.1262 | 2102.7816 | 19408.7179 | 1731.1358
2026-09-27 23:00 | 92.6537 | 1068.9792 | 1274.8001 | 653.6665 | 1236.3655 | 351.5752 | 1289.4356 | 3712.9887 | 7124.903 | 2034.9353 | 18840.3029 | 1632.3076
2026-10-04 23:00 | 87.9779 | 1156.6685 | 1304.058 | 694.6905 | 1239.2683 | 375.3885 | 1043.6358 | 3930.0271 | 6677.1524 | 2225.9525 | 18734.8195 | 1198.1318
2026-10-11 23:00 | 67.3365 | 1160.7322 | 1292.6594 | 681.8524 | 1274.0626 | 346.8023 | 1064.0473 | 3739.5043 | 6365.2891 | 2030.696 | 18022.9822 | 886.7211
2026-10-18 23:00 | 86.9837 | 1222.0842 | 1368.5465 | 655.8459 | 1300.9506 | 378.8773 | 1104.3589 | 3675.1818 | 6247.1124 | 1919.0661 | 17959.0073 | 605.5533
2026-10-25 23:00 | 95.9702 | 1230.5344 | 1392.9112 | 658.0785 | 1316.2618 | 407.8473 | 1063.536 | 3720.9496 | 6395.3399 | 1998.6194 | 18280.0482 | 456.6077
2026-11-01 23:00 | 91.1091 | 1241.0043 | 1390.5253 | 671.007 | 1332.7724 | 425.9448 | 1125.7748 | 3787.4769 | 6510.9093 | 2010.6319 | 18587.1559 | 447.4104
2026-11-08 23:00 | 107.1575 | 1272.5454 | 1481.2705 | 678.2146 | 1375.5045 | 479.2884 | 1185.5136 | 3833.2665 | 6566.2388 | 2141.1297 | 19120.1294 | 484.6058
2026-11-15 23:00 | 109.2343 | 1351.968 | 1528.0025 | 703.0201 | 1409.42 | 460.0647 | 1268.3531 | 3881.9682 | 6744.5201 | 2163.5826 | 19620.1336 | 629.3315
2026-11-22 23:00 | 110.532 | 1384.4224 | 1554.6192 | 725.9861 | 1416.2845 | 481.3705 | 1276.8616 | 4013.5986 | 6961.3927 | 2251.9543 | 20177.022 | 638.3026
2026-11-29 23:00 | 112.205 | 1441.4808 | 1604.164 | 745.1448 | 1465.2694 | 494.1057 | 1322.3584 | 4176.645 | 7116.9966 | 2274.6464 | 20753.0162 | 544.2964
2026-12-06 23:00 | 119.7909 | 1458.2399 | 1768.9085 | 740.838 | 1537.0054 | 520.0971 | 1385.6911 | 4116.3987 | 7081.739 | 2317.9273 | 21046.636 | 552.6325
2026-12-13 23:00 | 124.0231 | 1486.606 | 1801.8747 | 756.9642 | 1531.1071 | 576.6713 | 1395.4647 | 4277.7881 | 7131.553 | 2309.7241 | 21391.7763 | 678.8644
2026-12-20 23:00 | 124.6476 | 1527.8524 | 1830.3611 | 763.0154 | 1568.4968 | 545.4957 | 1468.8231 | 4282.7915 | 7219.3349 | 2276.2423 | 21607.0608 | 700.1513
2026-12-27 23:00 | 118.5021 | 1430.0684 | 1762.139 | 755.7967 | 1494.9923 | 519.5987 | 1373.5045 | 4250.204 | 7006.5296 | 2335.0371 | 21046.3726 | 725.0361
2027-01-03 23:00 | 130.183 | 1643.426 | 1836.4849 | 740.7887 | 1618.0625 | 539.11 | 1439.0402 | 4140.6571 | 6955.3208 | 2218.4977 | 21261.5709 | 743.9914
2027-01-10 23:00 | 139.1263 | 1646.7384 | 1897.4088 | 743.9751 | 1596.3533 | 556.071 | 1425.4259 | 4355.241 | 7340.2945 | 2305.1786 | 22005.8128 | 826.8994
2027-01-17 23:00 | 129.8985 | 1635.277 | 1861.8869 | 744.0425 | 1588.06 | 495.4798 | 1442.3408 | 4311.6909 | 7297.9476 | 2391.9165 | 21898.5406 | 841.1993
2027-01-24 23:00 | 139.1253 | 1591.8703 | 1781.7655 | 759.249 | 1536.3282 | 498.6626 | 1411.9318 | 4443.1063 | 7422.2483 | 2391.1003 | 21975.3876 | 871.9559
2027-01-31 23:00 | 138.4534 | 1655.7258 | 1862.2775 | 742.1467 | 1576.8216 | 523.0815 | 1436.2439 | 4343.3209 | 7426.1576 | 2253.7764 | 21958.0053 | 831.9633
2027-02-07 23:00 | 122.5152 | 1567.0381 | 1794.8519 | 749.5729 | 1581.6847 | 495.7816 | 1412.8223 | 4213.418 | 7312.6094 | 2144.6226 | 21394.9166 | 754.919
2027-02-14 23:00 | 120.0767 | 1566.4922 | 1802.3901 | 734.2619 | 1577.2497 | 497.3321 | 1416.9206 | 4124.1644 | 7383.4365 | 2128.4201 | 21350.7443 | 749.6377
2027-02-21 23:00 | 117.8971 | 1523.6959 | 1779.8137 | 723.4741 | 1588.4634 | 528.8276 | 1376.3469 | 4049.188 | 7181.411 | 2158.2513 | 21027.369 | 759.2493
2027-02-28 23:00 | 121.3903 | 1500.9519 | 1712.7142 | 736.5937 | 1562.4664 | 505.835 | 1343.3367 | 4136.7603 | 7292.1293 | 2060.496 | 20972.6738 | 659.4801
2027-03-07 23:00 | 111.954 | 1480.0131 | 1646.1644 | 715.7476 | 1563.5956 | 469.3014 | 1355.2676 | 4022.8225 | 7086.0866 | 1995.4891 | 20446.4418 | 676.4215
2027-03-14 23:00 | 117.0154 | 1380.926 | 1573.8513 | 717.9006 | 1530.0241 | 437.5874 | 1248.8829 | 4041.8102 | 6919.6789 | 2021.2841 | 19988.9608 | 693.9156
2027-03-21 23:00 | 104.0855 | 1355.6625 | 1547.0053 | 703.1668 | 1531.1628 | 438.3449 | 1213.392 | 3864.1866 | 6711.2818 | 2023.3984 | 19491.6865 | 635.2704
2027-03-28 23:00 | 108.2562 | 1279.3258 | 1480.4856 | 675.2857 | 1507.7337 | 465.2331 | 1166.2926 | 3793.3338 | 6540.7552 | 2033.6338 | 19050.3355 | 552.0023
2027-04-04 23:00 | 112.9449 | 1234.5978 | 1401.8583 | 680.6644 | 1460.6289 | 439.9468 | 1124.3587 | 3685.7485 | 6443.7448 | 1968.4092 | 18552.902 | 534.9822
2027-04-11 23:00 | 92.828 | 1236.5896 | 1385.5451 | 686.7154 | 1466.044 | 396.6279 | 1131.9703 | 3697.4314 | 6333.6639 | 1846.8602 | 18274.2759 | 544.8649
2027-04-18 23:00 | 110.6722 | 1109.7189 | 1315.2607 | 689.4707 | 1328.5275 | 395.9509 | 1083.2723 | 3653.3178 | 6288.0994 | 1983.6516 | 17957.942 | 692.1192
2027-04-25 23:00 | 98.0973 | 1162.9386 | 1281.0041 | 659.8478 | 1341.8251 | 360.8281 | 1082.9706 | 3627.7862 | 6220.3817 | 1831.4 | 17667.0794 | 626.497
2027-05-02 23:00 | 100.3427 | 1148.4249 | 1274.2764 | 658.3587 | 1336.3762 | 401.7416 | 1072.7663 | 3523.5971 | 6186.8465 | 1746.0565 | 17448.7869 | 606.5185
2027-05-09 23:00 | 98.9688 | 1148.8192 | 1305.1288 | 660.3307 | 1341.0766 | 372.1415 | 1071.2008 | 3564.4225 | 6146.0241 | 1765.452 | 17473.5649 | 738.0459
2027-05-16 23:00 | 81.363 | 921.952 | 1148.3926 | 683.152 | 1154.8033 | 321.7796 | 1058.7154 | 3931.5489 | 6166.1322 | 2044.7623 | 17512.6013 | 987.0282
2027-05-23 23:00 | 106.324 | 1184.9535 | 1418.4444 | 685.2737 | 1331.0647 | 361.8203 | 1129.0619 | 3663.2279 | 6487.6103 | 1823.5224 | 18191.303 | 1335.0437
2027-05-30 23:00 | 74.1594 | 1005.696 | 1184.5631 | 739.1928 | 1174.794 | 351.2611 | 1101.9362 | 3884.2552 | 6856.788 | 1986.7478 | 18359.3935 | 2055.3156
2027-06-06 23:00 | 76.2624 | 1082.027 | 1395.1399 | 777.8135 | 1252.6062 | 391.0116 | 1382.6435 | 3666.1627 | 7447.2866 | 1814.9436 | 19285.8971 | 2231.6497
2027-06-13 23:00 | 99.2318 | 1050.4882 | 1353.557 | 801.0709 | 1179.8596 | 317.1531 | 1288.0022 | 4090.0226 | 7397.9928 | 2241.3261 | 19818.7042 | 2169.1184
2027-06-20 23:00 | 84.663 | 1123.085 | 1406.4373 | 841.1951 | 1106.6417 | 345.0719 | 1232.9265 | 4585.9572 | 7739.3766 | 2404.745 | 20870.0994 | 2097.8104
2027-06-27 23:00 | 82.9154 | 1352.3624 | 1689.7938 | 868.4228 | 1261.5644 | 367.6512 | 1446.9659 | 4395.3003 | 8112.7154 | 2268.2065 | 21845.8981 | 1705.9127
2027-07-04 23:00 | 77.9331 | 1332.1363 | 1680.6117 | 859.7627 | 1221.4877 | 364.4206 | 1475.2708 | 4299.5522 | 8171.0762 | 2288.3499 | 21770.6012 | 1678.5404
2027-07-11 23:00 | 77.6359 | 1321.8423 | 1659.4197 | 922.4109 | 1141.3847 | 390.9034 | 1513.678 | 4614.1744 | 8490.4757 | 2445.1747 | 22577.0996 | 1778.0893
2027-07-18 23:00 | 75.7442 | 1364.2658 | 1733.2768 | 926.0523 | 1210.8491 | 418.6125 | 1562.4531 | 4593.5134 | 8486.3659 | 2354.8593 | 22725.9924 | 1763.6312
2027-07-25 23:00 | 76.9651 | 1377.435 | 1714.8024 | 935.8001 | 1196.7077 | 385.1868 | 1435.0883 | 4643.887 | 8598.6527 | 2421.6936 | 22786.2189 | 1711.2693
2027-08-01 23:00 | 90.187 | 1495.819 | 1806.8675 | 977.0109 | 1281.1616 | 383.4216 | 1463.2077 | 4568.978 | 7969.8308 | 2493.0369 | 22529.5211 | 1667.4227
2027-08-08 23:00 | 84.2199 | 1357.5711 | 1628.6483 | 921.7997 | 1230.2742 | 382.7284 | 1408.7284 | 4463.1277 | 8218.7004 | 2341.1097 | 22036.9079 | 1785.4362
2027-08-15 23:00 | 83.4721 | 1353.7069 | 1626.6679 | 929.3526 | 1257.2514 | 383.2699 | 1403.1276 | 4455.3801 | 8247.1437 | 2338.644 | 22078.0162 | 1647.3463
2027-08-22 23:00 | 87.822 | 1369.107 | 1688.9163 | 891.227 | 1314.5039 | 422.0102 | 1565.4982 | 4158.6869 | 8269.7821 | 2125.0272 | 21892.5808 | 1398.9137
2027-08-29 23:00 | 106.8971 | 1285.0904 | 1632.8181 | 898.0045 | 1237.1856 | 368.7509 | 1389.7234 | 4315.8455 | 8168.4011 | 2367.3863 | 21770.1028 | 1373.5444
2027-09-05 23:00 | 105.6315 | 1183.3541 | 1545.0633 | 916.9634 | 1188.0852 | 340.7776 | 1476.227 | 4358.3928 | 7966.0707 | 2359.1792 | 21439.7449 | 1731.1469
2027-09-12 23:00 | 87.8777 | 1110.5268 | 1365.6871 | 880.605 | 1269.1454 | 354.1988 | 1233.9115 | 4148.593 | 7719.7278 | 2095.9981 | 20266.2712 | 1976.5865
2027-09-19 23:00 | 98.2878 | 1188.4083 | 1453.1062 | 833.5052 | 1219.5864 | 344.8213 | 1114.1271 | 4045.7202 | 7105.9132 | 2335.8131 | 19739.2888 | 1766.7307
2027-09-26 23:00 | 91.5483 | 1149.9846 | 1328.1024 | 829.4007 | 1285.2826 | 370.2027 | 1280.9785 | 3883.3051 | 6759.9392 | 2161.0958 | 19139.8399 | 1666.0759
2027-10-03 23:00 | 83.6168 | 1184.9181 | 1333.6233 | 795.809 | 1333.6007 | 377.3516 | 1123.962 | 3859.7553 | 6587.6977 | 2140.8537 | 18821.1881 | 1376.7894
Back to main menu

## Table 1.1.2 Planned
Back to main menu
Table 1.1.2 Planned: Weekly Coincident Peak Demand by Zone
Week Ending | Planned Hourly Coincident Peak Demand (MW)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario | Load Forecast Uncertainty
2026-04-05 23:00 | 102.2519 | 1249.6738 | 1406.2029 | 612.8824 | 1455.3048 | 399.221 | 1149.5362 | 3675.9338 | 6490.1761 | 1844.0599 | 18385.2427 | 565.5318
2026-04-12 23:00 | 95.555 | 1223.7214 | 1376.5874 | 596.2721 | 1415.4034 | 392.2743 | 1120.3621 | 3635.3802 | 6256.2484 | 1842.4778 | 17954.2822 | 579.7828
2026-04-19 23:00 | 115.6608 | 1202.3194 | 1344.0218 | 567.9934 | 1368.5969 | 405.9545 | 1083.5923 | 3504.1961 | 6297.0873 | 1815.0455 | 17704.468 | 684.7229
2026-04-26 23:00 | 103.8157 | 1149.99 | 1301.8572 | 583.1676 | 1288.1039 | 364.1115 | 1058.2611 | 3536.8893 | 6172.8237 | 1882.3968 | 17441.4166 | 611.0689
2026-05-03 23:00 | 110.1586 | 1154.5125 | 1299.7513 | 540.8267 | 1254.9822 | 380.9108 | 1052.8386 | 3476.2159 | 6164.9746 | 1790.9151 | 17226.0863 | 630.6048
2026-05-10 23:00 | 103.7106 | 953.86 | 1195.2636 | 575.3645 | 1175.7528 | 385.2052 | 1085.6304 | 3515.4016 | 6353.3776 | 1913.8244 | 17257.3907 | 757.3017
2026-05-17 23:00 | 95.6409 | 1054.2513 | 1243.7565 | 582.374 | 1217.8198 | 347.2327 | 1163.1303 | 3520.4618 | 6469.0616 | 1654.9901 | 17348.719 | 1057.6708
2026-05-24 23:00 | 92.1498 | 1129.9022 | 1299.1798 | 669.5657 | 1192.5767 | 347.0446 | 1060.0637 | 3580.4075 | 6730.4623 | 1853.3916 | 17954.7439 | 1424.1393
2026-05-31 23:00 | 90.3871 | 1060.4073 | 1305.4749 | 631.833 | 1182.6664 | 339.2622 | 1215.248 | 3526.3243 | 7251.0158 | 1825.7595 | 18428.3786 | 2122.2379
2026-06-07 23:00 | 79.2177 | 1022.229 | 1310.334 | 739.1554 | 1169.7796 | 361.575 | 1212.7521 | 4073.8547 | 7240.7609 | 2046.5221 | 19256.1805 | 2227.6961
2026-06-14 23:00 | 80.2905 | 1164.8887 | 1413.1393 | 709.2108 | 1154.7861 | 369.042 | 1335.4215 | 3933.7174 | 7443.8192 | 2115.4106 | 19719.7262 | 2187.2199
2026-06-21 23:00 | 76.2351 | 1302.047 | 1684.4791 | 804.4032 | 1133.5326 | 333.0648 | 1251.3291 | 4145.8029 | 7945.346 | 2159.984 | 20836.2237 | 2002.8552
2026-06-28 23:00 | 84.1992 | 1244.0568 | 1505.1761 | 825.4645 | 1138.4638 | 337.4295 | 1305.8025 | 4505.204 | 8336.9708 | 2427.8192 | 21710.5863 | 1693.3771
2026-07-05 23:00 | 73.4927 | 1340.2884 | 1678.4365 | 830.0891 | 1118.0584 | 361.5694 | 1392.3041 | 4427.2632 | 8064.2208 | 2398.1028 | 21683.8255 | 1705.7683
2026-07-12 23:00 | 81.7 | 1248.7777 | 1611.291 | 816.2224 | 1156.3803 | 366.04 | 1539.298 | 4525.701 | 8604.8252 | 2436.2641 | 22386.4998 | 1776.3979
2026-07-19 23:00 | 77.926 | 1345.6858 | 1639.913 | 821.9947 | 1162.2852 | 371.1634 | 1562.5865 | 4762.6039 | 8268.9981 | 2513.2018 | 22526.3585 | 1716.9988
2026-07-26 23:00 | 78.7816 | 1373.991 | 1711.5467 | 832.2773 | 1157.8643 | 386.7487 | 1430.0791 | 4609.5498 | 8536.0505 | 2428.087 | 22544.9759 | 1705.8787
2026-08-02 23:00 | 93.5152 | 1491.6476 | 1820.2317 | 848.8448 | 1293.6585 | 410.5267 | 1488.4496 | 4319.1278 | 8183.7773 | 2344.863 | 22294.6422 | 1631.6787
2026-08-09 23:00 | 96.3367 | 1331.5486 | 1600.8821 | 789.9617 | 1189.6518 | 366.4855 | 1455.7844 | 4395.0249 | 8279.4618 | 2259.7128 | 21764.8503 | 1794.5396
2026-08-16 23:00 | 90.9357 | 1313.6296 | 1612.9718 | 821.5433 | 1188.6799 | 402.2807 | 1256.9444 | 4400.6871 | 8417.865 | 2312.131 | 21817.6686 | 1614.4493
2026-08-23 23:00 | 90.4011 | 1337.0983 | 1598.9086 | 807.6634 | 1223.2693 | 390.2046 | 1397.552 | 4543.6676 | 7858.6057 | 2410.5061 | 21657.8766 | 1386.0845
2026-08-30 23:00 | 98.215 | 1272.7788 | 1621.6 | 771.06 | 1226.1949 | 368.3808 | 1479.5595 | 4215.0847 | 8154.7143 | 2320.1295 | 21527.7175 | 1407.7311
2026-09-06 23:00 | 101.4181 | 1235.0684 | 1544.7107 | 762.1758 | 1191.2395 | 371.6915 | 1419.2501 | 4261.4742 | 7841.9483 | 2369.7196 | 21098.6963 | 1785.7035
2026-09-13 23:00 | 93.5779 | 1122.5401 | 1329.0269 | 748.78 | 1129.0972 | 347.1577 | 1096.9363 | 4234.864 | 7440.1263 | 2359.9421 | 19902.0485 | 1994.6572
2026-09-20 23:00 | 77.3777 | 1128.3994 | 1426.6732 | 709.4588 | 1213.8989 | 367.9212 | 1256.2769 | 3944.949 | 7181.2291 | 2102.8118 | 19408.9959 | 1728.7287
2026-09-27 23:00 | 92.6534 | 1068.975 | 1274.7951 | 653.6639 | 1236.3607 | 351.5739 | 1289.4305 | 3712.9741 | 7124.875 | 2034.9273 | 18840.229 | 1631.4449
2026-10-04 23:00 | 87.9806 | 1156.7038 | 1304.0978 | 694.7117 | 1239.306 | 375.3999 | 1043.6676 | 3930.1469 | 6677.356 | 2226.0203 | 18735.3906 | 1197.6541
2026-10-11 23:00 | 67.3369 | 1160.7393 | 1292.6674 | 681.8567 | 1274.0705 | 346.8044 | 1064.0539 | 3739.5274 | 6365.3285 | 2030.7086 | 18023.0937 | 886.6486
2026-10-18 23:00 | 86.9824 | 1222.0664 | 1368.5266 | 655.8363 | 1300.9316 | 378.8718 | 1104.3429 | 3675.1284 | 6247.0215 | 1919.0382 | 17958.7462 | 605.7631
2026-10-25 23:00 | 95.97 | 1230.5317 | 1392.9082 | 658.077 | 1316.2589 | 407.8464 | 1063.5337 | 3720.9416 | 6395.3261 | 1998.6151 | 18280.0087 | 456.385
2026-11-01 23:00 | 91.1081 | 1240.9903 | 1390.5096 | 670.9994 | 1332.7573 | 425.94 | 1125.7621 | 3787.4341 | 6510.8356 | 2010.6092 | 18586.9456 | 447.7858
2026-11-08 23:00 | 107.1588 | 1272.5615 | 1481.2893 | 678.2232 | 1375.5219 | 479.2944 | 1185.5286 | 3833.3151 | 6566.322 | 2141.1568 | 19120.3716 | 484.4094
2026-11-15 23:00 | 109.2351 | 1351.9778 | 1528.0135 | 703.0251 | 1409.4302 | 460.068 | 1268.3623 | 3881.9961 | 6744.5687 | 2163.5982 | 19620.2749 | 629.23
2026-11-22 23:00 | 110.5333 | 1384.4391 | 1554.638 | 725.9949 | 1416.3017 | 481.3763 | 1276.877 | 4013.6471 | 6961.4768 | 2251.9815 | 20177.2657 | 637.7032
2026-11-29 23:00 | 112.2057 | 1441.4894 | 1604.1736 | 745.1493 | 1465.2782 | 494.1087 | 1322.3663 | 4176.67 | 7117.0391 | 2274.66 | 20753.1402 | 544.2409
2026-12-06 23:00 | 119.7911 | 1458.2423 | 1768.9113 | 740.8393 | 1537.008 | 520.098 | 1385.6934 | 4116.4054 | 7081.7506 | 2317.9311 | 21046.6704 | 552.3492
2026-12-13 23:00 | 124.0225 | 1486.5981 | 1801.8652 | 756.9601 | 1531.099 | 576.6682 | 1395.4573 | 4277.7655 | 7131.5153 | 2309.7118 | 21391.6631 | 678.9496
2026-12-20 23:00 | 124.6476 | 1527.8532 | 1830.3621 | 763.0158 | 1568.4976 | 545.496 | 1468.8239 | 4282.7937 | 7219.3387 | 2276.2435 | 21607.072 | 700.0377
2026-12-27 23:00 | 118.5026 | 1430.0734 | 1762.1452 | 755.7993 | 1494.9976 | 519.6005 | 1373.5093 | 4250.2188 | 7006.554 | 2335.0453 | 21046.4459 | 725.1088
2027-01-03 23:00 | 125.5546 | 1517.3617 | 1823.3193 | 739.4575 | 1518.6273 | 518.7984 | 1406.1401 | 4248.8116 | 7040.3288 | 2333.9601 | 21272.3594 | 745.2127
2027-01-10 23:00 | 139.1235 | 1646.7047 | 1903.8225 | 743.9598 | 1599.0623 | 556.0596 | 1425.3967 | 4372.5831 | 7340.1439 | 2305.1313 | 22031.9874 | 826.9467
2027-01-17 23:00 | 129.9004 | 1635.3 | 1868.0533 | 744.053 | 1590.6442 | 495.4868 | 1442.361 | 4329.0287 | 7298.0501 | 2391.9501 | 21924.8274 | 840.9227
2027-01-24 23:00 | 139.1252 | 1591.8691 | 1788.0661 | 759.2484 | 1539.0621 | 498.6622 | 1411.9307 | 4460.5471 | 7422.2424 | 2391.0984 | 22001.8516 | 872.0555
2027-01-31 23:00 | 138.4525 | 1655.7156 | 1868.7184 | 742.1421 | 1579.5355 | 523.0783 | 1436.2351 | 4360.6774 | 7426.1117 | 2253.7625 | 21984.429 | 831.5717
2027-02-07 23:00 | 122.5179 | 1567.0729 | 1803.1036 | 749.5895 | 1585.3162 | 495.7926 | 1412.8537 | 4236.5776 | 7312.7718 | 2144.6702 | 21430.2661 | 755.1531
2027-02-14 23:00 | 123.639 | 1524.3131 | 1736.6328 | 739.096 | 1543.8268 | 472.9642 | 1360.8425 | 4264.1962 | 7327.3444 | 2292.6923 | 21385.5472 | 750.2706
2027-02-21 23:00 | 117.8963 | 1523.6857 | 1788.6476 | 723.4693 | 1591.9986 | 528.8241 | 1376.3377 | 4072.2882 | 7181.363 | 2158.2368 | 21062.7473 | 759.7449
2027-02-28 23:00 | 121.3907 | 1500.9575 | 1720.963 | 736.5965 | 1566.0819 | 505.8369 | 1343.3418 | 4159.9276 | 7292.1567 | 2060.5037 | 21007.7564 | 659.3427
2027-03-07 23:00 | 111.9566 | 1480.0474 | 1655.5179 | 715.7642 | 1567.5098 | 469.3123 | 1355.299 | 4047.8623 | 7086.251 | 1995.5354 | 20485.0561 | 676.4356
2027-03-14 23:00 | 117.0149 | 1380.9199 | 1583.2438 | 717.8975 | 1533.9304 | 437.5855 | 1248.8774 | 4066.9642 | 6919.6484 | 2021.2752 | 20027.3569 | 693.5968
2027-03-21 23:00 | 104.089 | 1355.7085 | 1556.3643 | 703.1906 | 1535.0549 | 438.3598 | 1213.4332 | 3889.0939 | 6711.5096 | 2023.467 | 19530.2707 | 634.6554
2027-03-28 23:00 | 108.2581 | 1279.3483 | 1489.8326 | 675.2975 | 1511.6063 | 465.2412 | 1166.313 | 3818.2156 | 6540.8698 | 2033.6694 | 19088.6518 | 552.1422
2027-04-04 23:00 | 102.4473 | 1215.4315 | 1394.4923 | 690.7044 | 1448.0898 | 398.5689 | 1107.6755 | 3790.9568 | 6453.1018 | 1991.8175 | 18593.2859 | 534.3369
2027-04-11 23:00 | 92.83 | 1236.6164 | 1397.0978 | 686.7303 | 1470.9984 | 396.6365 | 1131.9949 | 3728.3698 | 6333.8012 | 1846.9003 | 18321.9755 | 545.1945
2027-04-18 23:00 | 110.6751 | 1109.7478 | 1326.4449 | 689.4886 | 1333.4753 | 395.9612 | 1083.3005 | 3684.5544 | 6288.2631 | 1983.7033 | 18005.6142 | 692.1307
2027-04-25 23:00 | 98.0958 | 1162.9202 | 1292.6931 | 659.8374 | 1346.8062 | 360.8224 | 1082.9535 | 3659.0869 | 6220.2837 | 1831.3711 | 17714.8703 | 626.5332
2027-05-02 23:00 | 100.3424 | 1148.4215 | 1285.8651 | 658.3567 | 1341.3246 | 401.7404 | 1072.7631 | 3554.6318 | 6186.8282 | 1746.0513 | 17496.3252 | 606.6183
2027-05-09 23:00 | 98.9638 | 1148.7614 | 1318.6751 | 660.2974 | 1346.8028 | 372.1228 | 1071.1468 | 3600.6716 | 6145.7148 | 1765.3631 | 17528.5197 | 738.3346
2027-05-16 23:00 | 81.3691 | 922.0207 | 1161.427 | 683.2029 | 1160.3494 | 321.8036 | 1058.7942 | 3967.4126 | 6166.5916 | 2044.9147 | 17567.8857 | 986.9986
2027-05-23 23:00 | 97.9414 | 1220.0055 | 1412.6935 | 683.2722 | 1350.4817 | 360.3123 | 1125.2596 | 3710.8756 | 6491.4844 | 1794.0303 | 18246.3565 | 1333.7615
2027-05-30 23:00 | 74.5744 | 1169.5558 | 1408.801 | 760.6123 | 1270.3126 | 336.4082 | 1162.4874 | 3669.5542 | 6671.5552 | 1890.6126 | 18414.4737 | 2054.7285
2027-06-06 23:00 | 76.233 | 1081.6101 | 1411.1741 | 777.5139 | 1259.3901 | 390.861 | 1382.1109 | 3711.5894 | 7444.4177 | 1814.2445 | 19349.1447 | 2232.6992
2027-06-13 23:00 | 99.2273 | 1050.4399 | 1369.4246 | 801.034 | 1186.4867 | 317.1385 | 1287.943 | 4134.6062 | 7397.6526 | 2241.223 | 19885.1757 | 2168.5913
2027-06-20 23:00 | 84.6729 | 1123.2159 | 1422.6977 | 841.2931 | 1113.2557 | 345.1122 | 1233.0702 | 4630.0251 | 7740.2786 | 2405.0253 | 20938.6467 | 2096.2554
2027-06-27 23:00 | 82.9065 | 1352.2169 | 1706.1522 | 868.3294 | 1268.2123 | 367.6116 | 1446.8102 | 4440.2757 | 8111.8425 | 2267.9624 | 21912.3195 | 1705.9135
2027-07-04 23:00 | 61.5901 | 1332.8955 | 1616.4063 | 920.0674 | 1185.051 | 372.5766 | 1619.2323 | 4417.9722 | 7963.867 | 2352.7549 | 21842.4133 | 1678.353
2027-07-11 23:00 | 77.6304 | 1321.7496 | 1678.3551 | 922.3461 | 1149.0253 | 390.8759 | 1513.5718 | 4666.6472 | 8489.8799 | 2445.0031 | 22655.0845 | 1778.406
2027-07-18 23:00 | 95.4244 | 1353.0406 | 1700.4454 | 911.8771 | 1181.7273 | 377.4825 | 1515.0375 | 4790.1517 | 8258.7588 | 2619.7232 | 22803.6685 | 1763.2613
2027-07-25 23:00 | 76.9599 | 1377.3419 | 1733.6064 | 935.7368 | 1203.9353 | 385.1608 | 1434.9913 | 4696.1711 | 8598.0712 | 2421.5299 | 22863.5045 | 1711.5669
2027-08-01 23:00 | 90.169 | 1495.5191 | 1821.8185 | 976.815 | 1290.0975 | 383.3447 | 1462.9143 | 4626.169 | 7968.2328 | 2492.537 | 22607.6168 | 1665.9966
2027-08-08 23:00 | 84.218 | 1357.5401 | 1651.2523 | 921.7787 | 1238.6561 | 382.7196 | 1408.6962 | 4521.1942 | 8218.5126 | 2341.0562 | 22125.624 | 1784.8107
2027-08-15 23:00 | 96.9945 | 1334.7142 | 1625.2377 | 908.2773 | 1268.1082 | 370.4551 | 1460.9267 | 4499.6546 | 8337.0238 | 2265.2952 | 22166.6873 | 1648.1333
2027-08-22 23:00 | 87.8034 | 1368.8176 | 1711.8343 | 891.0386 | 1323.1525 | 421.921 | 1565.1673 | 4217.8085 | 8268.0339 | 2124.578 | 21980.155 | 1399.5105
2027-08-29 23:00 | 106.8916 | 1285.0247 | 1654.9434 | 897.9586 | 1245.6156 | 368.7321 | 1389.6523 | 4374.3202 | 8167.9835 | 2367.2653 | 21858.3872 | 1373.6996
2027-09-05 23:00 | 105.5927 | 1182.9194 | 1567.4328 | 928.4682 | 1197.0037 | 340.6524 | 1475.6847 | 4417.1881 | 7963.1443 | 2358.3126 | 21536.3988 | 1730.0362
2027-09-12 23:00 | 87.877 | 1110.5175 | 1387.7914 | 892.3743 | 1278.2073 | 354.1958 | 1233.9011 | 4208.6236 | 7719.6625 | 2095.9804 | 20369.1308 | 1975.2118
2027-09-19 23:00 | 98.3018 | 1188.5771 | 1474.802 | 845.0668 | 1228.5753 | 344.8702 | 1114.2853 | 4104.6592 | 7106.9222 | 2336.1448 | 19842.2045 | 1766.2413
2027-09-26 23:00 | 91.5333 | 1149.7967 | 1350.6703 | 841.3104 | 1294.4088 | 370.1422 | 1280.7692 | 3944.105 | 6758.8348 | 2160.7427 | 19242.3134 | 1666.484
2027-10-03 23:00 | 98.879 | 1172.198 | 1351.1532 | 822.0232 | 1394.633 | 377.4147 | 1114.4367 | 3880.3255 | 6633.7101 | 2081.1006 | 18925.8738 | 1375.5564
Back to main menu

## Table 1.1.3 Firm
Back to main menu
Table 1.1.3 Firm: Weekly Energy Demand by Zone
Week Ending | Firm Weekly Normal Energy (GWh)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario
2026-04-05 23:00 | 14.906 | 165.9028 | 189.9808 | 91.4906 | 220.9672 | 64.2654 | 162.1374 | 531.4037 | 912.8604 | 272.4731 | 2626.3874
2026-04-12 23:00 | 14.0571 | 162.0481 | 184.2474 | 91.6198 | 216.1706 | 62.8288 | 157.6374 | 532.0702 | 908.2992 | 268.2089 | 2597.1875
2026-04-19 23:00 | 14.7885 | 156.5442 | 180.5693 | 87.5183 | 211.7851 | 61.6602 | 154.497 | 516.775 | 898.1847 | 265.667 | 2547.9893
2026-04-26 23:00 | 13.2357 | 148.3243 | 168.819 | 87.7565 | 208.555 | 57.9207 | 152.3416 | 522.7938 | 896.1942 | 262.7266 | 2518.6673
2026-05-03 23:00 | 14.7415 | 151.9432 | 177.978 | 87.1595 | 197.0135 | 59.6829 | 146.6958 | 510.9213 | 886.1456 | 268.4316 | 2500.7128
2026-05-10 23:00 | 13.7396 | 141.7473 | 173.7755 | 88.1265 | 196.6848 | 60.3604 | 147.8888 | 510.9219 | 891.7498 | 263.6923 | 2488.6869
2026-05-17 23:00 | 12.8293 | 141.2824 | 168.4651 | 87.3326 | 192.7894 | 55.2122 | 152.6657 | 513.9116 | 898.2187 | 260.3682 | 2483.0751
2026-05-24 23:00 | 12.6432 | 139.2253 | 171.7884 | 86.3538 | 196.0508 | 54.8426 | 150.7273 | 504.055 | 883.5776 | 254.1747 | 2453.4387
2026-05-31 23:00 | 11.3419 | 140.8851 | 169.5867 | 90.8061 | 191.9749 | 53.9153 | 153.7657 | 522.7774 | 924.5843 | 267.756 | 2527.3934
2026-06-07 23:00 | 12.8153 | 147.5058 | 182.0302 | 97.213 | 196.9941 | 60.2369 | 155.5647 | 543.2937 | 946.913 | 279.3016 | 2621.8683
2026-06-14 23:00 | 11.8782 | 147.7647 | 180.0585 | 98.4053 | 189.9249 | 56.0257 | 168.5689 | 541.7938 | 980.1885 | 284.7502 | 2659.3587
2026-06-21 23:00 | 11.3601 | 154.9494 | 188.1659 | 103.698 | 186.7703 | 54.812 | 161.7764 | 576.2161 | 1027.0652 | 297.2979 | 2762.1115
2026-06-28 23:00 | 12.7136 | 156.9875 | 191.1695 | 106.1182 | 197.6943 | 58.2538 | 177.199 | 589.5936 | 1041.5081 | 314.8246 | 2846.0621
2026-07-05 23:00 | 10.9104 | 164.9237 | 192.8663 | 108.9775 | 192.5459 | 56.679 | 163.8157 | 601.5836 | 1012.1128 | 321.6134 | 2826.0283
2026-07-12 23:00 | 10.3488 | 170.2771 | 202.3414 | 110.8398 | 197.6058 | 57.9504 | 184.5772 | 598.8806 | 1099.7657 | 308.7526 | 2941.3395
2026-07-19 23:00 | 11.7872 | 172.7012 | 199.433 | 114.3305 | 197.9215 | 57.6033 | 179.8351 | 628.7751 | 1078.0625 | 336.596 | 2977.0453
2026-07-26 23:00 | 11.7772 | 171.3492 | 201.8293 | 114.9454 | 194.8771 | 56.995 | 181.0296 | 630.2999 | 1083.1896 | 337.0342 | 2983.3263
2026-08-02 23:00 | 11.6581 | 171.1937 | 205.1738 | 111.189 | 197.4741 | 60.4834 | 182.2108 | 601.8906 | 1092.4429 | 320.9224 | 2954.6387
2026-08-09 23:00 | 12.2757 | 171.697 | 202.4985 | 112.3478 | 196.5477 | 57.4379 | 180.9684 | 589.5701 | 1053.0635 | 315.4535 | 2891.8602
2026-08-16 23:00 | 12.0948 | 168.6874 | 202.257 | 110.2439 | 200.978 | 58.6102 | 177.8868 | 584.1356 | 1063.87 | 309.1989 | 2887.9625
2026-08-23 23:00 | 12.8579 | 166.1292 | 194.6264 | 111.4508 | 205.1656 | 58.3597 | 169.5184 | 593.8015 | 1049.13 | 315.0054 | 2876.045
2026-08-30 23:00 | 13.0195 | 170.288 | 198.3347 | 108.9525 | 195.822 | 55.9071 | 176.5353 | 568.61 | 1052.7148 | 304.1717 | 2844.3556
2026-09-06 23:00 | 14.0237 | 162.4028 | 186.7777 | 106.8713 | 198.4272 | 56.0542 | 167.485 | 568.5733 | 995.8158 | 312.9539 | 2769.3849
2026-09-13 23:00 | 12.2983 | 147.5973 | 170.5803 | 103.5898 | 194.5859 | 54.6334 | 151.5742 | 557.2377 | 931.8427 | 309.3482 | 2633.2876
2026-09-20 23:00 | 11.8882 | 146.3052 | 173.2774 | 100.5968 | 195.6684 | 56.1534 | 160.4593 | 544.0947 | 944.8126 | 299.4048 | 2632.6607
2026-09-27 23:00 | 12.3466 | 150.6288 | 175.259 | 96.4707 | 202.454 | 57.7719 | 160.4937 | 527.3468 | 932.0213 | 280.4385 | 2595.2314
2026-10-04 23:00 | 11.7471 | 147.626 | 172.4355 | 100.0982 | 203.4696 | 59.8728 | 151.9418 | 529.7719 | 905.4995 | 287.9512 | 2570.4137
2026-10-11 23:00 | 10.9114 | 150.1267 | 171.5441 | 101.0618 | 203.1333 | 57.8952 | 150.3836 | 526.9237 | 901.9087 | 281.8631 | 2555.7517
2026-10-18 23:00 | 11.6464 | 153.0389 | 176.2461 | 99.9134 | 207.1645 | 58.9316 | 152.4988 | 517.444 | 885.0971 | 277.2272 | 2539.208
2026-10-25 23:00 | 12.712 | 159.4155 | 180.8235 | 102.0681 | 205.8648 | 61.0571 | 154.1181 | 537.3276 | 904.5073 | 292.2415 | 2610.1355
2026-11-01 23:00 | 12.5734 | 164.4838 | 185.3166 | 104.5365 | 205.3524 | 63.9624 | 159.3169 | 544.9599 | 915.5781 | 303.173 | 2659.2531
2026-11-08 23:00 | 13.7355 | 166.7701 | 192.5475 | 105.0605 | 209.7065 | 69.7472 | 159.4714 | 552.378 | 928.4655 | 310.81 | 2708.6923
2026-11-15 23:00 | 14.0814 | 176.6 | 200.4296 | 106.5165 | 217.7811 | 70.0079 | 170.4975 | 554.8713 | 946.3212 | 310.8328 | 2767.9393
2026-11-22 23:00 | 14.7264 | 184.1487 | 208.1853 | 109.5346 | 222.0446 | 73.3452 | 172.3598 | 565.8423 | 971.6029 | 322.4779 | 2844.2677
2026-11-29 23:00 | 15.8858 | 194.0696 | 216.9847 | 112.4099 | 229.3987 | 76.5029 | 178.8195 | 578.3901 | 990.7039 | 326.3604 | 2919.5254
2026-12-06 23:00 | 16.5995 | 197.1284 | 235.9326 | 112.8199 | 236.7381 | 79.6885 | 188.7704 | 589.0792 | 998.5463 | 331.5801 | 2986.883
2026-12-13 23:00 | 17.325 | 200.2728 | 243.577 | 114.1738 | 236.9354 | 88.4388 | 187.9057 | 606.3747 | 1002.6384 | 336.6832 | 3034.3248
2026-12-20 23:00 | 16.4776 | 200.8725 | 241.2783 | 115.8297 | 240.4411 | 82.6722 | 191.4972 | 610.7781 | 1010.5357 | 341.3694 | 3051.7518
2026-12-27 23:00 | 16.48 | 195.4042 | 236.6221 | 112.1677 | 236.1498 | 82.4769 | 182.541 | 583.3249 | 962.9964 | 331.5523 | 2939.7152
2027-01-03 23:00 | 15.8193 | 199.5028 | 242.0544 | 109.7669 | 245.7273 | 84.5213 | 186.1939 | 578.7581 | 960.0888 | 325.6962 | 2948.129
2027-01-10 23:00 | 18.3116 | 221.5274 | 250.0609 | 111.6539 | 243.4898 | 83.2042 | 197.1926 | 620.0555 | 1035.5979 | 337.6807 | 3118.7744
2027-01-17 23:00 | 18.7737 | 225.1268 | 256.5673 | 112.7463 | 248.8441 | 81.907 | 195.8409 | 626.1222 | 1035.9958 | 337.2959 | 3139.2198
2027-01-24 23:00 | 18.515 | 221.022 | 249.0453 | 115.5838 | 251.5626 | 80.6465 | 194.3968 | 629.704 | 1056.7396 | 348.7878 | 3166.0034
2027-01-31 23:00 | 18.9806 | 222.8326 | 253.9936 | 114.3178 | 251.8827 | 79.2828 | 197.3431 | 625.6922 | 1058.6806 | 339.8274 | 3162.8334
2027-02-07 23:00 | 17.4776 | 214.7526 | 247.5515 | 114.6698 | 251.8724 | 76.0213 | 198.0295 | 602.5026 | 1046.154 | 322.3464 | 3091.3777
2027-02-14 23:00 | 17.1112 | 210.8689 | 244.422 | 114.5039 | 254.3461 | 81.7562 | 192.195 | 600.0657 | 1048.2934 | 316.3186 | 3079.881
2027-02-21 23:00 | 17.4753 | 210.4306 | 243.3133 | 111.5627 | 257.1656 | 83.594 | 192.8556 | 579.4284 | 1018.1478 | 312.5591 | 3026.5323
2027-02-28 23:00 | 17.5866 | 202.163 | 237.5587 | 111.7354 | 250.078 | 78.979 | 191.0478 | 592.2545 | 1037.7626 | 303.6705 | 3022.836
2027-03-07 23:00 | 16.9179 | 189.7675 | 219.5298 | 110.7284 | 241.1005 | 70.4325 | 186.3578 | 585.666 | 1022.8842 | 306.5327 | 2949.9172
2027-03-14 23:00 | 16.6272 | 184.034 | 216.3045 | 107.4994 | 249.6877 | 72.1405 | 183.5547 | 574.8517 | 996.4019 | 290.2954 | 2891.3969
2027-03-21 23:00 | 15.485 | 177.6155 | 204.6452 | 107.0208 | 236.1943 | 69.2333 | 173.1281 | 567.6718 | 981.8394 | 294.0685 | 2826.902
2027-03-28 23:00 | 15.6285 | 170.9598 | 200.9492 | 102.5652 | 236.3351 | 71.2781 | 169.2903 | 543.1851 | 938.3452 | 284.9915 | 2733.528
2027-04-04 23:00 | 15.3593 | 167.6676 | 193.8277 | 104.8338 | 227.4876 | 67.1737 | 161.6685 | 545.1572 | 933.8069 | 277.736 | 2694.7184
2027-04-11 23:00 | 14.1738 | 161.9762 | 187.0471 | 105.1896 | 224.6372 | 63.4151 | 157.9508 | 542.9254 | 919.7393 | 270.2483 | 2647.3029
2027-04-18 23:00 | 14.4396 | 157.5908 | 180.8635 | 101.4649 | 222.0055 | 62.644 | 157.9018 | 524.9261 | 906.8115 | 259.0039 | 2587.6516
2027-04-25 23:00 | 13.6141 | 152.1696 | 176.2759 | 101.285 | 215.0389 | 59.011 | 153.9238 | 521.5191 | 902.8502 | 260.0479 | 2555.7354
2027-05-02 23:00 | 14.146 | 151.3109 | 175.1509 | 101.2069 | 207.0664 | 59.1272 | 150.7462 | 517.7839 | 897.2442 | 258.3591 | 2532.1417
2027-05-09 23:00 | 14.1585 | 145.2856 | 174.4703 | 101.9912 | 205.5888 | 56.2451 | 149.9567 | 521.5274 | 898.3135 | 257.3299 | 2524.8668
2027-05-16 23:00 | 13.4088 | 143.4147 | 173.6434 | 102.5815 | 198.9215 | 54.5805 | 147.7706 | 522.2032 | 890.4922 | 268.401 | 2515.4173
2027-05-23 23:00 | 13.1957 | 140.3582 | 173.5272 | 101.3922 | 205.8815 | 55.4169 | 152.6386 | 522.5233 | 909.4307 | 252.5015 | 2526.8658
2027-05-30 23:00 | 12.36 | 138.3402 | 171.0131 | 103.2858 | 201.9952 | 55.8734 | 149.4446 | 521.7764 | 900.0446 | 257.3443 | 2511.4776
2027-06-06 23:00 | 12.3638 | 146.0093 | 178.8104 | 111.4635 | 197.5399 | 55.6634 | 165.7604 | 534.9705 | 957.5998 | 280.6774 | 2640.8584
2027-06-13 23:00 | 12.3226 | 146.3027 | 177.3172 | 115.5282 | 195.8161 | 54.9785 | 161.5377 | 559.8274 | 970.7555 | 291.6944 | 2686.0802
2027-06-20 23:00 | 11.5909 | 146.608 | 180.8903 | 119.1077 | 198.0665 | 55.8406 | 163.8189 | 596.6436 | 999.788 | 311.2046 | 2783.559
2027-06-27 23:00 | 11.7598 | 158.7937 | 194.6396 | 122.0153 | 202.8814 | 57.2243 | 179.0995 | 588.1451 | 1052.9349 | 303.1644 | 2870.6578
2027-07-04 23:00 | 10.8589 | 170.241 | 204.9972 | 123.0347 | 201.3732 | 55.5737 | 186.181 | 573.0882 | 1031.3164 | 302.2178 | 2858.8821
2027-07-11 23:00 | 11.0913 | 179.7371 | 208.325 | 127.3615 | 195.6816 | 54.7734 | 186.5255 | 599.1912 | 1084.1662 | 317.0863 | 2963.939
2027-07-18 23:00 | 10.7694 | 173.0334 | 208.552 | 128.7535 | 204.1826 | 59.7607 | 187.3356 | 612.4085 | 1114.4374 | 314.0814 | 3013.3144
2027-07-25 23:00 | 11.6936 | 170.4445 | 202.965 | 131.8903 | 201.8338 | 56.7644 | 185.2513 | 631.4477 | 1097.2461 | 333.4722 | 3023.0089
2027-08-01 23:00 | 11.6168 | 173.2941 | 208.2495 | 128.7535 | 209.3291 | 60.7713 | 187.5939 | 613.6245 | 1080.0685 | 322.0024 | 2995.3036
2027-08-08 23:00 | 12.151 | 169.4379 | 200.1021 | 132.0574 | 207.9802 | 57.5439 | 174.8405 | 598.8523 | 1062.6831 | 320.805 | 2936.4534
2027-08-15 23:00 | 11.9465 | 165.854 | 195.3851 | 130.8822 | 206.9198 | 57.0951 | 171.6482 | 605.7152 | 1060.5436 | 320.833 | 2926.8227
2027-08-22 23:00 | 12.9609 | 168.6443 | 200.8071 | 128.8932 | 207.6902 | 58.6167 | 183.8818 | 582.4488 | 1057.66 | 310.4559 | 2912.0589
2027-08-29 23:00 | 13.0959 | 166.2194 | 195.6517 | 129.5796 | 207.6572 | 56.9209 | 170.2259 | 591.703 | 1041.321 | 313.0529 | 2885.4274
2027-09-05 23:00 | 13.1036 | 153.0492 | 181.9907 | 128.9111 | 202.0023 | 56.0823 | 174.9532 | 590.5078 | 1003.1841 | 320.5629 | 2824.3473
2027-09-12 23:00 | 13.138 | 151.6996 | 175.7937 | 125.2815 | 203.8818 | 54.5189 | 157.1906 | 543.39 | 959.5501 | 298.7343 | 2683.1786
2027-09-19 23:00 | 13.7747 | 152.8437 | 178.6425 | 122.3788 | 204.8461 | 56.703 | 159.1212 | 550.611 | 930.2684 | 308.409 | 2677.5985
2027-09-26 23:00 | 11.7437 | 149.1524 | 174.1154 | 120.9571 | 205.9454 | 57.9966 | 160.3921 | 540.6205 | 920.8847 | 293.2263 | 2635.0342
2027-10-03 23:00 | 11.67 | 152.9865 | 173.0561 | 122.3517 | 204.5773 | 58.0702 | 156.3983 | 535.7619 | 907.3883 | 295.4898 | 2617.7502
Back to main menu

## Table 1.1.3 Planned
Back to main menu
Table 1.1.3 Planned: Weekly Energy Demand by Zone
Week Ending | Planned Weekly Normal Energy (GWh)
| Bruce | East | Essa | Niagara | NorthEast | NorthWest | Ottawa | SouthWest | Toronto | West | Ontario
2026-04-05 23:00 | 14.906 | 165.9028 | 189.9808 | 91.4906 | 220.9672 | 64.2654 | 162.1374 | 531.4037 | 912.8604 | 272.4731 | 2626.3874
2026-04-12 23:00 | 14.0571 | 162.0481 | 184.2474 | 91.6198 | 216.1706 | 62.8288 | 157.6374 | 532.0702 | 908.2992 | 268.2089 | 2597.1875
2026-04-19 23:00 | 14.7885 | 156.5442 | 180.5693 | 87.5183 | 211.7851 | 61.6602 | 154.497 | 516.775 | 898.1847 | 265.667 | 2547.9893
2026-04-26 23:00 | 13.2357 | 148.3243 | 168.819 | 87.7565 | 208.555 | 57.9207 | 152.3416 | 522.7938 | 896.1942 | 262.7266 | 2518.6673
2026-05-03 23:00 | 14.7415 | 151.9432 | 177.978 | 87.1595 | 197.0135 | 59.6829 | 146.6958 | 510.9213 | 886.1456 | 268.4316 | 2500.7128
2026-05-10 23:00 | 13.7396 | 141.7473 | 173.7755 | 88.1265 | 196.6848 | 60.3604 | 147.8888 | 510.9219 | 891.7498 | 263.6923 | 2488.6869
2026-05-17 23:00 | 12.8293 | 141.2824 | 168.4651 | 87.3326 | 192.7894 | 55.2122 | 152.6657 | 513.9116 | 898.2187 | 260.3682 | 2483.0751
2026-05-24 23:00 | 12.6432 | 139.2253 | 171.7884 | 86.3538 | 196.0508 | 54.8426 | 150.7273 | 504.055 | 883.5776 | 254.1747 | 2453.4387
2026-05-31 23:00 | 11.3419 | 140.8851 | 169.5867 | 90.8061 | 191.9749 | 53.9153 | 153.7657 | 522.7774 | 924.5843 | 267.756 | 2527.3934
2026-06-07 23:00 | 12.8153 | 147.5058 | 182.0302 | 97.213 | 196.9941 | 60.2369 | 155.5647 | 543.2937 | 946.913 | 279.3016 | 2621.8683
2026-06-14 23:00 | 11.8782 | 147.7647 | 180.0585 | 98.4053 | 189.9249 | 56.0257 | 168.5689 | 541.7938 | 980.1885 | 284.7502 | 2659.3587
2026-06-21 23:00 | 11.3601 | 154.9494 | 188.1659 | 103.698 | 186.7703 | 54.812 | 161.7764 | 576.2161 | 1027.0652 | 297.2979 | 2762.1115
2026-06-28 23:00 | 12.7136 | 156.9875 | 191.1695 | 106.1182 | 197.6943 | 58.2538 | 177.199 | 589.5936 | 1041.5081 | 314.8246 | 2846.0621
2026-07-05 23:00 | 10.9104 | 164.9237 | 192.8663 | 108.9775 | 192.5459 | 56.679 | 163.8157 | 601.5836 | 1012.1128 | 321.6134 | 2826.0283
2026-07-12 23:00 | 10.3488 | 170.2771 | 202.3414 | 110.8398 | 197.6058 | 57.9504 | 184.5772 | 598.8806 | 1099.7657 | 308.7526 | 2941.3395
2026-07-19 23:00 | 11.7872 | 172.7012 | 199.433 | 114.3305 | 197.9215 | 57.6033 | 179.8351 | 628.7751 | 1078.0625 | 336.596 | 2977.0453
2026-07-26 23:00 | 11.7772 | 171.3492 | 201.8293 | 114.9454 | 194.8771 | 56.995 | 181.0296 | 630.2999 | 1083.1896 | 337.0342 | 2983.3263
2026-08-02 23:00 | 11.6581 | 171.1937 | 205.1738 | 111.189 | 197.4741 | 60.4834 | 182.2108 | 601.8906 | 1092.4429 | 320.9224 | 2954.6387
2026-08-09 23:00 | 12.2757 | 171.697 | 202.4985 | 112.3478 | 196.5477 | 57.4379 | 180.9684 | 589.5701 | 1053.0635 | 315.4535 | 2891.8602
2026-08-16 23:00 | 12.0948 | 168.6874 | 202.257 | 110.2439 | 200.978 | 58.6102 | 177.8868 | 584.1356 | 1063.87 | 309.1989 | 2887.9625
2026-08-23 23:00 | 12.8579 | 166.1292 | 194.6264 | 111.4508 | 205.1656 | 58.3597 | 169.5184 | 593.8015 | 1049.13 | 315.0054 | 2876.045
2026-08-30 23:00 | 13.0195 | 170.288 | 198.3347 | 108.9525 | 195.822 | 55.9071 | 176.5353 | 568.61 | 1052.7148 | 304.1717 | 2844.3556
2026-09-06 23:00 | 14.0237 | 162.4028 | 186.7777 | 106.8713 | 198.4272 | 56.0542 | 167.485 | 568.5733 | 995.8158 | 312.9539 | 2769.3849
2026-09-13 23:00 | 12.2983 | 147.5973 | 170.5803 | 103.5898 | 194.5859 | 54.6334 | 151.5742 | 557.2377 | 931.8427 | 309.3482 | 2633.2876
2026-09-20 23:00 | 11.8882 | 146.3052 | 173.2774 | 100.5968 | 195.6684 | 56.1534 | 160.4593 | 544.0947 | 944.8126 | 299.4048 | 2632.6607
2026-09-27 23:00 | 12.3466 | 150.6288 | 175.259 | 96.4707 | 202.454 | 57.7719 | 160.4937 | 527.3468 | 932.0213 | 280.4385 | 2595.2314
2026-10-04 23:00 | 11.7471 | 147.626 | 172.4355 | 100.0982 | 203.4696 | 59.8728 | 151.9418 | 529.7719 | 905.4995 | 287.9512 | 2570.4137
2026-10-11 23:00 | 10.9114 | 150.1267 | 171.5441 | 101.0618 | 203.1333 | 57.8952 | 150.3836 | 526.9237 | 901.9087 | 281.8631 | 2555.7517
2026-10-18 23:00 | 11.6464 | 153.0389 | 176.2461 | 99.9134 | 207.1645 | 58.9316 | 152.4988 | 517.444 | 885.0971 | 277.2272 | 2539.208
2026-10-25 23:00 | 12.712 | 159.4155 | 180.8235 | 102.0681 | 205.8648 | 61.0571 | 154.1181 | 537.3276 | 904.5073 | 292.2415 | 2610.1355
2026-11-01 23:00 | 12.5734 | 164.4838 | 185.3166 | 104.5365 | 205.3524 | 63.9624 | 159.3169 | 544.9599 | 915.5781 | 303.173 | 2659.2531
2026-11-08 23:00 | 13.7355 | 166.7701 | 192.5475 | 105.0605 | 209.7065 | 69.7472 | 159.4714 | 552.378 | 928.4655 | 310.81 | 2708.6923
2026-11-15 23:00 | 14.0814 | 176.6 | 200.4296 | 106.5165 | 217.7811 | 70.0079 | 170.4975 | 554.8713 | 946.3212 | 310.8328 | 2767.9393
2026-11-22 23:00 | 14.7264 | 184.1487 | 208.1853 | 109.5346 | 222.0446 | 73.3452 | 172.3598 | 565.8423 | 971.6029 | 322.4779 | 2844.2677
2026-11-29 23:00 | 15.8858 | 194.0696 | 216.9847 | 112.4099 | 229.3987 | 76.5029 | 178.8195 | 578.3901 | 990.7039 | 326.3604 | 2919.5254
2026-12-06 23:00 | 16.5995 | 197.1284 | 235.9326 | 112.8199 | 236.7381 | 79.6885 | 188.7704 | 589.0792 | 998.5463 | 331.5801 | 2986.883
2026-12-13 23:00 | 17.325 | 200.2728 | 243.577 | 114.1738 | 236.9354 | 88.4388 | 187.9057 | 606.3747 | 1002.6384 | 336.6832 | 3034.3248
2026-12-20 23:00 | 16.4776 | 200.8725 | 241.2783 | 115.8297 | 240.4411 | 82.6722 | 191.4972 | 610.7781 | 1010.5357 | 341.3694 | 3051.7518
2026-12-27 23:00 | 16.48 | 195.4042 | 236.6221 | 112.1677 | 236.1498 | 82.4769 | 182.541 | 583.3249 | 962.9964 | 331.5523 | 2939.7152
2027-01-03 23:00 | 16.7072 | 203.8892 | 241.8311 | 109.5501 | 237.144 | 77.2991 | 190.496 | 582.2742 | 968.4118 | 322.3674 | 2949.9702
2027-01-10 23:00 | 18.312 | 221.5318 | 251.0618 | 111.656 | 243.9505 | 83.2058 | 197.1965 | 622.9532 | 1035.6185 | 337.6874 | 3123.1735
2027-01-17 23:00 | 18.7742 | 225.1336 | 257.5632 | 112.7497 | 249.304 | 81.9094 | 195.8468 | 629.0046 | 1036.0273 | 337.3061 | 3143.6188
2027-01-24 23:00 | 18.5141 | 221.0109 | 250.0795 | 115.578 | 252.029 | 80.6424 | 194.3871 | 632.7039 | 1056.6871 | 348.7704 | 3170.4024
2027-01-31 23:00 | 18.9801 | 222.8266 | 255.0167 | 114.3146 | 252.3472 | 79.2806 | 197.3378 | 628.6588 | 1058.652 | 339.8181 | 3167.2325
2027-02-07 23:00 | 17.4778 | 214.7556 | 248.8729 | 114.6714 | 252.4866 | 76.0224 | 198.0323 | 606.3703 | 1046.1688 | 322.3508 | 3097.2089
2027-02-14 23:00 | 17.4895 | 212.9506 | 245.697 | 115.6343 | 251.2107 | 76.195 | 193.7112 | 603.2348 | 1044.2809 | 325.3082 | 3085.7123
2027-02-21 23:00 | 17.4756 | 210.4339 | 244.6332 | 111.5644 | 257.7802 | 83.5953 | 192.8586 | 583.2947 | 1018.1636 | 312.5641 | 3032.3635
2027-02-28 23:00 | 17.5869 | 202.1659 | 238.8796 | 111.737 | 250.6924 | 78.9801 | 191.0505 | 596.1226 | 1037.7775 | 303.6748 | 3028.6673
2027-03-07 23:00 | 16.9175 | 189.7629 | 220.964 | 110.7256 | 241.7705 | 70.4308 | 186.3533 | 589.9149 | 1022.8589 | 306.525 | 2956.2233
2027-03-14 23:00 | 16.6272 | 184.0344 | 217.7272 | 107.4996 | 250.3559 | 72.1406 | 183.555 | 579.0637 | 996.4035 | 290.296 | 2897.703
2027-03-21 23:00 | 15.4845 | 177.61 | 206.0808 | 107.0174 | 236.8647 | 69.2311 | 173.1226 | 571.9289 | 981.8086 | 294.0594 | 2833.2081
2027-03-28 23:00 | 15.6285 | 170.9589 | 202.3744 | 102.5646 | 237.0036 | 71.2777 | 169.2894 | 547.4063 | 938.3404 | 284.9902 | 2739.8341
2027-04-04 23:00 | 14.3985 | 164.2418 | 192.4179 | 107.1764 | 224.4577 | 63.5859 | 160.7744 | 551.4717 | 942.554 | 280.79 | 2701.8683
2027-04-11 23:00 | 14.1745 | 161.9843 | 188.8036 | 105.1948 | 225.4618 | 63.4183 | 157.9587 | 548.0901 | 919.7852 | 270.2619 | 2655.1332
2027-04-18 23:00 | 14.4404 | 157.5999 | 182.617 | 101.4706 | 222.8297 | 62.6476 | 157.9109 | 530.0835 | 906.8635 | 259.0187 | 2595.4818
2027-04-25 23:00 | 13.6137 | 152.1649 | 178.065 | 101.2817 | 215.8677 | 59.0091 | 153.9192 | 526.7812 | 902.8231 | 260.0401 | 2563.5657
2027-05-02 23:00 | 14.1468 | 151.3193 | 176.9732 | 101.2124 | 207.9296 | 59.1305 | 150.7546 | 523.1856 | 897.2948 | 258.3736 | 2540.3205
2027-05-09 23:00 | 14.1581 | 145.2816 | 176.5829 | 101.9882 | 206.5494 | 56.2435 | 149.9526 | 527.628 | 898.2892 | 257.3228 | 2533.9963
2027-05-16 23:00 | 13.4088 | 143.4152 | 175.7429 | 102.5818 | 199.8802 | 54.5806 | 147.7711 | 528.2683 | 890.4954 | 268.4024 | 2524.5468
2027-05-23 23:00 | 13.5081 | 144.4561 | 178.8787 | 101.7497 | 206.4158 | 56.2683 | 150.8721 | 522.1627 | 907.0226 | 254.6612 | 2535.9953
2027-05-30 23:00 | 11.9002 | 141.1479 | 174.3712 | 104.0739 | 200.3765 | 53.205 | 152.6828 | 515.3824 | 907.6621 | 259.8051 | 2520.6071
2027-06-06 23:00 | 12.3628 | 145.9979 | 181.3131 | 111.4544 | 198.7087 | 55.6589 | 165.747 | 542.3865 | 957.5227 | 280.6557 | 2651.8076
2027-06-13 23:00 | 12.3219 | 146.2944 | 179.884 | 115.5213 | 197.0124 | 54.9752 | 161.5287 | 567.4236 | 970.7019 | 291.6783 | 2697.3417
2027-06-20 23:00 | 11.59 | 146.5972 | 183.465 | 119.0988 | 199.2646 | 55.8364 | 163.8071 | 604.2612 | 999.7178 | 311.1824 | 2794.8205
2027-06-27 23:00 | 11.7576 | 158.7656 | 197.2639 | 121.9935 | 204.0905 | 57.2141 | 179.0684 | 595.9036 | 1052.7513 | 303.1108 | 2881.9192
2027-07-04 23:00 | 11.3172 | 166.8629 | 201.6996 | 122.7177 | 207.8226 | 57.5906 | 185.4781 | 589.6706 | 1022.0185 | 306.0666 | 2871.2444
2027-07-11 23:00 | 11.0938 | 179.7778 | 211.2079 | 127.39 | 197.0368 | 54.7857 | 186.5683 | 607.6156 | 1084.4147 | 317.1582 | 2977.0489
2027-07-18 23:00 | 11.5115 | 172.6843 | 206.7664 | 130.6246 | 205.354 | 58.3087 | 180.5494 | 634.1156 | 1097.2482 | 329.2616 | 3026.4243
2027-07-25 23:00 | 11.6939 | 170.449 | 205.9423 | 131.8937 | 203.2122 | 56.7658 | 185.2564 | 640.1465 | 1097.277 | 333.482 | 3036.1188
2027-08-01 23:00 | 11.616 | 173.2819 | 211.2828 | 128.744 | 210.7413 | 60.7669 | 187.5807 | 622.6066 | 1079.9927 | 321.9794 | 3008.5924
2027-08-08 23:00 | 12.1501 | 169.4251 | 203.4733 | 132.0469 | 209.5305 | 57.5394 | 174.8276 | 608.7115 | 1062.6038 | 320.7807 | 2951.0888
2027-08-15 23:00 | 12.3166 | 169.1509 | 203.4392 | 130.3602 | 203.3631 | 56.75 | 180.5444 | 605.4465 | 1066.8044 | 313.2827 | 2941.458
2027-08-22 23:00 | 12.9618 | 168.6566 | 204.1079 | 128.9023 | 209.2258 | 58.621 | 183.8956 | 592.1047 | 1057.7397 | 310.4787 | 2926.6943
2027-08-29 23:00 | 13.0964 | 166.2254 | 198.97 | 129.584 | 209.1966 | 56.9229 | 170.2324 | 601.4094 | 1041.3614 | 313.0643 | 2900.0628
2027-09-05 23:00 | 13.1062 | 153.0803 | 185.316 | 130.3021 | 203.5649 | 56.0937 | 174.9888 | 600.2658 | 1003.3898 | 320.6277 | 2840.7354
2027-09-12 23:00 | 13.1389 | 151.7098 | 179.1855 | 127.2449 | 205.4749 | 54.5225 | 157.2014 | 553.3996 | 959.6159 | 298.7543 | 2700.2476
2027-09-19 23:00 | 13.775 | 152.8468 | 182.0465 | 124.3506 | 206.4409 | 56.7044 | 159.1242 | 560.6702 | 930.291 | 308.4178 | 2694.6675
2027-09-26 23:00 | 11.7436 | 149.1514 | 177.5328 | 122.9344 | 207.542 | 57.9962 | 160.391 | 550.7082 | 920.8793 | 293.2243 | 2652.1033
2027-10-03 23:00 | 12.7945 | 150.9472 | 179.2621 | 124.6584 | 215.6085 | 59.5059 | 153.348 | 542.1951 | 912.3668 | 284.9421 | 2635.6287
Back to main menu

## Table 1.2 Firm
Back to main menu
Table 1.2 Firm: Forecasted Seasonal Peaks
Season | Firm Normal Weather Peak (MW) | Firm Extreme Weather Peak (MW)
Summer 2026 | 23973.6189 | 26248.5909
Winter 2026-27 | 22630.4034 | 23702.6123
Summer 2027 | 24070.4954 | 26456.1025
Back to main menu

## Table 1.2 Planned
Back to main menu
Table 1.2 Planned: Forecasted Seasonal Peaks
Season | Planned Normal Weather Peak (MW) | Planned Extreme Weather Peak (MW)
Summer 2026 | 23973.6189 | 26248.5909
Winter 2026-27 | 22657.0485 | 23729.1832
Summer 2027 | 24148.4464 | 26533.4523
Back to main menu

## Table 1.3
Back to main menu
Table 1.3: Large Step Load Impacts, Firm and Planned Demand
| Firm |  | Planned
Demand Forecast | Energy (GWh) | Peak (MW) | Energy (GWh) | Peak (MW)
Summer 2026 | 286.8758 | 147.9757 | 286.8758 | 147.9757
Winter 2026-27 | 354.0063 | 201.4608 | 396.7687 | 236.0875
Summer 2027 | 707.2658 | 343.7165 | 878.4637 | 431.1535
Back to main menu

## Table 1.4 Firm
Back to main menu
Table 1.4 Firm: Weekly Energy and Peak Demand Forecast
Week | Firm Normal Peak | Firm Extreme Peak | Load Forecast Uncertainty | Firm Normal Energy Demand
Week Ending | (MW) | (MW) | (MW) | (GWh)
2026-04-05 23:00 | 18384.9856 | 19490.3749 | 565.9887 | 2626.3874
2026-04-12 23:00 | 17954.1126 | 18983.3823 | 579.6748 | 2597.1875
2026-04-19 23:00 | 17704.4692 | 18906.9571 | 683.878 | 2547.9893
2026-04-26 23:00 | 17441.4331 | 18506.4362 | 611.1489 | 2518.6673
2026-05-03 23:00 | 17226.1989 | 18554.3779 | 630.4626 | 2500.7128
2026-05-10 23:00 | 17257.6517 | 19256.5915 | 756.5348 | 2488.6869
2026-05-17 23:00 | 17349.1867 | 20250.5755 | 1058.1867 | 2483.0751
2026-05-24 23:00 | 17954.2374 | 21206.4812 | 1424.7734 | 2453.4387
2026-05-31 23:00 | 18428.2577 | 22196.4803 | 2122.9778 | 2527.3934
2026-06-07 23:00 | 19255.558 | 23347.3139 | 2228.7139 | 2621.8683
2026-06-14 23:00 | 19718.2415 | 23597.9343 | 2187.4856 | 2659.3587
2026-06-21 23:00 | 20835.4507 | 24602.2291 | 2004.776 | 2762.1115
2026-06-28 23:00 | 21711.6342 | 24737.2192 | 1693.5311 | 2846.0621
2026-07-05 23:00 | 21684.6354 | 25085.5688 | 1705.7306 | 2826.0283
2026-07-12 23:00 | 22386.396 | 26019.4691 | 1777.0801 | 2941.3395
2026-07-19 23:00 | 22525.8787 | 25786.4908 | 1718.1777 | 2977.0453
2026-07-26 23:00 | 22545.4491 | 25650.1042 | 1705.3875 | 2983.3263
2026-08-02 23:00 | 22294.4112 | 25174.7698 | 1632.1208 | 2954.6387
2026-08-09 23:00 | 21765.1918 | 25039.0767 | 1794.5334 | 2891.8602
2026-08-16 23:00 | 21817.1338 | 24558.2022 | 1615.1329 | 2887.9625
2026-08-23 23:00 | 21657.3607 | 24552.5909 | 1386.6259 | 2876.045
2026-08-30 23:00 | 21527.5692 | 24207.598 | 1407.9515 | 2844.3556
2026-09-06 23:00 | 21099.167 | 24282.3066 | 1785.5627 | 2769.3849
2026-09-13 23:00 | 19902.443 | 23652.9423 | 1993.4029 | 2633.2876
2026-09-20 23:00 | 19408.7179 | 23178.8715 | 1731.1358 | 2632.6607
2026-09-27 23:00 | 18840.3029 | 22354.2635 | 1632.3076 | 2595.2314
2026-10-04 23:00 | 18734.8195 | 21665.2953 | 1198.1318 | 2570.4137
2026-10-11 23:00 | 18022.9822 | 20543.507 | 886.7211 | 2555.7517
2026-10-18 23:00 | 17959.0073 | 19800.1636 | 605.5533 | 2539.208
2026-10-25 23:00 | 18280.0482 | 19128.1776 | 456.6077 | 2610.1355
2026-11-01 23:00 | 18587.1559 | 19383.7307 | 447.4104 | 2659.2531
2026-11-08 23:00 | 19120.1294 | 20000.1514 | 484.6058 | 2708.6923
2026-11-15 23:00 | 19620.1336 | 20856.8759 | 629.3315 | 2767.9393
2026-11-22 23:00 | 20177.022 | 21396.3519 | 638.3026 | 2844.2677
2026-11-29 23:00 | 20753.0162 | 21706.4784 | 544.2964 | 2919.5254
2026-12-06 23:00 | 21046.636 | 21977.4419 | 552.6325 | 2986.883
2026-12-13 23:00 | 21391.7763 | 22692.9005 | 678.8644 | 3034.3248
2026-12-20 23:00 | 21607.0608 | 22861.6954 | 700.1513 | 3051.7518
2026-12-27 23:00 | 21046.3726 | 22319.4008 | 725.0361 | 2939.7152
2027-01-03 23:00 | 21261.5709 | 22717.8274 | 743.9914 | 2948.129
2027-01-10 23:00 | 22005.8128 | 23547.1257 | 826.8994 | 3118.7744
2027-01-17 23:00 | 21898.5406 | 23487.0234 | 841.1993 | 3139.2198
2027-01-24 23:00 | 21975.3876 | 23588.5481 | 871.9559 | 3166.0034
2027-01-31 23:00 | 21958.0053 | 23339.5586 | 831.9633 | 3162.8334
2027-02-07 23:00 | 21394.9166 | 22819.3779 | 754.919 | 3091.3777
2027-02-14 23:00 | 21350.7443 | 22858.9909 | 749.6377 | 3079.881
2027-02-21 23:00 | 21027.369 | 22657.7006 | 759.2493 | 3026.5323
2027-02-28 23:00 | 20972.6738 | 22365.8094 | 659.4801 | 3022.836
2027-03-07 23:00 | 20446.4418 | 21622.7458 | 676.4215 | 2949.9172
2027-03-14 23:00 | 19988.9608 | 21261.5797 | 693.9156 | 2891.3969
2027-03-21 23:00 | 19491.6865 | 20693.8819 | 635.2704 | 2826.902
2027-03-28 23:00 | 19050.3355 | 20029.5991 | 552.0023 | 2733.528
2027-04-04 23:00 | 18552.902 | 19619.8031 | 534.9822 | 2694.7184
2027-04-11 23:00 | 18274.2759 | 19250.1059 | 544.8649 | 2647.3029
2027-04-18 23:00 | 17957.942 | 19180.9006 | 692.1192 | 2587.6516
2027-04-25 23:00 | 17667.0794 | 18740.9148 | 626.497 | 2555.7354
2027-05-02 23:00 | 17448.7869 | 18671.1055 | 606.5185 | 2532.1417
2027-05-09 23:00 | 17473.5649 | 19109.8896 | 738.0459 | 2524.8668
2027-05-16 23:00 | 17512.6013 | 20216.571 | 987.0282 | 2515.4173
2027-05-23 23:00 | 18191.303 | 21339.7329 | 1335.0437 | 2526.8658
2027-05-30 23:00 | 18359.3935 | 22138.0892 | 2055.3156 | 2511.4776
2027-06-06 23:00 | 19285.8971 | 23318.434 | 2231.6497 | 2640.8584
2027-06-13 23:00 | 19818.7042 | 23766.3795 | 2169.1184 | 2686.0802
2027-06-20 23:00 | 20870.0994 | 24787.7358 | 2097.8104 | 2783.559
2027-06-27 23:00 | 21845.8981 | 24929.6212 | 1705.9127 | 2870.6578
2027-07-04 23:00 | 21770.6012 | 25047.969 | 1678.5404 | 2858.8821
2027-07-11 23:00 | 22577.0996 | 26245.5288 | 1778.0893 | 2963.939
2027-07-18 23:00 | 22725.9924 | 26043.5072 | 1763.6312 | 3013.3144
2027-07-25 23:00 | 22786.2189 | 25891.8935 | 1711.2693 | 3023.0089
2027-08-01 23:00 | 22529.5211 | 25386.1554 | 1667.4227 | 2995.3036
2027-08-08 23:00 | 22036.9079 | 25290.2506 | 1785.4362 | 2936.4534
2027-08-15 23:00 | 22078.0162 | 24794.3607 | 1647.3463 | 2926.8227
2027-08-22 23:00 | 21892.5808 | 24785.8579 | 1398.9137 | 2912.0589
2027-08-29 23:00 | 21770.1028 | 24413.83 | 1373.5444 | 2885.4274
2027-09-05 23:00 | 21439.7449 | 24534.4337 | 1731.1469 | 2824.3473
2027-09-12 23:00 | 20266.2712 | 23898.5067 | 1976.5865 | 2683.1786
2027-09-19 23:00 | 19739.2888 | 23638.7494 | 1766.7307 | 2677.5985
2027-09-26 23:00 | 19139.8399 | 22619.7392 | 1666.0759 | 2635.0342
2027-10-03 23:00 | 18821.1881 | 22410.6283 | 1376.7894 | 2617.7502
Back to main menu

## Table 1.4 Planned
Back to main menu
Table 1.4 Planned: Weekly Energy and Peak Demand Forecast
Week | Planned Normal Peak | Planned Extreme Peak | Load Forecast Uncertainty | Planned Normal Energy Demand
Week Ending | (MW) | (MW) | (MW) | (GWh)
2026-04-05 23:00 | 18385.2427 | 19490.3749 | 565.5318 | 2626.3874
2026-04-12 23:00 | 17954.2822 | 18983.3823 | 579.7828 | 2597.1875
2026-04-19 23:00 | 17704.468 | 18906.9571 | 684.7229 | 2547.9893
2026-04-26 23:00 | 17441.4166 | 18506.4362 | 611.0689 | 2518.6673
2026-05-03 23:00 | 17226.0863 | 18554.3779 | 630.6048 | 2500.7128
2026-05-10 23:00 | 17257.3907 | 19256.5915 | 757.3017 | 2488.6869
2026-05-17 23:00 | 17348.719 | 20250.5755 | 1057.6708 | 2483.0751
2026-05-24 23:00 | 17954.7439 | 21206.4812 | 1424.1393 | 2453.4387
2026-05-31 23:00 | 18428.3786 | 22196.4803 | 2122.2379 | 2527.3934
2026-06-07 23:00 | 19256.1805 | 23347.3139 | 2227.6961 | 2621.8683
2026-06-14 23:00 | 19719.7262 | 23597.9343 | 2187.2199 | 2659.3587
2026-06-21 23:00 | 20836.2237 | 24602.2291 | 2002.8552 | 2762.1115
2026-06-28 23:00 | 21710.5863 | 24737.2192 | 1693.3771 | 2846.0621
2026-07-05 23:00 | 21683.8255 | 25085.5688 | 1705.7683 | 2826.0283
2026-07-12 23:00 | 22386.4998 | 26019.4691 | 1776.3979 | 2941.3395
2026-07-19 23:00 | 22526.3585 | 25786.4908 | 1716.9988 | 2977.0453
2026-07-26 23:00 | 22544.9759 | 25650.1042 | 1705.8787 | 2983.3263
2026-08-02 23:00 | 22294.6422 | 25174.7698 | 1631.6787 | 2954.6387
2026-08-09 23:00 | 21764.8503 | 25039.0767 | 1794.5396 | 2891.8602
2026-08-16 23:00 | 21817.6686 | 24558.2022 | 1614.4493 | 2887.9625
2026-08-23 23:00 | 21657.8766 | 24552.5909 | 1386.0845 | 2876.045
2026-08-30 23:00 | 21527.7175 | 24207.598 | 1407.7311 | 2844.3556
2026-09-06 23:00 | 21098.6963 | 24282.3066 | 1785.7035 | 2769.3849
2026-09-13 23:00 | 19902.0485 | 23652.9423 | 1994.6572 | 2633.2876
2026-09-20 23:00 | 19408.9959 | 23178.8715 | 1728.7287 | 2632.6607
2026-09-27 23:00 | 18840.229 | 22354.2635 | 1631.4449 | 2595.2314
2026-10-04 23:00 | 18735.3906 | 21665.2953 | 1197.6541 | 2570.4137
2026-10-11 23:00 | 18023.0937 | 20543.507 | 886.6486 | 2555.7517
2026-10-18 23:00 | 17958.7462 | 19800.1636 | 605.7631 | 2539.208
2026-10-25 23:00 | 18280.0087 | 19128.1776 | 456.385 | 2610.1355
2026-11-01 23:00 | 18586.9456 | 19383.7307 | 447.7858 | 2659.2531
2026-11-08 23:00 | 19120.3716 | 20000.1514 | 484.4094 | 2708.6923
2026-11-15 23:00 | 19620.2749 | 20856.8759 | 629.23 | 2767.9393
2026-11-22 23:00 | 20177.2657 | 21396.3519 | 637.7032 | 2844.2677
2026-11-29 23:00 | 20753.1402 | 21706.4784 | 544.2409 | 2919.5254
2026-12-06 23:00 | 21046.6704 | 21977.4419 | 552.3492 | 2986.883
2026-12-13 23:00 | 21391.6631 | 22692.9005 | 678.9496 | 3034.3248
2026-12-20 23:00 | 21607.072 | 22861.6954 | 700.0377 | 3051.7518
2026-12-27 23:00 | 21046.4459 | 22319.4008 | 725.1088 | 2939.7152
2027-01-03 23:00 | 21272.3594 | 22718.1566 | 745.2127 | 2949.9702
2027-01-10 23:00 | 22031.9874 | 23573.5729 | 826.9467 | 3123.1735
2027-01-17 23:00 | 21924.8274 | 23513.7697 | 840.9227 | 3143.6188
2027-01-24 23:00 | 22001.8516 | 23615.1952 | 872.0555 | 3170.4024
2027-01-31 23:00 | 21984.429 | 23366.1731 | 831.5717 | 3167.2325
2027-02-07 23:00 | 21430.2661 | 22854.3683 | 755.1531 | 3097.2089
2027-02-14 23:00 | 21385.5472 | 22894.5314 | 750.2706 | 3085.7123
2027-02-21 23:00 | 21062.7473 | 22693.1288 | 759.7449 | 3032.3635
2027-02-28 23:00 | 21007.7564 | 22401.2288 | 659.3427 | 3028.6673
2027-03-07 23:00 | 20485.0561 | 21661.0955 | 676.4356 | 2956.2233
2027-03-14 23:00 | 20027.3569 | 21300.0083 | 693.5968 | 2897.703
2027-03-21 23:00 | 19530.2707 | 20732.3103 | 634.6554 | 2833.2081
2027-03-28 23:00 | 19088.6518 | 20067.9874 | 552.1422 | 2739.8341
2027-04-04 23:00 | 18593.2859 | 19658.5194 | 534.3369 | 2701.8683
2027-04-11 23:00 | 18321.9755 | 19297.7861 | 545.1945 | 2655.1332
2027-04-18 23:00 | 18005.6142 | 19228.5807 | 692.1307 | 2595.4818
2027-04-25 23:00 | 17714.8703 | 18788.595 | 626.5332 | 2563.5657
2027-05-02 23:00 | 17496.3252 | 18718.3868 | 606.6183 | 2540.3205
2027-05-09 23:00 | 17528.5197 | 19164.6308 | 738.3346 | 2533.9963
2027-05-16 23:00 | 17567.8857 | 20272.0329 | 986.9986 | 2524.5468
2027-05-23 23:00 | 18246.3565 | 21394.8185 | 1333.7615 | 2535.9953
2027-05-30 23:00 | 18414.4737 | 22192.9648 | 2054.7285 | 2520.6071
2027-06-06 23:00 | 19349.1447 | 23385.8285 | 2232.6992 | 2651.8076
2027-06-13 23:00 | 19885.1757 | 23834.4025 | 2168.5913 | 2697.3417
2027-06-20 23:00 | 20938.6467 | 24856.0457 | 2096.2554 | 2794.8205
2027-06-27 23:00 | 21912.3195 | 24997.311 | 1705.9135 | 2881.9192
2027-07-04 23:00 | 21842.4133 | 25126.3329 | 1678.353 | 2871.2444
2027-07-11 23:00 | 22655.0845 | 26323.2686 | 1778.406 | 2977.0489
2027-07-18 23:00 | 22803.6685 | 26120.8674 | 1763.2613 | 3026.4243
2027-07-25 23:00 | 22863.5045 | 25970.0566 | 1711.5669 | 3036.1188
2027-08-01 23:00 | 22607.6168 | 25463.5257 | 1665.9966 | 3008.5924
2027-08-08 23:00 | 22125.624 | 25378.7784 | 1784.8107 | 2951.0888
2027-08-15 23:00 | 22166.6873 | 24883.5843 | 1648.1333 | 2941.458
2027-08-22 23:00 | 21980.155 | 24873.8854 | 1399.5105 | 2926.6943
2027-08-29 23:00 | 21858.3872 | 24501.8575 | 1373.6996 | 2900.0628
2027-09-05 23:00 | 21536.3988 | 24637.564 | 1730.0362 | 2840.7354
2027-09-12 23:00 | 20369.1308 | 24002.3322 | 1975.2118 | 2700.2476
2027-09-19 23:00 | 19842.2045 | 23741.6568 | 1766.2413 | 2694.6675
2027-09-26 23:00 | 19242.3134 | 22723.4825 | 1666.484 | 2652.1033
2027-10-03 23:00 | 18925.8738 | 22513.5313 | 1375.5564 | 2635.6287
Back to main menu

## Table 1.4.1
Back to main menu
Table 1.4.1: Weekly Weather and Demand History
Week Number | Week Ending | Actual Energy (GWh) | Weekly Average Temperature (°C) | Peak Day | Actual Peak (MW) | Peak Day Temperature (°C)
19 | 2003-05-11 | 2675.239 | 13.4714 | 2003-05-05 | 18741 | 13.1
20 | 2003-05-18 | 2632.509 | 11.8333 | 2003-05-12 | 18362 | 11.1
21 | 2003-05-25 | 2571.07 | 13.4762 | 2003-05-20 | 18599 | 15.7
22 | 2003-06-01 | 2649.124 | 15.0952 | 2003-05-29 | 18226 | 24.2
23 | 2003-06-08 | 2665.141 | 16.219 | 2003-06-04 | 18410 | 16.1
24 | 2003-06-15 | 2678.946 | 18.0381 | 2003-06-11 | 19042 | 24.6
25 | 2003-06-22 | 2742.722 | 19.4 | 2003-06-18 | 19935 | 22.6
26 | 2003-06-29 | 3084.92 | 25.8857 | 2003-06-26 | 24753 | 33.3
27 | 2003-07-06 | 2992.491 | 25.419 | 2003-07-04 | 23199 | 31.3
28 | 2003-07-13 | 2852.473 | 21.5524 | 2003-07-08 | 22167 | 28.6
29 | 2003-07-20 | 2847.944 | 21.2667 | 2003-07-14 | 21133 | 28
30 | 2003-07-27 | 2885.618 | 22.5905 | 2003-07-25 | 20868 | 28.7
31 | 2003-08-03 | 2897.737 | 22.3905 | 2003-07-30 | 21414 | 28.3
32 | 2003-08-10 | 3017.672 | 23.3 | 2003-08-07 | 22326 | 26.9
33 | 2003-08-17 | 2723.58 | 22.1 | 2003-08-14 | 23932 | 31
34 | 2003-08-24 | 2750.549 | 23.4048 | 2003-08-21 | 20709 | 31.7
35 | 2003-08-31 | 2853.562 | 21.7952 | 2003-08-26 | 21951 | 30
36 | 2003-09-07 | 2703.488 | 20.1095 | 2003-09-03 | 19841 | 23.2
37 | 2003-09-14 | 2870.007 | 20.7381 | 2003-09-11 | 20699 | 26.8
38 | 2003-09-21 | 2785.104 | 17.9857 | 2003-09-15 | 20233 | 19.6
39 | 2003-09-28 | 2698.174 | 15.6048 | 2003-09-22 | 19269 | 18.4
40 | 2003-10-05 | 2734.489 | 8.3905 | 2003-10-02 | 18929 | 9.4
41 | 2003-10-12 | 2696.531 | 15.3286 | 2003-10-09 | 18922 | 23.6
42 | 2003-10-19 | 2672.208 | 9.2952 | 2003-10-14 | 19092 | 16.2
43 | 2003-10-26 | 2799.532 | 7.4905 | 2003-10-23 | 19738 | 5.4
44 | 2003-11-02 | 2803.196 | 9.2762 | 2003-10-28 | 20426 | 9.7
45 | 2003-11-09 | 2900.177 | 4.019 | 2003-11-04 | 20899 | 4.7
46 | 2003-11-16 | 2927.031 | 4.5857 | 2003-11-13 | 21169 | 2
47 | 2003-11-23 | 2875.998 | 8.0048 | 2003-11-17 | 20954 | 5.3
48 | 2003-11-30 | 2975.154 | 4.1333 | 2003-11-24 | 21504 | 13.4
49 | 2003-12-07 | 2646.415 | -2.919 | 2003-12-02 | 22026 | -5.6
50 | 2003-12-14 | 3161.767 | -0.07619 | 2003-12-08 | 22584 | 1.4
51 | 2003-12-21 | 3602.808 | -0.2619 | 2003-12-15 | 22524 | 1.1
52 | 2003-12-28 | 2643.779 | 3.3333 | 2003-12-22 | 20772 | 5.9
1 | 2004-01-04 | 2717.783 | 4.4048 | 2003-12-30 | 19967 | 3
2 | 2004-01-11 | 3371.766 | -10.2286 | 2004-01-09 | 23998 | -18.3
3 | 2004-01-18 | 3441.886 | -10.7095 | 2004-01-15 | 24877 | -19.7
4 | 2004-01-25 | 3452.82 | -12.0905 | 2004-01-19 | 23728 | -8.7
5 | 2004-02-01 | 3428.432 | -8.3667 | 2004-01-26 | 24659 | -12.8
6 | 2004-02-08 | 3246.898 | -3.9905 | 2004-02-04 | 22494 | -3.9
7 | 2004-02-15 | 3235.171 | -4.1857 | 2004-02-09 | 22239 | 2.1
8 | 2004-02-22 | 3167.121 | -1.7619 | 2004-02-16 | 22792 | -5.7
9 | 2004-02-29 | 3050.511 | 0.28571 | 2004-02-23 | 21479 | -1.2
10 | 2004-03-07 | 2977.639 | 5.0048 | 2004-03-03 | 20620 | 5.8
11 | 2004-03-14 | 3038.073 | -0.10476 | 2004-03-08 | 21125 | 0.2
12 | 2004-03-21 | 3064.243 | -1.1333 | 2004-03-16 | 21476 | -3.1
13 | 2004-03-28 | 2933.927 | 5.9476 | 2004-03-22 | 21429 | -2.8
14 | 2004-04-04 | 2856.708 | 5.4857 | 2004-04-01 | 19881 | 5.2
15 | 2004-04-11 | 2757.816 | 4.5952 | 2004-04-05 | 19965 | 3.2
16 | 2004-04-18 | 2750.228 | 8.3476 | 2004-04-13 | 19339 | 4.2
17 | 2004-04-25 | 2704.802 | 10.5048 | 2004-04-21 | 18430 | 20
18 | 2004-05-02 | 2727.854 | 11.5095 | 2004-04-27 | 18771 | 5.8
19 | 2004-05-09 | 2708.043 | 9.719 | 2004-05-03 | 18664 | 8.3
20 | 2004-05-16 | 2745.619 | 18.7143 | 2004-05-13 | 20218 | 27.3
21 | 2004-05-23 | 2670.063 | 15.8571 | 2004-05-20 | 18943 | 23.6
22 | 2004-05-30 | 2605.734 | 14.3905 | 2004-05-25 | 18349 | 13.6
23 | 2004-06-06 | 2660.545 | 15.7048 | 2004-05-31 | 18508 | 13.2
24 | 2004-06-13 | 2887.122 | 20.4048 | 2004-06-09 | 23153 | 31.3
25 | 2004-06-20 | 2888.011 | 19.9476 | 2004-06-14 | 21752 | 27.3
26 | 2004-06-27 | 2761.454 | 18.481 | 2004-06-24 | 20108 | 25.8
27 | 2004-07-04 | 2745.2 | 20.8762 | 2004-06-30 | 19465 | 23.9
28 | 2004-07-11 | 2789.817 | 20.5143 | 2004-07-05 | 19911 | 20.8
29 | 2004-07-18 | 2908.264 | 22.6857 | 2004-07-12 | 22092 | 27.4
30 | 2004-07-25 | 2975.51 | 21.9143 | 2004-07-22 | 23831 | 30.1
31 | 2004-08-01 | 2924.264 | 21.5 | 2004-07-29 | 21709 | 26.7
32 | 2004-08-08 | 2841.852 | 20.7905 | 2004-08-03 | 23071 | 28.6
33 | 2004-08-15 | 2822.098 | 19.7857 | 2004-08-10 | 21120 | 26.5
34 | 2004-08-22 | 2802.037 | 19.7381 | 2004-08-18 | 20534 | 25.5
35 | 2004-08-29 | 3020.753 | 22.519 | 2004-08-27 | 22554 | 27.6
36 | 2004-09-05 | 2940.62 | 21.4238 | 2004-09-03 | 21395 | 28.4
37 | 2004-09-12 | 2839.863 | 20.6571 | 2004-09-07 | 21019 | 24.6
38 | 2004-09-19 | 2865.462 | 18.3095 | 2004-09-15 | 21740 | 25.8
39 | 2004-09-26 | 2885.929 | 20.4905 | 2004-09-23 | 21431 | 27.5
40 | 2004-10-03 | 2771.707 | 16.1 | 2004-09-27 | 19918 | 23.6
41 | 2004-10-10 | 2739.189 | 15.4238 | 2004-10-07 | 19509 | 26.8
42 | 2004-10-17 | 2707.201 | 10.481 | 2004-10-14 | 19253 | 13.4
43 | 2004-10-24 | 2819.211 | 8.4 | 2004-10-18 | 19704 | 8.8
44 | 2004-10-31 | 2793.89 | 11.381 | 2004-10-27 | 19492 | 11.4
45 | 2004-11-07 | 2855.622 | 7.7952 | 2004-11-04 | 20642 | 6.2
46 | 2004-11-14 | 2961.444 | 3.3857 | 2004-11-09 | 21076 | 1.4
47 | 2004-11-21 | 2880.44 | 8.8286 | 2004-11-15 | 20707 | 13.4
48 | 2004-11-28 | 3001.181 | 4.2905 | 2004-11-24 | 21769 | 3.4
49 | 2004-12-05 | 3085.202 | 2.0143 | 2004-12-03 | 22046 | -0.6
50 | 2004-12-12 | 3622.393 | 2.1286 | 2004-12-06 | 23352 | -1.7
51 | 2004-12-18 | 2800.887 | -3.7286 | 2004-12-14 | 23436 | -4.9
52 | 2004-12-26 | 3162.779 | -7.8762 | 2004-12-20 | 24809 | -12.3
53 | 2005-01-02 | 2907.357 | -0.25714 | 2004-12-27 | 21226 | -8.5
1 | 2005-01-09 | 3184.351 | -1.2714 | 2005-01-06 | 23183 | -2.7
2 | 2005-01-16 | 3215.38 | -1.7 | 2005-01-11 | 22615 | -1.6
3 | 2005-01-23 | 3527.552 | -13.9905 | 2005-01-18 | 24307 | -14.5
4 | 2005-01-30 | 3421.373 | -9.7857 | 2005-01-27 | 24291 | -14.6
5 | 2005-02-06 | 3165.178 | -1.5905 | 2005-01-31 | 22574 | -1.5
6 | 2005-02-13 | 3141.846 | -1.8048 | 2005-02-09 | 22244 | -3.9
7 | 2005-02-20 | 3212.867 | -2.7238 | 2005-02-18 | 22232 | -9.3
8 | 2005-02-27 | 3229.884 | -5.4238 | 2005-02-24 | 22328 | -5.7
9 | 2005-03-06 | 3169.752 | -3.019 | 2005-02-28 | 22106 | 1.8
10 | 2005-03-13 | 3205.601 | -4.2143 | 2005-03-08 | 22684 | -8.5
11 | 2005-03-20 | 3043.77 | -0.7619 | 2005-03-14 | 20989 | -0.8
12 | 2005-03-27 | 2884.713 | 2.181 | 2005-03-23 | 20899 | 1.5
13 | 2005-04-03 | 2873.583 | 6.4333 | 2005-03-28 | 19566 | 6.6
14 | 2005-04-10 | 2777.064 | 9.6524 | 2005-04-04 | 19276 | 10.9
15 | 2005-04-17 | 2705.24 | 9.9 | 2005-04-11 | 18600 | 7.9
16 | 2005-04-24 | 2733.207 | 10.4952 | 2005-04-20 | 18469 | 16.2
17 | 2005-05-01 | 2760.182 | 7.9714 | 2005-04-25 | 19320 | 6.5
18 | 2005-05-08 | 2661.14 | 10.4952 | 2005-05-02 | 18469 | 8.6
19 | 2005-05-15 | 2664.748 | 12.5952 | 2005-05-11 | 18520 | 22.6
20 | 2005-05-22 | 2633.858 | 12.9 | 2005-05-16 | 18288 | 11
21 | 2005-05-29 | 2614.715 | 16.5381 | 2005-05-26 | 18610 | 24.2
22 | 2005-06-05 | 2822.357 | 20.0714 | 2005-06-02 | 19972 | 26
23 | 2005-06-12 | 3339.343 | 26.3952 | 2005-06-10 | 24469 | 30.5
24 | 2005-06-19 | 2967.375 | 20.219 | 2005-06-14 | 24901 | 29.7
25 | 2005-06-26 | 3086.688 | 23.9857 | 2005-06-24 | 23657 | 34
26 | 2005-07-03 | 3201.62 | 25.3905 | 2005-06-27 | 25922 | 31.6
27 | 2005-07-10 | 3047.491 | 24.081 | 2005-07-04 | 23149 | 29.5
28 | 2005-07-17 | 3478.761 | 28.4 | 2005-07-13 | 25872 | 34.6
29 | 2005-07-24 | 3345.132 | 26.5381 | 2005-07-18 | 25545 | 33.3
30 | 2005-07-31 | 3059.465 | 23.3286 | 2005-07-25 | 25053 | 33.8
31 | 2005-08-07 | 3304.047 | 26.2429 | 2005-08-04 | 24979 | 32.8
32 | 2005-08-14 | 3294.582 | 25.0333 | 2005-08-09 | 25638 | 32.9
33 | 2005-08-21 | 3046.904 | 22.5143 | 2005-08-15 | 22081 | 27.6
34 | 2005-08-28 | 2960.83 | 21.0952 | 2005-08-26 | 21349 | 27.4
35 | 2005-09-04 | 3014.828 | 21.8524 | 2005-08-29 | 22761 | 28.4
36 | 2005-09-11 | 2896.404 | 20.4048 | 2005-09-07 | 22170 | 27.5
37 | 2005-09-18 | 3053.565 | 22.3429 | 2005-09-13 | 23689 | 30.1
38 | 2005-09-25 | 2907.237 | 20.0476 | 2005-09-21 | 20979 | 28.5
39 | 2005-10-02 | 2755.984 | 16.7381 | 2005-09-26 | 19927 | 22.3
40 | 2005-10-09 | 2805.329 | 16.7238 | 2005-10-04 | 20676 | 25.8
41 | 2005-10-16 | 2663.132 | 12.9905 | 2005-10-12 | 19064 | 13.2
42 | 2005-10-23 | 2759.787 | 8.8429 | 2005-10-20 | 19120 | 11.9
43 | 2005-10-30 | 2835.05 | 7.419 | 2005-10-26 | 19803 | 8.1
44 | 2005-11-06 | 2777.496 | 11.9 | 2005-11-02 | 19773 | 12.3
45 | 2005-11-13 | 2809.872 | 9.0571 | 2005-11-10 | 20392 | 5.7
46 | 2005-11-20 | 2905.28 | 4.1619 | 2005-11-17 | 21171 | 2.7
47 | 2005-11-27 | 3058.861 | -2.4381 | 2005-11-24 | 22566 | -6.3
48 | 2005-12-04 | 3000.238 | 2.119 | 2005-12-02 | 21616 | -0.8
49 | 2005-12-11 | 3199.968 | -3.7476 | 2005-12-07 | 22958 | -4.3
50 | 2005-12-17 | 2855.631 | -5.3 | 2005-12-12 | 23626 | -9.8
51 | 2005-12-25 | 3103.127 | -1.3286 | 2005-12-19 | 23257 | -4.7
52 | 2006-01-01 | 3208.112 | -1.0048 | 2005-12-29 | 20147 | 0.8
1 | 2006-01-08 | 3060.448 | -0.042857 | 2006-01-06 | 21905 | -5.2
2 | 2006-01-15 | 3046.688 | 1.5524 | 2006-01-09 | 21700 | 2.6
3 | 2006-01-22 | 3134.613 | 0.28571 | 2006-01-17 | 22861 | 0.7
4 | 2006-01-29 | 3075.232 | 0.77619 | 2006-01-26 | 22236 | -3.7
5 | 2006-02-05 | 3002.114 | 2.7476 | 2006-01-31 | 21295 | 1.3
6 | 2006-02-12 | 3166.709 | -5.3429 | 2006-02-08 | 22080 | -6.1
7 | 2006-02-19 | 3166.361 | -3.5857 | 2006-02-16 | 22079 | -0.9
8 | 2006-02-26 | 3126.432 | -2.5857 | 2006-02-20 | 21828 | -3.4
9 | 2006-03-05 | 3153.109 | -4.1429 | 2006-02-27 | 22114 | -4.1
10 | 2006-03-12 | 2943.659 | 4.2857 | 2006-03-06 | 20835 | 0.3
11 | 2006-03-19 | 2983.336 | 0.83333 | 2006-03-15 | 20716 | 2.6
12 | 2006-03-26 | 2968.069 | 0.92857 | 2006-03-20 | 21034 | -1.7
13 | 2006-04-02 | 2778.61 | 8.4048 | 2006-03-27 | 19548 | 11.5
14 | 2006-04-09 | 2829.331 | 5.1476 | 2006-04-04 | 19558 | 6.6
15 | 2006-04-16 | 2607.914 | 12.0143 | 2006-04-12 | 18530 | 16.9
16 | 2006-04-23 | 2642.006 | 11.7 | 2006-04-18 | 17818 | 15.5
17 | 2006-04-30 | 2668.331 | 9.481 | 2006-04-25 | 18633 | 7.2
18 | 2006-05-07 | 2607.266 | 14.1619 | 2006-05-04 | 18132 | 23
19 | 2006-05-14 | 2619.082 | 15.5762 | 2006-05-10 | 18225 | 23.4
20 | 2006-05-21 | 2603.746 | 12.0571 | 2006-05-16 | 17933 | 14.1
21 | 2006-05-28 | 2631.006 | 15.8857 | 2006-05-26 | 18581 | 18.8
22 | 2006-06-04 | 3030.444 | 22.6476 | 2006-05-30 | 24823 | 32.8
23 | 2006-06-11 | 2789.813 | 18.2381 | 2006-06-07 | 21130 | 27.1
24 | 2006-06-18 | 2952.481 | 22.1714 | 2006-06-17 | 21455 | 33.3
25 | 2006-06-25 | 3012.124 | 22.1429 | 2006-06-22 | 23082 | 30.6
26 | 2006-07-02 | 2974.16 | 23.3619 | 2006-06-28 | 22172 | 26.2
27 | 2006-07-09 | 2898.73 | 23.0667 | 2006-07-04 | 22330 | 28.9
28 | 2006-07-16 | 3145.2 | 24.8476 | 2006-07-14 | 23664 | 30
29 | 2006-07-23 | 3182.345 | 23.8095 | 2006-07-17 | 25658 | 33.8
30 | 2006-07-30 | 3285.355 | 25.7 | 2006-07-26 | 24177 | 30.5
31 | 2006-08-06 | 3356.688 | 26.619 | 2006-08-01 | 26768 | 36.4
32 | 2006-08-13 | 2889.38 | 21.7667 | 2006-08-09 | 21246 | 26.2
33 | 2006-08-20 | 2979.046 | 22.2429 | 2006-08-18 | 22702 | 30.4
34 | 2006-08-27 | 2879.36 | 20.9048 | 2006-08-22 | 21273 | 27.5
35 | 2006-09-03 | 2772.402 | 18.5286 | 2006-08-28 | 20529 | 23.6
36 | 2006-09-10 | 2694.952 | 18.6381 | 2006-09-08 | 19896 | 28
37 | 2006-09-17 | 2712.798 | 17.819 | 2006-09-13 | 18845 | 20.9
38 | 2006-09-24 | 2692.215 | 16.4619 | 2006-09-19 | 19775 | 18.1
39 | 2006-10-01 | 2653.947 | 13.1095 | 2006-09-27 | 18522 | 22.3
40 | 2006-10-08 | 2637.776 | 13.3524 | 2006-10-03 | 18796 | 23.3
41 | 2006-10-15 | 2621.631 | 9.7952 | 2006-10-12 | 18710 | 7.8
42 | 2006-10-22 | 2704.531 | 10.2095 | 2006-10-17 | 19000 | 12.2
43 | 2006-10-29 | 2780.566 | 5.0286 | 2006-10-25 | 19176 | 7.8
44 | 2006-11-05 | 2810.968 | 5.2762 | 2006-11-02 | 20205 | 4.4
45 | 2006-11-12 | 2770.862 | 7.5476 | 2006-11-07 | 20025 | 10.8
46 | 2006-11-19 | 2833.259 | 5.619 | 2006-11-13 | 20552 | 5.4
47 | 2006-11-26 | 2852.001 | 3.9476 | 2006-11-20 | 21129 | 1.5
48 | 2006-12-03 | 2903.458 | 6.3714 | 2006-12-01 | 20698 | 3.6
49 | 2006-12-10 | 3088.927 | -1.5333 | 2006-12-07 | 22656 | -5.5
50 | 2006-12-17 | 3355.996 | 6.6714 | 2006-12-11 | 21675 | 4.9
51 | 2006-12-23 | 2520.519 | 4.1619 | 2006-12-19 | 21351 | 4.4
52 | 2006-12-30 | 2682.677 | 0.95714 | 2006-12-29 | 19804 | -2.6
1 | 2007-01-07 | 2759.189 | 6.181 | 2007-01-03 | 20288 | 7.6
2 | 2007-01-14 | 3014.616 | 0.18095 | 2007-01-10 | 22026 | -3
3 | 2007-01-21 | 3180.515 | -5.5381 | 2007-01-16 | 22888 | -8.6
4 | 2007-01-28 | 3233.013 | -7.2095 | 2007-01-25 | 23328 | -13.1
5 | 2007-02-04 | 3255.384 | -8.5762 | 2007-01-29 | 22753 | -6.3
6 | 2007-02-11 | 3311.569 | -9.3238 | 2007-02-05 | 23640 | -10.5
7 | 2007-02-18 | 3308.032 | -10.5905 | 2007-02-13 | 23639 | -14
8 | 2007-02-25 | 3134.21 | -3.1619 | 2007-02-19 | 22345 | -5.3
9 | 2007-03-04 | 3045.905 | -1.4905 | 2007-03-01 | 21475 | -0.8
10 | 2007-03-11 | 3143.056 | -4.8762 | 2007-03-06 | 22772 | -12.5
11 | 2007-03-18 | 2924.953 | 2.9381 | 2007-03-16 | 20225 | -2.4
12 | 2007-03-25 | 2927.949 | 2.819 | 2007-03-20 | 20535 | -2.3
13 | 2007-04-01 | 2749.563 | 7.9619 | 2007-03-26 | 18807 | 19.2
14 | 2007-04-08 | 2814.703 | 0.95238 | 2007-04-05 | 19409 | -3
15 | 2007-04-15 | 2872.975 | 3.2143 | 2007-04-11 | 19680 | 4.1
16 | 2007-04-22 | 2680.61 | 11.6571 | 2007-04-16 | 19250 | 5.2
17 | 2007-04-29 | 2634.277 | 12.4524 | 2007-04-27 | 18211 | 16.8
18 | 2007-05-06 | 2572.418 | 11.681 | 2007-05-01 | 17888 | 9.7
19 | 2007-05-13 | 2603.987 | 16.381 | 2007-05-11 | 18478 | 20.5
20 | 2007-05-20 | 2605.33 | 14.1667 | 2007-05-15 | 19025 | 28.4
21 | 2007-05-27 | 2682.48 | 18.5143 | 2007-05-25 | 20875 | 27.4
22 | 2007-06-03 | 2917.633 | 21.7143 | 2007-05-31 | 21316 | 27.5
23 | 2007-06-10 | 2731.849 | 18.0048 | 2007-06-08 | 21794 | 31.2
24 | 2007-06-17 | 3052.251 | 24 | 2007-06-13 | 23299 | 29.7
25 | 2007-06-24 | 2875.267 | 21.2381 | 2007-06-18 | 22883 | 28.3
26 | 2007-07-01 | 3058.01 | 23.4048 | 2007-06-26 | 25628 | 34.2
27 | 2007-07-08 | 2763.077 | 22.1952 | 2007-07-06 | 20184 | 28.2
28 | 2007-07-15 | 2900.476 | 22.9286 | 2007-07-09 | 24173 | 33.7
29 | 2007-07-22 | 2832.297 | 22.1333 | 2007-07-18 | 21283 | 27.5
30 | 2007-07-29 | 3006.625 | 22.9667 | 2007-07-26 | 22020 | 27.5
31 | 2007-08-05 | 3270.026 | 26.6905 | 2007-08-02 | 25418 | 34.5
32 | 2007-08-12 | 3077.078 | 24.8095 | 2007-08-08 | 24012 | 31.7
33 | 2007-08-19 | 2869.053 | 21.7476 | 2007-08-16 | 22156 | 29.6
34 | 2007-08-26 | 2921.618 | 22.1381 | 2007-08-24 | 23409 | 32.8
35 | 2007-09-02 | 2932.442 | 22.4333 | 2007-08-29 | 24663 | 33.5
36 | 2007-09-09 | 2943.478 | 23.1 | 2007-09-07 | 23710 | 32.9
37 | 2007-09-16 | 2692.56 | 16.3429 | 2007-09-10 | 19512 | 23
38 | 2007-09-23 | 2761.954 | 19.4286 | 2007-09-21 | 20122 | 27.5
39 | 2007-09-30 | 2779.605 | 19.219 | 2007-09-25 | 22133 | 32.8
40 | 2007-10-07 | 2737.832 | 19.5238 | 2007-10-05 | 19206 | 24.3
41 | 2007-10-14 | 2644.804 | 14.4048 | 2007-10-09 | 18915 | 22.2
42 | 2007-10-21 | 2634.581 | 15.6286 | 2007-10-16 | 18570 | 12.8
43 | 2007-10-28 | 2652.985 | 11.981 | 2007-10-22 | 18634 | 24.8
44 | 2007-11-04 | 2684.867 | 9.0667 | 2007-11-01 | 18869 | 8.9
45 | 2007-11-11 | 2815.137 | 4.181 | 2007-11-07 | 20267 | 3.1
46 | 2007-11-18 | 2825.038 | 5.4 | 2007-11-12 | 20217 | 10.4
47 | 2007-11-25 | 2957.028 | 0.92857 | 2007-11-22 | 21494 | -3.4
48 | 2007-12-02 | 3497.435 | -0.97143 | 2007-11-28 | 21582 | -0.3
49 | 2007-12-09 | 3127.851 | -3.8143 | 2007-12-05 | 22385 | -7.9
50 | 2007-12-15 | 2735.781 | -2.8905 | 2007-12-11 | 22334 | 1.1
51 | 2007-12-23 | 2596.65 | 0.37143 | 2007-12-17 | 22585 | -3.4
52 | 2007-12-30 | 3120.152 | -0.18095 | 2007-12-27 | 19369 | 2.4
1 | 2008-01-06 | 2932.004 | -3.0143 | 2008-01-03 | 22307 | -7.7
2 | 2008-01-13 | 2878.326 | 5.8143 | 2008-01-10 | 20540 | 3.6
3 | 2008-01-20 | 3072.046 | -3.1762 | 2008-01-15 | 21303 | -0.8
4 | 2008-01-27 | 3182.096 | -5.7905 | 2008-01-21 | 22612 | -7.4
5 | 2008-02-03 | 3068.717 | -1.8905 | 2008-01-30 | 22270 | -8
6 | 2008-02-10 | 3024.216 | -1.8333 | 2008-02-06 | 21276 | -1.7
7 | 2008-02-17 | 3155.123 | -6.4333 | 2008-02-11 | 22834 | -9.3
8 | 2008-02-24 | 3046.81 | -4.7286 | 2008-02-20 | 21645 | -6.8
9 | 2008-03-02 | 3095.645 | -5.3 | 2008-02-27 | 21953 | -10.1
10 | 2008-03-09 | 2996.993 | -1.719 | 2008-03-04 | 20576 | -1.6
11 | 2008-03-16 | 2919.677 | -0.99524 | 2008-03-10 | 20185 | -0.7
12 | 2008-03-23 | 2852.89 | -0.5381 | 2008-03-18 | 19865 | 3
13 | 2008-03-30 | 2876.386 | 0.47143 | 2008-03-25 | 20067 | 2.6
14 | 2008-04-06 | 2775.843 | 5.519 | 2008-03-31 | 19196 | 5.3
15 | 2008-04-13 | 2704.624 | 8.2429 | 2008-04-11 | 19187 | 5.2
16 | 2008-04-20 | 2603.618 | 13.819 | 2008-04-14 | 18166 | 9.7
17 | 2008-04-27 | 2562.259 | 16.2286 | 2008-04-22 | 17791 | 20.9
18 | 2008-05-04 | 2615.088 | 8.1095 | 2008-04-28 | 18242 | 6.9
19 | 2008-05-11 | 2533.921 | 12.3333 | 2008-05-07 | 17750 | 15.6
20 | 2008-05-18 | 2538.939 | 13.2619 | 2008-05-14 | 17662 | 17
21 | 2008-05-25 | 2519.535 | 12.1619 | 2008-05-21 | 17701 | 9.4
22 | 2008-06-01 | 2585.264 | 16.3 | 2008-05-26 | 18453 | 26.9
23 | 2008-06-08 | 2844.201 | 22.0524 | 2008-06-06 | 21341 | 32.7
24 | 2008-06-15 | 2954.631 | 22.3952 | 2008-06-09 | 24001 | 33.1
25 | 2008-06-22 | 2684.657 | 17.0095 | 2008-06-16 | 19710 | 22.9
26 | 2008-06-29 | 2916.525 | 22.3238 | 2008-06-27 | 22302 | 27
27 | 2008-07-06 | 2712.781 | 20.6429 | 2008-07-02 | 20429 | 27.8
28 | 2008-07-13 | 3034.078 | 23.9381 | 2008-07-08 | 23224 | 30.7
29 | 2008-07-20 | 3049.678 | 23.9714 | 2008-07-17 | 23622 | 30
30 | 2008-07-27 | 2886.07 | 22.2333 | 2008-07-21 | 21078 | 24.8
31 | 2008-08-03 | 2954.73 | 23.0905 | 2008-07-31 | 21710 | 26.4
32 | 2008-08-10 | 2790.248 | 19.9571 | 2008-08-05 | 22376 | 26.1
33 | 2008-08-17 | 2764.063 | 20.4524 | 2008-08-14 | 19560 | 23.4
34 | 2008-08-24 | 2917.179 | 21.581 | 2008-08-18 | 22296 | 29.4
35 | 2008-08-31 | 2751.703 | 19.8095 | 2008-08-25 | 19101 | 20.4
36 | 2008-09-07 | 2871.959 | 21.281 | 2008-09-03 | 22900 | 30.3
37 | 2008-09-14 | 2702.472 | 18.6619 | 2008-09-14 | 18875 | 28
38 | 2008-09-21 | 2650.985 | 16.3952 | 2008-09-17 | 18274 | 23
39 | 2008-09-28 | 2666.45 | 17.1333 | 2008-09-25 | 18980 | 23.5
40 | 2008-10-05 | 2586.319 | 11.6524 | 2008-10-02 | 18029 | 12.6
41 | 2008-10-12 | 2584.606 | 13.0429 | 2008-10-08 | 18514 | 14.6
42 | 2008-10-19 | 2523.674 | 11.7952 | 2008-10-15 | 18128 | 15.9
43 | 2008-10-26 | 2640.237 | 7.7905 | 2008-10-21 | 18772 | 5.9
44 | 2008-11-02 | 2677.429 | 5.8095 | 2008-10-29 | 19171 | 3.3
45 | 2008-11-09 | 2591.332 | 10.4714 | 2008-11-03 | 18815 | 15.6
46 | 2008-11-16 | 2677.321 | 5.9429 | 2008-11-11 | 19640 | 5.6
47 | 2008-11-23 | 2922.821 | -3.3476 | 2008-11-19 | 20906 | -1.6
48 | 2008-11-30 | 2866.8 | 1.8238 | 2008-11-24 | 20878 | 3.8
49 | 2008-12-07 | 3373.616 | -1.7048 | 2008-12-04 | 20833 | 0.9
50 | 2008-12-14 | 3069.714 | -2.4048 | 2008-12-08 | 22230 | -3.7
51 | 2008-12-21 | 2183.151 | -5.1 | 2008-12-19 | 21903 | -8.9
52 | 2008-12-28 | 3488.556 | -0.44286 | 2008-12-22 | 21582 | -7.7
1 | 2009-01-04 | 2364.119 | -4.2571 | 2009-01-04 | 19721 | -2.1
2 | 2009-01-11 | 3024.795 | -5.7524 | 2009-01-08 | 21006 | -4.5
3 | 2009-01-18 | 3221.451 | -10.2429 | 2009-01-15 | 22804 | -11.3
4 | 2009-01-25 | 3120.821 | -8.0571 | 2009-01-20 | 22018 | -10.4
5 | 2009-02-01 | 3076.809 | -6.6524 | 2009-01-26 | 22003 | -8.9
6 | 2009-02-08 | 2983.238 | -5.0857 | 2009-02-04 | 21876 | -13.1
7 | 2009-02-15 | 2829.295 | 0.82857 | 2009-02-09 | 19841 | 2.6
8 | 2009-02-22 | 2852.638 | -3.1286 | 2009-02-19 | 20313 | -5.2
9 | 2009-03-01 | 2918.702 | -4.0571 | 2009-02-23 | 20882 | -6.1
10 | 2009-03-08 | 2865.83 | -0.40952 | 2009-03-02 | 21266 | -9.6
11 | 2009-03-15 | 2771.815 | 0.61429 | 2009-03-12 | 19558 | -3.4
12 | 2009-03-22 | 2607.907 | 4.3143 | 2009-03-19 | 18039 | 3.2
13 | 2009-03-29 | 2607.578 | 5.3143 | 2009-03-23 | 18345 | 1.6
14 | 2009-04-05 | 2566.444 | 6.6429 | 2009-03-30 | 18071 | 4.9
15 | 2009-04-12 | 2522.072 | 3.2905 | 2009-04-07 | 18329 | -0.5
16 | 2009-04-19 | 2427.499 | 10.4667 | 2009-04-13 | 16813 | 5.8
17 | 2009-04-26 | 2441.504 | 10.3286 | 2009-04-20 | 17644 | 5.6
18 | 2009-05-03 | 2369.714 | 13.219 | 2009-04-28 | 16573 | 10.4
19 | 2009-05-10 | 2381.014 | 14.1143 | 2009-05-07 | 16491 | 18.6
20 | 2009-05-17 | 2347.918 | 13.0524 | 2009-05-11 | 16538 | 13.2
21 | 2009-05-24 | 2324.301 | 17.9429 | 2009-05-21 | 17123 | 28.6
22 | 2009-05-31 | 2342.86 | 14.281 | 2009-05-25 | 17618 | 18.3
23 | 2009-06-07 | 2373.702 | 14.9619 | 2009-06-01 | 16474 | 15.3
24 | 2009-06-14 | 2393.083 | 16.7762 | 2009-06-11 | 16801 | 19.8
25 | 2009-06-21 | 2471.227 | 18.6476 | 2009-06-16 | 17669 | 23.4
26 | 2009-06-28 | 2827.027 | 23.3 | 2009-06-24 | 22403 | 30.7
27 | 2009-07-05 | 2429.956 | 19.0667 | 2009-06-29 | 18263 | 22.6
28 | 2009-07-12 | 2535.934 | 20.3619 | 2009-07-10 | 18804 | 25.9
29 | 2009-07-19 | 2495.28 | 19.519 | 2009-07-16 | 19044 | 27
30 | 2009-07-26 | 2542.821 | 20.1619 | 2009-07-20 | 18226 | 23.8
31 | 2009-08-02 | 2628.104 | 22.6857 | 2009-07-28 | 19678 | 27.4
32 | 2009-08-09 | 2560.875 | 20.9905 | 2009-08-04 | 20188 | 26.4
33 | 2009-08-16 | 2991.132 | 24.2952 | 2009-08-10 | 22022 | 29.9
34 | 2009-08-23 | 2953.422 | 23.9762 | 2009-08-17 | 24005 | 31.2
35 | 2009-08-30 | 2573.979 | 18.8048 | 2009-08-25 | 19558 | 25.5
36 | 2009-09-06 | 2550 | 19.1238 | 2009-09-03 | 18676 | 23.7
37 | 2009-09-13 | 2569.99 | 20.0429 | 2009-09-08 | 19551 | 25.1
38 | 2009-09-20 | 2494.128 | 16.5238 | 2009-09-14 | 18364 | 25
39 | 2009-09-27 | 2551.282 | 18.4286 | 2009-09-23 | 19258 | 27.2
40 | 2009-10-04 | 2445.95 | 11.2571 | 2009-10-01 | 17454 | 11.4
41 | 2009-10-11 | 2468.75 | 10.6286 | 2009-10-07 | 17436 | 12.4
42 | 2009-10-18 | 2540.442 | 4.7 | 2009-10-15 | 18320 | 4.1
43 | 2009-10-25 | 2553.259 | 10.3524 | 2009-10-22 | 18089 | 15.7
44 | 2009-11-01 | 2549.81 | 10.719 | 2009-10-26 | 18029 | 11.7
45 | 2009-11-08 | 2588.982 | 6.7429 | 2009-11-04 | 18972 | 5.9
46 | 2009-11-15 | 2553.776 | 8.6048 | 2009-11-09 | 18511 | 18.6
47 | 2009-11-22 | 2605.388 | 6.7571 | 2009-11-19 | 19067 | 9.6
48 | 2009-11-29 | 2640.481 | 6.1714 | 2009-11-24 | 19159 | 7.6
49 | 2009-12-06 | 2733.895 | 2.6714 | 2009-11-30 | 19685 | 3.7
50 | 2009-12-13 | 3384.411 | -1.4952 | 2009-12-10 | 21496 | -2.7
51 | 2009-12-20 | 3363.008 | -3.1857 | 2009-12-16 | 21747 | -3.8
52 | 2009-12-27 | 1989.13 | -2.0048 | 2009-12-22 | 21296 | -5.7
53 | 2010-01-03 | 2796.407 | -6.0238 | 2010-01-03 | 20770 | -8.6
1 | 2010-01-10 | 3076.419 | -7.5952 | 2010-01-04 | 21982 | -7.3
2 | 2010-01-17 | 2937.308 | -1.3429 | 2010-01-11 | 21483 | -4.7
3 | 2010-01-24 | 2897.403 | -0.53333 | 2010-01-20 | 20700 | -2.5
4 | 2010-01-31 | 3024.325 | -5.6381 | 2010-01-28 | 21864 | -7
5 | 2010-02-07 | 3008.541 | -4.8048 | 2010-02-01 | 21246 | -3.6
6 | 2010-02-14 | 2984.921 | -4.1476 | 2010-02-09 | 21018 | -3.9
7 | 2010-02-21 | 2846.377 | -0.30476 | 2010-02-17 | 20254 | 0.4
8 | 2010-02-28 | 2886.967 | -1.319 | 2010-02-25 | 20690 | -5.8
9 | 2010-03-07 | 2737.389 | 1.7714 | 2010-03-01 | 19282 | 2
10 | 2010-03-14 | 2623.207 | 6.7714 | 2010-03-08 | 18194 | 13.6
11 | 2010-03-21 | 2530.337 | 9.1429 | 2010-03-15 | 17362 | 12.1
12 | 2010-03-28 | 2652.551 | 3.4762 | 2010-03-25 | 18335 | 8.6
13 | 2010-04-04 | 2403.602 | 12.3048 | 2010-03-29 | 17597 | 8.4
14 | 2010-04-11 | 2494.844 | 10.6048 | 2010-04-09 | 17422 | 3.6
15 | 2010-04-18 | 2465.674 | 10.8905 | 2010-04-12 | 16709 | 13.1
16 | 2010-04-25 | 2447.052 | 11.5762 | 2010-04-21 | 16662 | 17.4
17 | 2010-05-02 | 2436.561 | 14.5476 | 2010-04-27 | 16607 | 9.4
18 | 2010-05-09 | 2477.159 | 13.0619 | 2010-05-05 | 17328 | 26.9
19 | 2010-05-16 | 2452.8 | 10.8143 | 2010-05-13 | 17005 | 11.3
20 | 2010-05-23 | 2470.298 | 18.5524 | 2010-05-20 | 17924 | 28.3
21 | 2010-05-30 | 2863.471 | 24.0429 | 2010-05-26 | 22806 | 31.4
22 | 2010-06-06 | 2736.188 | 20.3905 | 2010-05-31 | 20859 | 27.6
23 | 2010-06-13 | 2517.432 | 17.1 | 2010-06-11 | 17458 | 22.7
24 | 2010-06-20 | 2668.044 | 21.9286 | 2010-06-18 | 19093 | 25
25 | 2010-06-27 | 2793.61 | 22.2571 | 2010-06-23 | 21498 | 28.3
26 | 2010-07-04 | 2545.158 | 21.0905 | 2010-06-28 | 21240 | 28.9
27 | 2010-07-11 | 3196.825 | 26.9619 | 2010-07-08 | 24507 | 33.3
28 | 2010-07-18 | 3102.44 | 25.1238 | 2010-07-15 | 23587 | 28.9
29 | 2010-07-25 | 3004.401 | 24.5714 | 2010-07-21 | 22164 | 30.1
30 | 2010-08-01 | 2842.254 | 22.3952 | 2010-07-27 | 22449 | 28.3
31 | 2010-08-08 | 2931.57 | 24.3286 | 2010-08-04 | 23582 | 31.5
32 | 2010-08-15 | 3119.634 | 25.1429 | 2010-08-10 | 23426 | 29.4
33 | 2010-08-22 | 2797.864 | 22.019 | 2010-08-16 | 20994 | 27
34 | 2010-08-29 | 2729.423 | 21.1619 | 2010-08-29 | 20028 | 30.1
35 | 2010-09-05 | 3027.002 | 23.8286 | 2010-08-31 | 24566 | 32.9
36 | 2010-09-12 | 2502.796 | 18.1857 | 2010-09-07 | 19337 | 29.6
37 | 2010-09-19 | 2489.772 | 15.7571 | 2010-09-13 | 17472 | 23.6
38 | 2010-09-26 | 2539.512 | 17.6952 | 2010-09-24 | 18721 | 30.5
39 | 2010-10-03 | 2473.737 | 13.3762 | 2010-09-27 | 17513 | 15.7
40 | 2010-10-10 | 2460.436 | 14.119 | 2010-10-04 | 17452 | 12
41 | 2010-10-17 | 2431.16 | 10.9381 | 2010-10-13 | 17484 | 14.8
42 | 2010-10-24 | 2522.859 | 9.1714 | 2010-10-21 | 17759 | 7.7
43 | 2010-10-31 | 2506.893 | 11.4571 | 2010-10-26 | 17556 | 20.5
44 | 2010-11-07 | 2607.736 | 4.3 | 2010-11-05 | 18079 | 3.2
45 | 2010-11-14 | 2579.985 | 6.2429 | 2010-11-08 | 18433 | 10
46 | 2010-11-21 | 2623.409 | 5.5333 | 2010-11-18 | 18798 | 6.2
47 | 2010-11-28 | 2720.021 | 4.019 | 2010-11-25 | 19835 | 4.2
48 | 2010-12-05 | 2793.795 | 1.2 | 2010-12-02 | 20038 | 0.8
49 | 2010-12-12 | 2920.398 | -2.4 | 2010-12-08 | 21364 | -3.6
50 | 2010-12-19 | 3433.803 | -6.3476 | 2010-12-13 | 22099 | -11.6
51 | 2010-12-26 | 2822.777 | -4.6714 | 2010-12-21 | 20800 | -3.7
52 | 2011-01-02 | 2228.135 | 0.57143 | 2010-12-28 | 19037 | -0.7
1 | 2011-01-09 | 2924.562 | -4.4905 | 2011-01-06 | 20762 | -3.2
2 | 2011-01-16 | 3035.07 | -7.1476 | 2011-01-12 | 21182 | -7.7
3 | 2011-01-23 | 3110.626 | -9.0762 | 2011-01-17 | 21671 | -7.1
4 | 2011-01-30 | 3041.869 | -4.9571 | 2011-01-24 | 22531 | -9
5 | 2011-02-06 | 3045.758 | -7.2619 | 2011-01-31 | 21756 | -10.7
6 | 2011-02-13 | 2994.743 | -6.8476 | 2011-02-08 | 21510 | -9.9
7 | 2011-02-20 | 2838.845 | -0.033333 | 2011-02-15 | 20475 | -4.9
8 | 2011-02-27 | 2903.379 | -3.9714 | 2011-02-22 | 20461 | -3.9
9 | 2011-03-06 | 2872.379 | -1.1667 | 2011-03-02 | 20490 | -4.3
10 | 2011-03-13 | 2819.458 | 0.45238 | 2011-03-07 | 19974 | -2.1
11 | 2011-03-20 | 2658.262 | 4.1524 | 2011-03-14 | 18508 | 2.7
12 | 2011-03-27 | 2775.701 | -1.9524 | 2011-03-23 | 19208 | -4.5
13 | 2011-04-03 | 2648.138 | 3.5 | 2011-03-28 | 18693 | 2.2
14 | 2011-04-10 | 2564.081 | 7.4286 | 2011-04-05 | 17726 | 5.2
15 | 2011-04-17 | 2519.186 | 7.8381 | 2011-04-13 | 16945 | 11.2
16 | 2011-04-24 | 2501.655 | 6.5 | 2011-04-18 | 17763 | 3.7
17 | 2011-05-01 | 2420.774 | 10.4619 | 2011-04-26 | 16703 | 11.6
18 | 2011-05-08 | 2412.314 | 11.2286 | 2011-05-03 | 17036 | 7
19 | 2011-05-15 | 2392.347 | 14.6667 | 2011-05-13 | 16340 | 25.8
20 | 2011-05-22 | 2423.044 | 15.981 | 2011-05-16 | 16671 | 10.2
21 | 2011-05-29 | 2375.854 | 16.781 | 2011-05-26 | 16587 | 20.2
22 | 2011-06-05 | 2563.83 | 20.5857 | 2011-05-31 | 20689 | 29.3
23 | 2011-06-12 | 2660.324 | 21.2 | 2011-06-08 | 22533 | 33.3
24 | 2011-06-19 | 2568.452 | 19.8048 | 2011-06-16 | 18715 | 24.7
25 | 2011-06-26 | 2647.068 | 20.9238 | 2011-06-21 | 19867 | 25.6
26 | 2011-07-03 | 2627.884 | 22.2429 | 2011-06-28 | 19718 | 26.3
27 | 2011-07-10 | 2869.302 | 24.2762 | 2011-07-06 | 21238 | 29.2
28 | 2011-07-17 | 3001.318 | 25.819 | 2011-07-12 | 22605 | 31.7
29 | 2011-07-24 | 3340.465 | 28.8381 | 2011-07-21 | 25285 | 37.5
30 | 2011-07-31 | 2944.723 | 25.1714 | 2011-07-29 | 21553 | 31.4
31 | 2011-08-07 | 2980.877 | 24.7476 | 2011-08-02 | 21933 | 31.3
32 | 2011-08-14 | 2786.159 | 22.2286 | 2011-08-08 | 21737 | 26.2
33 | 2011-08-21 | 2857.856 | 23.8857 | 2011-08-18 | 21317 | 29.9
34 | 2011-08-28 | 2679.356 | 21.9095 | 2011-08-24 | 19849 | 27.9
35 | 2011-09-04 | 2834.56 | 23.3381 | 2011-09-02 | 21374 | 28.3
36 | 2011-09-11 | 2513.313 | 18.5333 | 2011-09-09 | 18252 | 25.2
37 | 2011-09-18 | 2549.873 | 16.4429 | 2011-09-12 | 19983 | 28.5
38 | 2011-09-25 | 2534.472 | 18.0286 | 2011-09-21 | 17934 | 21.7
39 | 2011-10-02 | 2528.475 | 15.5333 | 2011-09-26 | 18464 | 24.1
40 | 2011-10-09 | 2468.478 | 15.981 | 2011-10-03 | 17372 | 14
41 | 2011-10-16 | 2452.727 | 15.4476 | 2011-10-11 | 17674 | 22.7
42 | 2011-10-23 | 2487.87 | 9.7476 | 2011-10-19 | 17644 | 11.7
43 | 2011-10-30 | 2552.612 | 6.6667 | 2011-10-27 | 18178 | 4.7
44 | 2011-11-06 | 2534.665 | 8.0762 | 2011-11-01 | 17812 | 12.7
45 | 2011-11-13 | 2539.151 | 9.9667 | 2011-11-11 | 18180 | 5.5
46 | 2011-11-20 | 2565.766 | 7.581 | 2011-11-17 | 18729 | 4.3
47 | 2011-11-27 | 2623.685 | 6.381 | 2011-11-22 | 19370 | 1.3
48 | 2011-12-04 | 2700.273 | 4.1476 | 2011-11-29 | 19553 | 5.6
49 | 2011-12-11 | 2791.724 | 0.80476 | 2011-12-07 | 19881 | 1.2
50 | 2011-12-18 | 2774.329 | 2.681 | 2011-12-12 | 19666 | 6.5
51 | 2011-12-25 | 3136.682 | 0.8619 | 2011-12-20 | 20144 | -1.3
52 | 2012-01-01 | 2196.658 | -0.25238 | 2011-12-29 | 19407 | -2.8
1 | 2012-01-08 | 2822.035 | -1.7476 | 2012-01-03 | 21615 | -14.3
2 | 2012-01-15 | 2860.282 | -1.8952 | 2012-01-15 | 20042 | -7.5
3 | 2012-01-22 | 2975.382 | -2.3333 | 2012-01-18 | 20836 | -4.5
4 | 2012-01-29 | 2851.318 | 0.95238 | 2012-01-25 | 20096 | -0.9
5 | 2012-02-05 | 2790.934 | 1.7286 | 2012-01-30 | 20173 | -1.4
6 | 2012-02-12 | 2836.756 | -1.7524 | 2012-02-07 | 19731 | -0.3
7 | 2012-02-19 | 2774.69 | 0.64286 | 2012-02-14 | 19527 | 1
8 | 2012-02-26 | 2751.527 | 0.98095 | 2012-02-21 | 19456 | 3
9 | 2012-03-04 | 2791.485 | 1.4048 | 2012-02-29 | 19773 | 1.3
10 | 2012-03-11 | 2740.816 | 3.3857 | 2012-03-05 | 20341 | -2.8
11 | 2012-03-18 | 2477.837 | 11.5429 | 2012-03-12 | 17582 | 11.8
12 | 2012-03-25 | 2440.227 | 16.0571 | 2012-03-22 | 17270 | 23.7
13 | 2012-04-01 | 2573.313 | 3.9857 | 2012-03-26 | 17978 | 2.6
14 | 2012-04-08 | 2430.949 | 7.7857 | 2012-04-03 | 17337 | 10.7
15 | 2012-04-15 | 2487.758 | 9.9 | 2012-04-10 | 17665 | 8
16 | 2012-04-22 | 2459.347 | 11.1857 | 2012-04-17 | 16991 | 10.4
17 | 2012-04-29 | 2503.789 | 6.6048 | 2012-04-23 | 17691 | 4.1
18 | 2012-05-06 | 2429.049 | 12.8714 | 2012-04-30 | 17429 | 9.4
19 | 2012-05-13 | 2391.626 | 15.7048 | 2012-05-07 | 16606 | 15.3
20 | 2012-05-20 | 2425.019 | 17.3905 | 2012-05-15 | 16943 | 23.7
21 | 2012-05-27 | 2612.829 | 22.3619 | 2012-05-25 | 19995 | 30.7
22 | 2012-06-03 | 2571.502 | 18.3714 | 2012-05-28 | 20922 | 28.6
23 | 2012-06-10 | 2556.36 | 19.8429 | 2012-06-10 | 19088 | 29
24 | 2012-06-17 | 2718.756 | 21.6 | 2012-06-11 | 21312 | 27.7
25 | 2012-06-24 | 3033.376 | 25.3905 | 2012-06-20 | 23783 | 34.2
26 | 2012-07-01 | 2828.257 | 24.1095 | 2012-06-29 | 21988 | 32.4
27 | 2012-07-08 | 3062.451 | 26.4571 | 2012-07-04 | 23801 | 35.9
28 | 2012-07-15 | 3032.484 | 25.3476 | 2012-07-13 | 22707 | 32.3
29 | 2012-07-22 | 3051.299 | 25.5857 | 2012-07-17 | 24470 | 36.2
30 | 2012-07-29 | 2979.547 | 24.8476 | 2012-07-23 | 23530 | 34.1
31 | 2012-08-05 | 3109.533 | 25.8952 | 2012-08-03 | 23013 | 30.1
32 | 2012-08-12 | 2765.755 | 22.2143 | 2012-08-08 | 22190 | 28.2
33 | 2012-08-19 | 2704.955 | 21.1524 | 2012-08-16 | 20235 | 26.8
34 | 2012-08-26 | 2825.816 | 23.1095 | 2012-08-24 | 21121 | 28.7
35 | 2012-09-02 | 2825.634 | 23.1286 | 2012-08-31 | 21766 | 32.6
36 | 2012-09-09 | 2779.356 | 21.1286 | 2012-09-06 | 21168 | 27.1
37 | 2012-09-16 | 2571.289 | 18.7333 | 2012-09-13 | 19869 | 28.7
38 | 2012-09-23 | 2464.238 | 14.9238 | 2012-09-17 | 17723 | 23.2
39 | 2012-09-30 | 2445.948 | 13.9 | 2012-09-25 | 17165 | 22
40 | 2012-10-07 | 2466.144 | 14.5524 | 2012-10-03 | 17669 | 18.5
41 | 2012-10-14 | 2487.466 | 9.6857 | 2012-10-11 | 17849 | 12.8
42 | 2012-10-21 | 2473.934 | 11.2143 | 2012-10-15 | 17828 | 11
43 | 2012-10-28 | 2522.418 | 10.6476 | 2012-10-24 | 17874 | 11.4
44 | 2012-11-04 | 2619.849 | 5.0095 | 2012-10-29 | 18597 | 4.3
45 | 2012-11-11 | 2665.5 | 4.9714 | 2012-11-06 | 19302 | 2.7
46 | 2012-11-18 | 2623.09 | 5.5857 | 2012-11-13 | 19161 | 3
47 | 2012-11-25 | 2632.78 | 5.5667 | 2012-11-19 | 18772 | 8.4
48 | 2012-12-02 | 2803.389 | 1.6 | 2012-11-26 | 20012 | 2.5
49 | 2012-12-09 | 2345.457 | 3.6524 | 2012-12-05 | 20217 | 1.5
50 | 2012-12-16 | 3198.076 | 2.019 | 2012-12-11 | 20413 | -1
51 | 2012-12-23 | 3164.706 | 2.6952 | 2012-12-20 | 19846 | 2.6
52 | 2012-12-29 | 2659.264 | -3.1286 | 2012-12-27 | 19078 | -3.1
1 | 2013-01-06 | 2409.875 | -2.2571 | 2013-01-02 | 20601 | -2.8
2 | 2013-01-13 | 2742.03 | 4.7095 | 2013-01-07 | 20172 | 0.3
3 | 2013-01-20 | 2868.518 | -2.2524 | 2013-01-17 | 20779 | -7.3
4 | 2013-01-27 | 3164.884 | -9.9381 | 2013-01-24 | 22423 | -11.6
5 | 2013-02-03 | 2948.027 | -1.8524 | 2013-01-31 | 20602 | -2.6
6 | 2013-02-10 | 3044.013 | -6.3143 | 2013-02-04 | 21493 | -5.8
7 | 2013-02-17 | 2878.093 | -2.5857 | 2013-02-12 | 20053 | 0.6
8 | 2013-02-24 | 2887.399 | -2.9762 | 2013-02-20 | 20805 | -5.5
9 | 2013-03-03 | 2805.264 | -1.3714 | 2013-02-27 | 19831 | 1.5
10 | 2013-03-10 | 2712.272 | 1.7524 | 2013-03-04 | 19863 | -1.8
11 | 2013-03-17 | 2714.361 | 0 | 2013-03-14 | 19065 | 0.1
12 | 2013-03-24 | 2752.129 | -1.081 | 2013-03-20 | 19269 | -1.3
13 | 2013-03-31 | 2517.294 | 5.8 | 2013-03-27 | 18211 | 6.9
14 | 2013-04-07 | 2632.151 | 2.6 | 2013-04-02 | 18820 | 2.5
15 | 2013-04-14 | 2618.614 | 5.0667 | 2013-04-11 | 18375 | 0.1
16 | 2013-04-21 | 2511.671 | 9.0619 | 2013-04-15 | 17215 | 12.6
17 | 2013-04-28 | 2451.728 | 9.219 | 2013-04-24 | 17430 | 12.3
18 | 2013-05-05 | 2371.425 | 17.0143 | 2013-04-29 | 16558 | 13.1
19 | 2013-05-12 | 2398.106 | 15.1762 | 2013-05-08 | 16570 | 21.8
20 | 2013-05-19 | 2365.876 | 14.0905 | 2013-05-13 | 16480 | 10.8
21 | 2013-05-26 | 2410.307 | 15.9429 | 2013-05-21 | 18107 | 24.6
22 | 2013-06-02 | 2602.253 | 21.0667 | 2013-05-31 | 20372 | 29.9
23 | 2013-06-09 | 2403.479 | 15.5667 | 2013-06-06 | 16509 | 14.8
24 | 2013-06-16 | 2505.328 | 19.4238 | 2013-06-12 | 17635 | 22.4
25 | 2013-06-23 | 2631.536 | 20.8857 | 2013-06-23 | 20041 | 31.9
26 | 2013-06-30 | 2860.767 | 23.5286 | 2013-06-24 | 22541 | 31.6
27 | 2013-07-07 | 2765.496 | 23.0667 | 2013-07-04 | 21251 | 27.8
28 | 2013-07-14 | 2882.921 | 23.6619 | 2013-07-10 | 21645 | 30.5
29 | 2013-07-21 | 3288.153 | 27.4 | 2013-07-17 | 24708 | 34.3
30 | 2013-07-28 | 2622.999 | 20.181 | 2013-07-23 | 20105 | 27.4
31 | 2013-08-04 | 2542.321 | 20.2667 | 2013-08-01 | 18382 | 25.7
32 | 2013-08-11 | 2601.064 | 21.5238 | 2013-08-08 | 20078 | 26.5
33 | 2013-08-18 | 2565.818 | 19.9714 | 2013-08-12 | 18022 | 23
34 | 2013-08-25 | 2844.42 | 23.7048 | 2013-08-21 | 22146 | 31.4
35 | 2013-09-01 | 2990.963 | 24.1476 | 2013-08-29 | 22809 | 28.2
36 | 2013-09-08 | 2490.095 | 18.4952 | 2013-09-04 | 18164 | 25.3
37 | 2013-09-15 | 2667.838 | 18.9095 | 2013-09-10 | 22545 | 33.9
38 | 2013-09-22 | 2468.567 | 15.1048 | 2013-09-20 | 17696 | 23.5
39 | 2013-09-29 | 2439.383 | 15.6 | 2013-09-26 | 17321 | 20.5
40 | 2013-10-06 | 2523.773 | 17.9048 | 2013-10-02 | 17992 | 24.6
41 | 2013-10-13 | 2431.049 | 13.5048 | 2013-10-09 | 17386 | 17.6
42 | 2013-10-20 | 2428.382 | 12.4619 | 2013-10-15 | 17497 | 17.1
43 | 2013-10-27 | 2568.283 | 6.6905 | 2013-10-24 | 18084 | 8.3
44 | 2013-11-03 | 2575.664 | 4.3048 | 2013-10-29 | 18356 | 6.6
45 | 2013-11-10 | 2613.409 | 6.2381 | 2013-11-04 | 18791 | 5.2
46 | 2013-11-17 | 2658.795 | 5.3476 | 2013-11-12 | 19763 | 0.5
47 | 2013-11-24 | 2766.996 | 1.0286 | 2013-11-24 | 19790 | -5.2
48 | 2013-11-30 | 2510.417 | -1.4143 | 2013-11-28 | 20469 | -3.3
49 | 2013-12-08 | 2843.653 | 0.71905 | 2013-12-02 | 20029 | 2.5
50 | 2013-12-15 | 3088.18 | -7.5905 | 2013-12-12 | 21727 | -7.8
51 | 2013-12-22 | 2533.378 | -3.0143 | 2013-12-16 | 21867 | -8.3
52 | 2013-12-29 | 3428.571 | -3.4048 | 2013-12-24 | 18960 | -9.9
1 | 2014-01-05 | 2980.559 | -9.9143 | 2014-01-02 | 22342 | -17.9
2 | 2014-01-12 | 3047.657 | -6.2667 | 2014-01-07 | 22725 | -17.4
3 | 2014-01-19 | 2893.573 | -1.0524 | 2014-01-15 | 20465 | -1.2
4 | 2014-01-26 | 3255.467 | -13.2571 | 2014-01-22 | 22717 | -14.4
5 | 2014-02-02 | 3111.181 | -7.5 | 2014-01-28 | 22377 | -12.8
6 | 2014-02-09 | 3095.934 | -9.9333 | 2014-02-05 | 21296 | -6.8
7 | 2014-02-16 | 3077.107 | -8.5905 | 2014-02-11 | 21772 | -10.2
8 | 2014-02-23 | 2869.348 | -1.419 | 2014-02-18 | 20357 | -1.6
9 | 2014-03-02 | 3075.27 | -10.3714 | 2014-02-27 | 21728 | -12.2
10 | 2014-03-09 | 2981.282 | -7.2286 | 2014-03-03 | 21642 | -12.1
11 | 2014-03-16 | 2821.492 | -1.5952 | 2014-03-13 | 20245 | -8
12 | 2014-03-23 | 2834.923 | -1.3905 | 2014-03-17 | 20120 | -4.5
13 | 2014-03-30 | 2824.759 | -1.1238 | 2014-03-26 | 20046 | -5.1
14 | 2014-04-06 | 2621.434 | 4.2762 | 2014-04-03 | 18027 | 3.4
15 | 2014-04-13 | 2520.922 | 10.0714 | 2014-04-07 | 18102 | 9.1
16 | 2014-04-20 | 2506.027 | 6.0381 | 2014-04-15 | 18552 | -0.9
17 | 2014-04-27 | 2474.661 | 8.7905 | 2014-04-22 | 17253 | 11.3
18 | 2014-05-04 | 2476.605 | 9.119 | 2014-04-30 | 17633 | 6.6
19 | 2014-05-11 | 2372.395 | 14.1714 | 2014-05-07 | 16515 | 13
20 | 2014-05-18 | 2395.651 | 13.8714 | 2014-05-13 | 16859 | 20.6
21 | 2014-05-25 | 2331.344 | 17.0905 | 2014-05-21 | 16532 | 19.6
22 | 2014-06-01 | 2471.538 | 19.6524 | 2014-05-27 | 18762 | 29.4
23 | 2014-06-08 | 2515.024 | 19.8333 | 2014-06-02 | 18848 | 29.1
24 | 2014-06-15 | 2543.584 | 19.8952 | 2014-06-12 | 18594 | 26.2
25 | 2014-06-22 | 2599.973 | 21.0667 | 2014-06-17 | 19826 | 31.2
26 | 2014-06-29 | 2819.858 | 23.1095 | 2014-06-24 | 19847 | 27.9
27 | 2014-07-06 | 2714.132 | 23.3429 | 2014-06-30 | 20852 | 30.3
28 | 2014-07-13 | 2669.169 | 22.2 | 2014-07-07 | 20006 | 28.4
29 | 2014-07-20 | 2552.327 | 19.6857 | 2014-07-14 | 18418 | 22.4
30 | 2014-07-27 | 2741.847 | 22.7857 | 2014-07-22 | 21250 | 29.8
31 | 2014-08-03 | 2568.17 | 20.5286 | 2014-08-01 | 18453 | 27
32 | 2014-08-10 | 2650.137 | 21.681 | 2014-08-06 | 18833 | 24.7
33 | 2014-08-17 | 2568.169 | 19.481 | 2014-08-11 | 19849 | 27.5
34 | 2014-08-24 | 2668.166 | 20.7238 | 2014-08-21 | 19519 | 25.7
35 | 2014-08-31 | 2737.966 | 22.9857 | 2014-08-26 | 21457 | 31.3
36 | 2014-09-07 | 2734.093 | 22.9905 | 2014-09-05 | 21341 | 31.4
37 | 2014-09-14 | 2509.656 | 15.7048 | 2014-09-10 | 18939 | 22.7
38 | 2014-09-21 | 2416.075 | 15.4762 | 2014-09-15 | 17138 | 17.8
39 | 2014-09-28 | 2449.553 | 17.6095 | 2014-09-25 | 17439 | 20.9
40 | 2014-10-05 | 2455.573 | 15.6 | 2014-09-29 | 18206 | 23.9
41 | 2014-10-12 | 2413.467 | 10.8429 | 2014-10-09 | 17405 | 13.9
42 | 2014-10-19 | 2395.899 | 13.6714 | 2014-10-14 | 17562 | 22.1
43 | 2014-10-26 | 2452.995 | 10.5667 | 2014-10-20 | 17679 | 11.8
44 | 2014-11-02 | 2516.429 | 6.4143 | 2014-10-30 | 17777 | 9.1
45 | 2014-11-09 | 2562.845 | 6.1619 | 2014-11-07 | 18215 | 9
46 | 2014-11-16 | 2648.011 | 4.2238 | 2014-11-13 | 19129 | 16.5
47 | 2014-11-23 | 2821.612 | -3.4048 | 2014-11-19 | 20091 | 0.8
48 | 2014-11-30 | 2775.392 | 2.7714 | 2014-11-28 | 19823 | 1.3
49 | 2014-12-07 | 3283.115 | -0.72381 | 2014-12-02 | 20813 | -1.2
50 | 2014-12-14 | 2859.799 | 0.39048 | 2014-12-11 | 20252 | -3.9
51 | 2014-12-21 | 2411.784 | 0.33333 | 2014-12-18 | 20068 | -0.7
52 | 2014-12-28 | 2822.78 | 4.4286 | 2014-12-22 | 19495 | 1.6
1 | 2015-01-04 | 2301.463 | -3.0095 | 2014-12-30 | 19294 | -3.4
2 | 2015-01-11 | 3057.961 | -10.5857 | 2015-01-07 | 21689 | -15.7
3 | 2015-01-18 | 3017.139 | -6.4905 | 2015-01-13 | 21134 | -11.6
4 | 2015-01-25 | 2937.356 | -5.0667 | 2015-01-20 | 20704 | -6.7
5 | 2015-02-01 | 3027.87 | -7.981 | 2015-01-27 | 20823 | -6.8
6 | 2015-02-08 | 3041.641 | -8.3238 | 2015-02-02 | 20807 | -11.3
7 | 2015-02-15 | 3084.421 | -11.6714 | 2015-02-12 | 21014 | -14.5
8 | 2015-02-22 | 3132.266 | -13.0905 | 2015-02-19 | 21474 | -15.8
9 | 2015-03-01 | 3090.03 | -12.0143 | 2015-02-23 | 21440 | -15.5
10 | 2015-03-08 | 2913.928 | -5.5048 | 2015-03-05 | 20934 | -9.6
11 | 2015-03-15 | 2638.4 | 3.0333 | 2015-03-09 | 18606 | 5.4
12 | 2015-03-22 | 2632.494 | 1.0476 | 2015-03-18 | 18457 | 2
13 | 2015-03-29 | 2715.982 | -1.5143 | 2015-03-23 | 19292 | -2.9
14 | 2015-04-05 | 2505.908 | 4.6714 | 2015-03-30 | 18059 | 6.9
15 | 2015-04-12 | 2545.891 | 6.8667 | 2015-04-08 | 18322 | 2.4
16 | 2015-04-19 | 2332.075 | 12.8905 | 2015-04-16 | 16601 | 14.9
17 | 2015-04-26 | 2442.08 | 6.4 | 2015-04-23 | 17598 | 2.8
18 | 2015-05-03 | 2313.268 | 14.7286 | 2015-04-27 | 16471 | 12.1
19 | 2015-05-10 | 2410.036 | 18.5333 | 2015-05-08 | 16839 | 24.1
20 | 2015-05-17 | 2348.964 | 15.181 | 2015-05-11 | 17104 | 19.2
21 | 2015-05-24 | 2299.844 | 16.1762 | 2015-05-18 | 16442 | 28.2
22 | 2015-05-31 | 2569.175 | 21.2905 | 2015-05-26 | 19339 | 28.8
23 | 2015-06-07 | 2363.66 | 15.8952 | 2015-06-05 | 17230 | 24.3
24 | 2015-06-14 | 2485.383 | 19.8905 | 2015-06-10 | 18133 | 27.6
25 | 2015-06-21 | 2552.342 | 20.7619 | 2015-06-15 | 18899 | 24.1
26 | 2015-06-28 | 2526.585 | 19.4143 | 2015-06-22 | 19328 | 25.5
27 | 2015-07-05 | 2378.004 | 19.6 | 2015-07-05 | 17258 | 25.6
28 | 2015-07-12 | 2668.985 | 22.2762 | 2015-07-06 | 19906 | 26.6
29 | 2015-07-19 | 2745.486 | 22.7905 | 2015-07-13 | 20698 | 28.1
30 | 2015-07-26 | 2782.495 | 23.7429 | 2015-07-20 | 20434 | 28
31 | 2015-08-02 | 2964.323 | 25.6143 | 2015-07-28 | 22508 | 32.5
32 | 2015-08-09 | 2540.375 | 21.081 | 2015-08-04 | 18181 | 25.8
33 | 2015-08-16 | 2730.578 | 22.8476 | 2015-08-16 | 20595 | 30.4
34 | 2015-08-23 | 2843.997 | 23.1333 | 2015-08-17 | 22396 | 32.1
35 | 2015-08-30 | 2541.425 | 19.3762 | 2015-08-30 | 18040 | 25.4
36 | 2015-09-06 | 3001.099 | 25.8 | 2015-09-02 | 21922 | 32.6
37 | 2015-09-13 | 2697.254 | 20.5619 | 2015-09-08 | 21842 | 28.7
38 | 2015-09-20 | 2580.759 | 20.8571 | 2015-09-17 | 20119 | 27.2
39 | 2015-09-27 | 2446.319 | 17.6476 | 2015-09-24 | 17875 | 22.6
40 | 2015-10-04 | 2421.31 | 13.7714 | 2015-09-28 | 18125 | 21.7
41 | 2015-10-11 | 2401.672 | 14.2333 | 2015-10-05 | 17363 | 14.2
42 | 2015-10-18 | 2381.522 | 9.8905 | 2015-10-15 | 16920 | 17.6
43 | 2015-10-25 | 2450.749 | 11.0286 | 2015-10-21 | 17269 | 10.6
44 | 2015-11-01 | 2485.082 | 8.6429 | 2015-10-26 | 17633 | 9.7
45 | 2015-11-08 | 2402.716 | 11.919 | 2015-11-03 | 17328 | 20.6
46 | 2015-11-15 | 2469.064 | 7.5571 | 2015-11-10 | 17850 | 9.2
47 | 2015-11-22 | 2481.201 | 6.7762 | 2015-11-17 | 17754 | 7.6
48 | 2015-11-29 | 2613.703 | 4.0429 | 2015-11-23 | 19042 | 1.9
49 | 2015-12-06 | 2254.946 | 4.0333 | 2015-11-30 | 19088 | 3
50 | 2015-12-13 | 2968.924 | 6.6667 | 2015-12-07 | 19002 | 5.4
51 | 2015-12-20 | 2633.978 | 3.8429 | 2015-12-16 | 18979 | 4.3
52 | 2015-12-27 | 2384.288 | 7.0238 | 2015-12-21 | 18443 | 6.6
53 | 2016-01-03 | 2531.649 | -0.48095 | 2016-01-03 | 18387 | 1.6
1 | 2016-01-10 | 2788.552 | -1.4333 | 2016-01-04 | 20719 | -11.8
2 | 2016-01-17 | 2880.036 | -4.2095 | 2016-01-11 | 20456 | -6.6
3 | 2016-01-24 | 2913.484 | -6.3286 | 2016-01-19 | 20616 | -4.3
4 | 2016-01-31 | 2737.29 | 1.0238 | 2016-01-29 | 19334 | -5.1
5 | 2016-02-07 | 2659.753 | 2.9048 | 2016-02-04 | 18732 | 2.9
6 | 2016-02-14 | 2928.908 | -8.2524 | 2016-02-11 | 20638 | -10
7 | 2016-02-21 | 2773.267 | -0.43333 | 2016-02-17 | 19976 | -1.4
8 | 2016-02-28 | 2731.77 | 0.31905 | 2016-02-24 | 19513 | 1.7
9 | 2016-03-06 | 2774.538 | -3.5571 | 2016-03-01 | 19933 | -7.9
10 | 2016-03-13 | 2473.733 | 8.8381 | 2016-03-07 | 17751 | 11.5
11 | 2016-03-20 | 2492.021 | 4.8952 | 2016-03-14 | 17209 | 8.7
12 | 2016-03-27 | 2515.03 | 1.9524 | 2016-03-24 | 18071 | -0.2
13 | 2016-04-03 | 2481.273 | 5.0333 | 2016-03-29 | 17370 | 7.2
14 | 2016-04-10 | 2606.917 | -0.86667 | 2016-04-04 | 18021 | -2.4
15 | 2016-04-17 | 2425.388 | 8.0048 | 2016-04-12 | 17669 | 6.7
16 | 2016-04-24 | 2305.512 | 11.7 | 2016-04-18 | 16356 | 22.9
17 | 2016-05-01 | 2362.348 | 7.1381 | 2016-04-25 | 16796 | 7.4
18 | 2016-05-08 | 2270.087 | 12 | 2016-05-02 | 16020 | 12
19 | 2016-05-15 | 2270.723 | 12.219 | 2016-05-12 | 15980 | 20.5
20 | 2016-05-22 | 2256.595 | 14.8667 | 2016-05-19 | 15942 | 19.7
21 | 2016-05-29 | 2403.564 | 23.9762 | 2016-05-27 | 19637 | 28.9
22 | 2016-06-05 | 2599.792 | 21.6619 | 2016-05-30 | 19852 | 27.2
23 | 2016-06-12 | 2375.761 | 17.9857 | 2016-06-11 | 17525 | 30.2
24 | 2016-06-19 | 2588.618 | 21.9857 | 2016-06-19 | 20020 | 32.1
25 | 2016-06-26 | 2743.584 | 23.8762 | 2016-06-20 | 21673 | 34
26 | 2016-07-03 | 2563.388 | 22.3667 | 2016-06-27 | 21680 | 32.5
27 | 2016-07-10 | 2862.87 | 25.3 | 2016-07-07 | 21388 | 30.9
28 | 2016-07-17 | 2832.049 | 24.7 | 2016-07-13 | 22709 | 35
29 | 2016-07-24 | 2927.854 | 26.1476 | 2016-07-22 | 22068 | 35.1
30 | 2016-07-31 | 2899.923 | 25.7333 | 2016-07-27 | 21707 | 33.7
31 | 2016-08-07 | 2944.088 | 25.9571 | 2016-08-04 | 22364 | 31.9
32 | 2016-08-14 | 3104.654 | 27.3571 | 2016-08-10 | 23128 | 34.8
33 | 2016-08-21 | 2925.272 | 24.2952 | 2016-08-19 | 21654 | 29.3
34 | 2016-08-28 | 2849.378 | 24.3524 | 2016-08-25 | 21510 | 29.7
35 | 2016-09-04 | 2647.95 | 21.9714 | 2016-08-30 | 21380 | 30.1
36 | 2016-09-11 | 2875.792 | 25.2 | 2016-09-07 | 23106 | 34.5
37 | 2016-09-18 | 2523.08 | 20.2476 | 2016-09-13 | 18966 | 27.8
38 | 2016-09-25 | 2555.66 | 19.9476 | 2016-09-19 | 19615 | 25.6
39 | 2016-10-02 | 2370.988 | 16.3238 | 2016-09-27 | 16876 | 21.8
40 | 2016-10-09 | 2361.984 | 16.3762 | 2016-10-06 | 17376 | 23
41 | 2016-10-16 | 2300.832 | 13.8333 | 2016-10-11 | 16802 | 16.5
42 | 2016-10-23 | 2378.094 | 13.9857 | 2016-10-18 | 17360 | 25.2
43 | 2016-10-30 | 2466.419 | 7.2143 | 2016-10-27 | 18018 | 5.2
44 | 2016-11-06 | 2047.66 | 10.1714 | 2016-11-02 | 17131 | 18
45 | 2016-11-13 | 2394.658 | 7.9476 | 2016-11-08 | 17349 | 15.8
46 | 2016-11-20 | 2464.404 | 7.9143 | 2016-11-20 | 17779 | 1.4
47 | 2016-11-27 | 2658.614 | 2.5286 | 2016-11-23 | 19203 | 0.2
48 | 2016-12-04 | 2564.837 | 5.7238 | 2016-11-28 | 18210 | 7
49 | 2016-12-10 | 2332.178 | -0.48095 | 2016-12-09 | 19264 | -1.4
50 | 2016-12-18 | 2873.365 | -5.081 | 2016-12-15 | 20657 | -8.1
51 | 2016-12-25 | 3496.243 | -1.5857 | 2016-12-19 | 20592 | -7.8
52 | 2017-01-01 | 2194.803 | 0.15714 | 2016-12-28 | 17992 | -1.8
1 | 2017-01-08 | 2800.458 | -5.0571 | 2017-01-05 | 19869 | -6.6
2 | 2017-01-15 | 2791.668 | -1.5571 | 2017-01-09 | 20192 | -3.3
3 | 2017-01-22 | 2683.189 | 2.3524 | 2017-01-17 | 19118 | 1.7
4 | 2017-01-29 | 2682.02 | 0.59524 | 2017-01-24 | 18640 | 1.2
5 | 2017-02-05 | 2799.958 | -3.9333 | 2017-01-30 | 19704 | -4.9
6 | 2017-02-12 | 2791.09 | -2.3667 | 2017-02-07 | 19584 | -1.1
7 | 2017-02-19 | 2624.133 | 0.45714 | 2017-02-16 | 19189 | -3.7
8 | 2017-02-26 | 2472.737 | 4.5333 | 2017-02-21 | 17837 | 5.5
9 | 2017-03-05 | 2635.347 | -0.2381 | 2017-03-03 | 19004 | -5.6
10 | 2017-03-12 | 2648.322 | -0.27619 | 2017-03-10 | 18977 | -4.6
11 | 2017-03-19 | 2689.337 | -2.681 | 2017-03-13 | 19109 | -6.1
12 | 2017-03-26 | 2570.353 | 2.8857 | 2017-03-22 | 18574 | -2.5
13 | 2017-04-02 | 2479.132 | 6.7571 | 2017-03-30 | 17510 | 2.9
14 | 2017-04-09 | 2395.597 | 8.2048 | 2017-04-06 | 17281 | 7.3
15 | 2017-04-16 | 2228.476 | 13.0762 | 2017-04-12 | 16506 | 7.7
16 | 2017-04-23 | 2301.158 | 10.0524 | 2017-04-20 | 16381 | 5.4
17 | 2017-04-30 | 2255.022 | 11.581 | 2017-04-25 | 15935 | 9.3
18 | 2017-05-07 | 2331.499 | 8.681 | 2017-05-04 | 16227 | 10
19 | 2017-05-14 | 2283.432 | 10.1619 | 2017-05-08 | 16078 | 11.1
20 | 2017-05-21 | 2275.55 | 16.3476 | 2017-05-18 | 17704 | 29.6
21 | 2017-05-28 | 2250.356 | 16.0667 | 2017-05-25 | 15950 | 11.9
22 | 2017-06-04 | 2276.16 | 17.7857 | 2017-05-29 | 16317 | 25.1
23 | 2017-06-11 | 2391.17 | 19.9714 | 2017-06-11 | 18926 | 31.6
24 | 2017-06-18 | 2710.523 | 23.5667 | 2017-06-12 | 21165 | 32.4
25 | 2017-06-25 | 2514.885 | 20.7524 | 2017-06-19 | 18783 | 25.8
26 | 2017-07-02 | 2429.473 | 21.2333 | 2017-06-30 | 18253 | 27.9
27 | 2017-07-09 | 2564.696 | 22.919 | 2017-07-06 | 20312 | 29.6
28 | 2017-07-16 | 2641.147 | 22.4524 | 2017-07-11 | 20191 | 28.9
29 | 2017-07-23 | 2751.121 | 23.7905 | 2017-07-19 | 20580 | 31.5
30 | 2017-07-30 | 2540.604 | 21.8524 | 2017-07-27 | 19098 | 25.8
31 | 2017-08-06 | 2680.86 | 22.7905 | 2017-07-31 | 20184 | 30.8
32 | 2017-08-13 | 2550.852 | 22.0524 | 2017-08-09 | 19389 | 28.7
33 | 2017-08-20 | 2628.866 | 22.0619 | 2017-08-15 | 19198 | 27.2
34 | 2017-08-27 | 2482.693 | 19.8762 | 2017-08-21 | 20313 | 30
35 | 2017-09-03 | 2338.323 | 17.7238 | 2017-08-30 | 17703 | 23.9
36 | 2017-09-10 | 2247.089 | 16.6667 | 2017-09-05 | 16449 | 21
37 | 2017-09-17 | 2489.987 | 21.0095 | 2017-09-14 | 18415 | 27
38 | 2017-09-24 | 2771.142 | 24.2905 | 2017-09-24 | 20394 | 33.3
39 | 2017-10-01 | 2574.485 | 18.5667 | 2017-09-25 | 21682 | 31.3
40 | 2017-10-08 | 2374.265 | 19.4905 | 2017-10-04 | 17491 | 26.5
41 | 2017-10-15 | 2326.158 | 15.8048 | 2017-10-10 | 16620 | 22.9
42 | 2017-10-22 | 2276.504 | 15.0333 | 2017-10-16 | 16750 | 10.1
43 | 2017-10-29 | 2351.981 | 10.3095 | 2017-10-26 | 16698 | 10.6
44 | 2017-11-05 | 2448.709 | 8.081 | 2017-11-01 | 17664 | 6.7
45 | 2017-11-12 | 2573.358 | 2.3333 | 2017-11-10 | 18731 | -4
46 | 2017-11-19 | 2593.993 | 4.0905 | 2017-11-13 | 18616 | 5.3
47 | 2017-11-26 | 2582.342 | 4.1286 | 2017-11-22 | 18924 | 0.1
48 | 2017-12-03 | 2945.44 | 4.6762 | 2017-11-27 | 18998 | 3
49 | 2017-12-10 | 2308.909 | 1.1714 | 2017-12-07 | 19148 | 0.1
50 | 2017-12-17 | 3356.972 | -7.419 | 2017-12-13 | 20293 | -7.5
51 | 2017-12-24 | 2791.103 | -1.4714 | 2017-12-21 | 19627 | -2.9
52 | 2017-12-31 | 2472.533 | -12.5476 | 2017-12-28 | 20010 | -12.8
1 | 2018-01-07 | 3045.502 | -13.0476 | 2018-01-05 | 20747 | -15.2
2 | 2018-01-14 | 2841.975 | -1.9143 | 2018-01-14 | 19921 | -6.7
3 | 2018-01-21 | 2857.148 | -3.4571 | 2018-01-15 | 20175 | -7.3
4 | 2018-01-28 | 2752.903 | 0.21905 | 2018-01-24 | 19844 | -5.3
5 | 2018-02-04 | 2871.627 | -5.0286 | 2018-01-30 | 20211 | -8.3
6 | 2018-02-11 | 2928.324 | -6.9 | 2018-02-07 | 19913 | -5.1
7 | 2018-02-18 | 2730.743 | -0.79524 | 2018-02-13 | 19555 | -4.1
8 | 2018-02-25 | 2622.584 | 4.1095 | 2018-02-22 | 18620 | 1.4
9 | 2018-03-04 | 2536.83 | 3.9667 | 2018-02-26 | 17795 | 7
10 | 2018-03-11 | 2644.177 | -0.085714 | 2018-03-06 | 18393 | 0.2
11 | 2018-03-18 | 2611.579 | -0.17143 | 2018-03-12 | 18079 | -0.3
12 | 2018-03-25 | 2568.737 | -0.24286 | 2018-03-19 | 18015 | -0.1
13 | 2018-04-01 | 2458.085 | 3.9333 | 2018-03-27 | 17354 | 3
14 | 2018-04-08 | 2573.814 | 0.69048 | 2018-04-04 | 17882 | 2.4
15 | 2018-04-15 | 2582.041 | 2.1762 | 2018-04-09 | 17555 | 2.9
16 | 2018-04-22 | 2482.217 | 4.2286 | 2018-04-17 | 17480 | 0.7
17 | 2018-04-29 | 2319.02 | 9.6381 | 2018-04-25 | 16167 | 11
18 | 2018-05-06 | 2239.906 | 17.6238 | 2018-05-02 | 16086 | 27.5
19 | 2018-05-13 | 2234.572 | 13.9381 | 2018-05-08 | 15706 | 18.5
20 | 2018-05-20 | 2255.281 | 16.8667 | 2018-05-14 | 15980 | 24.1
21 | 2018-05-27 | 2375.999 | 20.5714 | 2018-05-25 | 17788 | 30.2
22 | 2018-06-03 | 2694.117 | 23.0476 | 2018-05-28 | 20394 | 30.7
23 | 2018-06-10 | 2332.158 | 17.3524 | 2018-06-08 | 16765 | 21.9
24 | 2018-06-17 | 2570.35 | 22.3571 | 2018-06-17 | 20161 | 31.3
25 | 2018-06-24 | 2589.977 | 20.6095 | 2018-06-18 | 20992 | 30.2
26 | 2018-07-01 | 2799.84 | 24.5 | 2018-06-29 | 21037 | 31
27 | 2018-07-08 | 2918.27 | 25.5048 | 2018-07-05 | 23374 | 33.2
28 | 2018-07-15 | 2959.067 | 25.5905 | 2018-07-15 | 21510 | 29.9
29 | 2018-07-22 | 2806.574 | 23.5857 | 2018-07-16 | 21455 | 31.5
30 | 2018-07-29 | 2804.722 | 23.5524 | 2018-07-24 | 21545 | 29.5
31 | 2018-08-05 | 2903.656 | 25.219 | 2018-08-03 | 21028 | 28.5
32 | 2018-08-12 | 2886.233 | 24.3524 | 2018-08-07 | 21190 | 27.5
33 | 2018-08-19 | 2947.795 | 24.6095 | 2018-08-15 | 21456 | 30.9
34 | 2018-08-26 | 2701.424 | 22.6238 | 2018-08-20 | 20142 | 25
35 | 2018-09-02 | 2867.372 | 23.8286 | 2018-08-28 | 22175 | 31.7
36 | 2018-09-09 | 2762.349 | 22.0048 | 2018-09-05 | 23131 | 33.9
37 | 2018-09-16 | 2678.651 | 21.0952 | 2018-09-16 | 20871 | 28.3
38 | 2018-09-23 | 2579.775 | 19.4524 | 2018-09-17 | 21233 | 26.3
39 | 2018-09-30 | 2380.053 | 15.619 | 2018-09-25 | 17419 | 20.4
40 | 2018-10-07 | 2394.01 | 12.7381 | 2018-10-02 | 16841 | 12.9
41 | 2018-10-14 | 2397.565 | 14.7 | 2018-10-09 | 18640 | 28.6
42 | 2018-10-21 | 2409.557 | 7.7714 | 2018-10-17 | 17040 | 8.5
43 | 2018-10-28 | 2514.239 | 5.3143 | 2018-10-24 | 17481 | 5.2
44 | 2018-11-04 | 2501.666 | 6.3857 | 2018-10-29 | 17267 | 8.5
45 | 2018-11-11 | 2555.529 | 5.1952 | 2018-11-09 | 18209 | 2.6
46 | 2018-11-18 | 2700.142 | 0.41905 | 2018-11-14 | 19232 | 0.3
47 | 2018-11-25 | 2739.306 | -0.68095 | 2018-11-22 | 20048 | -6.6
48 | 2018-12-02 | 2713.598 | 2.5476 | 2018-11-27 | 19248 | 1.2
49 | 2018-12-07 | 2019.62 | -1.8905 | 2018-12-07 | 19686 | -4
50 | 2018-12-16 | 3213.188 | 1.019 | 2018-12-11 | 19718 | -1.4
51 | 2018-12-23 | 2723.873 | 1.019 | 2018-12-18 | 19450 | 0.2
52 | 2018-12-30 | 2915.267 | 0.34286 | 2018-12-27 | 18108 | -0.2
1 | 2019-01-06 | 2616.032 | 0.071429 | 2019-01-02 | 19580 | -3.9
2 | 2019-01-13 | 2826.392 | -4.2524 | 2019-01-10 | 19872 | -5.1
3 | 2019-01-20 | 2947.535 | -6.981 | 2019-01-20 | 20841 | -14.5
4 | 2019-01-27 | 2983.872 | -7.0667 | 2019-01-21 | 21356 | -11.8
5 | 2019-02-03 | 3039.29 | -9.4762 | 2019-01-31 | 21174 | -14.6
6 | 2019-02-10 | 2825.025 | -1.5571 | 2019-02-06 | 19739 | -1.1
7 | 2019-02-17 | 2825.059 | -3.4714 | 2019-02-12 | 20043 | -1.2
8 | 2019-02-24 | 2768.176 | -2.0905 | 2019-02-19 | 19796 | -4.4
9 | 2019-03-03 | 2863.896 | -6.5167 | 2019-02-27 | 20436 | -7.7
10 | 2019-03-10 | 2833.518 | -6.8929 | 2019-03-05 | 20176 | -9
11 | 2019-03-17 | 2603.892 | 1.8333 | 2019-03-11 | 18103 | 2
12 | 2019-03-24 | 2559.903 | 3.1619 | 2019-03-18 | 18023 | 2.6
13 | 2019-03-31 | 2530.669 | 3.3833 | 2019-03-26 | 17633 | 3.6
14 | 2019-04-07 | 2474.168 | 5.1238 | 2019-04-01 | 17516 | 2.8
15 | 2019-04-14 | 2432.225 | 7.019 | 2019-04-11 | 17180 | 1.3
16 | 2019-04-21 | 2348.088 | 8.5762 | 2019-04-15 | 16614 | 8.3
17 | 2019-04-28 | 2332.199 | 9.1143 | 2019-04-24 | 16068 | 12.8
18 | 2019-05-05 | 2398.814 | 8.2857 | 2019-04-29 | 16946 | 6.9
19 | 2019-05-12 | 2293.824 | 11.0429 | 2019-05-09 | 15930 | 14.4
20 | 2019-05-19 | 2311.692 | 12.8381 | 2019-05-13 | 16416 | 7.2
21 | 2019-05-26 | 2263.491 | 16.2048 | 2019-05-22 | 15851 | 15.1
22 | 2019-06-02 | 2321.033 | 15.5857 | 2019-05-27 | 16051 | 22.5
23 | 2019-06-09 | 2325.469 | 17.6571 | 2019-06-07 | 16394 | 25.8
24 | 2019-06-16 | 2313.68 | 17.2286 | 2019-06-10 | 16208 | 18.4
25 | 2019-06-23 | 2433.787 | 20.3857 | 2019-06-19 | 17956 | 24.8
26 | 2019-06-30 | 2699.016 | 23.6095 | 2019-06-27 | 20178 | 28.9
27 | 2019-07-07 | 2873.591 | 24.8952 | 2019-07-05 | 21727 | 30.2
28 | 2019-07-14 | 2776.132 | 23.5 | 2019-07-10 | 21007 | 28.9
29 | 2019-07-21 | 3032.724 | 25.9286 | 2019-07-20 | 21636 | 32.4
30 | 2019-07-28 | 2840.069 | 23.9476 | 2019-07-26 | 21010 | 29.1
31 | 2019-08-04 | 2836.533 | 24.0619 | 2019-07-29 | 21614 | 31.4
32 | 2019-08-11 | 2687.182 | 23.3524 | 2019-08-07 | 20920 | 27.7
33 | 2019-08-18 | 2769.827 | 23.0143 | 2019-08-13 | 21061 | 28.1
34 | 2019-08-25 | 2679.421 | 21.9238 | 2019-08-21 | 21376 | 30.2
35 | 2019-09-01 | 2505.522 | 20.3524 | 2019-08-28 | 18637 | 26.9
36 | 2019-09-08 | 2386.035 | 18.1714 | 2019-09-03 | 17581 | 22
37 | 2019-09-15 | 2435.541 | 18.5333 | 2019-09-11 | 19703 | 28.6
38 | 2019-09-22 | 2476.362 | 20.481 | 2019-09-22 | 18758 | 30.7
39 | 2019-09-29 | 2406.897 | 18.4524 | 2019-09-23 | 17942 | 24.3
40 | 2019-10-06 | 2374.288 | 14.5905 | 2019-10-01 | 18222 | 31.2
41 | 2019-10-13 | 2286.694 | 13.2667 | 2019-10-07 | 16422 | 17.7
42 | 2019-10-20 | 2332.984 | 9.5905 | 2019-10-17 | 16740 | 8.5
43 | 2019-10-27 | 2347.65 | 11.1619 | 2019-10-24 | 16476 | 13.4
44 | 2019-11-03 | 2445.165 | 7.4762 | 2019-11-01 | 17017 | 4.6
45 | 2019-11-10 | 2561.37 | 3.1095 | 2019-11-07 | 18253 | 2.4
46 | 2019-11-17 | 2777.214 | -3.3333 | 2019-11-13 | 19534 | -4.1
47 | 2019-11-24 | 2647.337 | 2.9548 | 2019-11-18 | 19044 | 2.1
48 | 2019-12-01 | 2669.441 | 2.2167 | 2019-12-01 | 19107 | -1.3
49 | 2019-12-08 | 2792.114 | -0.61905 | 2019-12-02 | 19584 | -1.1
50 | 2019-12-15 | 2793.234 | 0.02381 | 2019-12-11 | 20228 | -3
51 | 2019-12-22 | 3251.249 | -3.519 | 2019-12-19 | 20823 | -7.8
52 | 2019-12-29 | 2108.993 | 2.5952 | 2019-12-23 | 17518 | 8.6
1 | 2020-01-05 | 2527.453 | 2.1143 | 2020-01-05 | 17946 | 0.9
2 | 2020-01-12 | 2767.482 | 0.07619 | 2020-01-08 | 19759 | -4.5
3 | 2020-01-19 | 2856.195 | -2.1476 | 2020-01-17 | 19989 | -8.5
4 | 2020-01-26 | 2801.928 | -1.3429 | 2020-01-20 | 19982 | -5.3
5 | 2020-02-02 | 2789.92 | -1.3857 | 2020-01-29 | 19370 | -2.9
6 | 2020-02-09 | 2806.795 | -3.2333 | 2020-02-06 | 19257 | -3.6
7 | 2020-02-16 | 2782.415 | -2.7 | 2020-02-14 | 19813 | -10.4
8 | 2020-02-23 | 2664.318 | -0.86667 | 2020-02-20 | 19663 | -4.7
9 | 2020-03-01 | 2716.574 | -1.5714 | 2020-02-27 | 19116 | -3.8
10 | 2020-03-08 | 2593.923 | 3.1667 | 2020-03-03 | 18046 | 3.8
11 | 2020-03-15 | 2517.192 | 4.9238 | 2020-03-11 | 17662 | 3.4
12 | 2020-03-22 | 2525.756 | 2.5286 | 2020-03-16 | 17414 | 3.9
13 | 2020-03-29 | 2381.873 | 6.3619 | 2020-03-23 | 16935 | 3.5
14 | 2020-04-05 | 2235.936 | 7.5476 | 2020-03-30 | 15763 | 8
15 | 2020-04-12 | 2142.126 | 7.8143 | 2020-04-07 | 14803 | 13.6
16 | 2020-04-19 | 2226.22 | 4.5476 | 2020-04-15 | 15450 | 4.4
17 | 2020-04-26 | 2186.118 | 5.4238 | 2020-04-21 | 15334 | 3.6
18 | 2020-05-03 | 2074.461 | 12.119 | 2020-04-30 | 14475 | 13.2
19 | 2020-05-10 | 2145.501 | 6.1286 | 2020-05-08 | 14730 | 4.8
20 | 2020-05-17 | 2135.825 | 9.4571 | 2020-05-14 | 14954 | 12.3
21 | 2020-05-24 | 2090.504 | 17.2714 | 2020-05-24 | 15545 | 25.7
22 | 2020-05-31 | 2479.051 | 20.7524 | 2020-05-26 | 20582 | 30.6
23 | 2020-06-07 | 2371.542 | 21.3762 | 2020-06-05 | 18973 | 27.6
24 | 2020-06-14 | 2372.026 | 19.4714 | 2020-06-10 | 20580 | 31.6
25 | 2020-06-21 | 2628.362 | 22.7762 | 2020-06-20 | 20024 | 30.4
26 | 2020-06-28 | 2645.033 | 23.619 | 2020-06-22 | 20415 | 29.7
27 | 2020-07-05 | 2942.976 | 27.2571 | 2020-07-02 | 22589 | 34.6
28 | 2020-07-12 | 3181.686 | 27.4905 | 2020-07-09 | 24497 | 34
29 | 2020-07-19 | 2916.228 | 25.219 | 2020-07-17 | 22195 | 30.6
30 | 2020-07-26 | 2890.849 | 24.7905 | 2020-07-26 | 22648 | 33.3
31 | 2020-08-02 | 2948.168 | 25.7048 | 2020-07-27 | 23901 | 31.3
32 | 2020-08-09 | 2606.352 | 22.0048 | 2020-08-09 | 20521 | 30.4
33 | 2020-08-16 | 2967.735 | 25.181 | 2020-08-10 | 23745 | 31.9
34 | 2020-08-23 | 2684.076 | 22.9286 | 2020-08-23 | 21353 | 31.3
35 | 2020-08-30 | 2730.506 | 22.7714 | 2020-08-24 | 23357 | 32.4
36 | 2020-09-06 | 2516.733 | 20.7857 | 2020-09-01 | 20341 | 27.4
37 | 2020-09-13 | 2345.377 | 17.7429 | 2020-09-09 | 16595 | 18.2
38 | 2020-09-20 | 2256.233 | 14.3762 | 2020-09-16 | 16056 | 24.8
39 | 2020-09-27 | 2359.117 | 19.3476 | 2020-09-24 | 16954 | 23.8
40 | 2020-10-04 | 2343.523 | 13.8238 | 2020-09-28 | 18076 | 25.9
41 | 2020-10-11 | 2269.56 | 13.3476 | 2020-10-08 | 16055 | 16
42 | 2020-10-18 | 2268.958 | 12.0095 | 2020-10-15 | 16376 | 11.9
43 | 2020-10-25 | 2387.319 | 10.081 | 2020-10-19 | 16946 | 8
44 | 2020-11-01 | 2495.502 | 5.1714 | 2020-10-27 | 17628 | 7
45 | 2020-11-08 | 2379.319 | 12.1667 | 2020-11-02 | 18169 | 4.2
46 | 2020-11-15 | 2387.329 | 10.2643 | 2020-11-13 | 17331 | 8.7
47 | 2020-11-22 | 2545.051 | 4.6367 | 2020-11-18 | 18958 | 0.2
48 | 2020-11-29 | 2573.636 | 4.75 | 2020-11-24 | 19172 | 0.1
49 | 2020-12-06 | 2264.397 | 0.91905 | 2020-12-01 | 18959 | -0.5
50 | 2020-12-13 | 3079.802 | 2.1429 | 2020-12-07 | 19403 | 0.9
51 | 2020-12-20 | 2811.958 | -2.3 | 2020-12-16 | 20675 | -6.8
52 | 2020-12-27 | 2618.5 | 0.96667 | 2020-12-22 | 19042 | 2.6
53 | 2021-01-03 | 2586.452 | 0.17143 | 2020-12-29 | 19053 | -1.8
1 | 2021-01-10 | 2748.677 | -1.0857 | 2021-01-08 | 19296 | -3.6
2 | 2021-01-17 | 2698.095 | 1.0238 | 2021-01-12 | 19427 | -1.6
3 | 2021-01-24 | 2787.687 | -2.8857 | 2021-01-20 | 19515 | -4.5
4 | 2021-01-31 | 2875.028 | -5.7286 | 2021-01-28 | 20154 | -8.4
5 | 2021-02-07 | 2822.533 | -4.7 | 2021-02-01 | 19818 | -4
6 | 2021-02-14 | 2958.496 | -8.4952 | 2021-02-08 | 20361 | -6.9
7 | 2021-02-21 | 2869.063 | -5.9714 | 2021-02-16 | 20221 | -7.1
8 | 2021-02-28 | 2677.562 | 1.9429 | 2021-02-22 | 18774 | 2.8
9 | 2021-03-07 | 2723.977 | -2.6905 | 2021-03-01 | 19485 | -0.8
10 | 2021-03-14 | 2516.079 | 5.6762 | 2021-03-08 | 18026 | 9.4
11 | 2021-03-21 | 2529.233 | 3.7143 | 2021-03-15 | 17940 | -1.4
12 | 2021-03-28 | 2386.575 | 9.9524 | 2021-03-26 | 16268 | 9.6
13 | 2021-04-04 | 2365.144 | 5.6571 | 2021-04-01 | 16767 | 1.8
14 | 2021-04-11 | 2231.181 | 13.7524 | 2021-04-05 | 15668 | 12.8
15 | 2021-04-18 | 2306.786 | 8.981 | 2021-04-15 | 15802 | 8
16 | 2021-04-25 | 2326.647 | 7.1857 | 2021-04-20 | 16402 | 4.8
17 | 2021-05-02 | 2279.233 | 9.8524 | 2021-04-29 | 15646 | 10.5
18 | 2021-05-09 | 2272.663 | 9.6667 | 2021-05-03 | 15827 | 12.4
19 | 2021-05-16 | 2202.781 | 13.3952 | 2021-05-11 | 15447 | 9.5
20 | 2021-05-23 | 2473.753 | 22.5476 | 2021-05-21 | 19259 | 31.5
21 | 2021-05-30 | 2291.647 | 15.7381 | 2021-05-25 | 19291 | 31.6
22 | 2021-06-06 | 2495.72 | 22.7 | 2021-06-06 | 20677 | 33.5
23 | 2021-06-13 | 2787.64 | 23.981 | 2021-06-07 | 21207 | 31.1
24 | 2021-06-20 | 2453.821 | 20.6667 | 2021-06-20 | 18486 | 26.1
25 | 2021-06-27 | 2575.032 | 22.3714 | 2021-06-27 | 20656 | 30.7
26 | 2021-07-04 | 2714.895 | 23.6476 | 2021-06-28 | 22193 | 31.6
27 | 2021-07-11 | 2618.1 | 21.4429 | 2021-07-06 | 21748 | 31.7
28 | 2021-07-18 | 2759.419 | 23.5571 | 2021-07-14 | 21487 | 29.2
29 | 2021-07-25 | 2705.506 | 22.7714 | 2021-07-19 | 20895 | 28.9
30 | 2021-08-01 | 2564.649 | 21.0333 | 2021-07-26 | 20858 | 30.1
31 | 2021-08-08 | 2701.63 | 23.0857 | 2021-08-05 | 20993 | 27.3
32 | 2021-08-15 | 2947.49 | 25.2476 | 2021-08-09 | 22335 | 30.6
33 | 2021-08-22 | 3002.528 | 25.2429 | 2021-08-19 | 21877 | 30.8
34 | 2021-08-29 | 3137.955 | 26.6333 | 2021-08-24 | 22909 | 33.1
35 | 2021-09-05 | 2602.69 | 21.081 | 2021-08-30 | 21570 | 28.7
36 | 2021-09-12 | 2451.704 | 20.3714 | 2021-09-07 | 18560 | 25.5
37 | 2021-09-19 | 2487.729 | 20.0381 | 2021-09-17 | 18786 | 26
38 | 2021-09-26 | 2359.527 | 16.5143 | 2021-09-21 | 17846 | 24.4
39 | 2021-10-03 | 2347.134 | 16.8976 | 2021-09-27 | 16826 | 24.2
40 | 2021-10-10 | 2423.924 | 17.619 | 2021-10-07 | 17039 | 19.8
41 | 2021-10-17 | 2367.858 | 17.0571 | 2021-10-12 | 17270 | 21.95
42 | 2021-10-24 | 2344.856 | 11.6095 | 2021-10-18 | 16337 | 13.8
43 | 2021-10-31 | 2400.534 | 9.4414 | 2021-10-25 | 16946 | 8.25
44 | 2021-11-07 | 2460.598 | 6.1143 | 2021-11-04 | 17537 | 9
45 | 2021-11-14 | 2451.66 | 8.4762 | 2021-11-14 | 17628 | 4.7
46 | 2021-11-21 | 2567.212 | 5.0238 | 2021-11-16 | 18445 | 5.5
47 | 2021-11-28 | 2679.479 | 1.0571 | 2021-11-23 | 18744 | 3.3
48 | 2021-12-05 | 2748.075 | 1.5714 | 2021-11-29 | 19612 | 0.15
49 | 2021-12-11 | 2859.142 | 1.7429 | 2021-12-08 | 20443 | -2
50 | 2021-12-19 | 2672.947 | 3.8381 | 2021-12-19 | 19133 | -3.4
51 | 2021-12-26 | 2272.806 | 0.59524 | 2021-12-22 | 19457 | -0.7
52 | 2022-01-02 | 2988.475 | 0.20476 | 2022-01-02 | 18986 | -6.3
1 | 2022-01-09 | 2867.241 | -3.8857 | 2022-01-07 | 20239 | -7
2 | 2022-01-16 | 3020.725 | -7.6524 | 2022-01-11 | 21420 | -10
3 | 2022-01-23 | 3009.042 | -7.9667 | 2022-01-20 | 21166 | -12.1
4 | 2022-01-30 | 3094.318 | -10.4095 | 2022-01-24 | 21146 | -6.1
5 | 2022-02-06 | 2960.041 | -4.6905 | 2022-02-04 | 20513 | -10.6
6 | 2022-02-13 | 2832.569 | -2.0286 | 2022-02-13 | 20058 | -9.5
7 | 2022-02-20 | 2885.157 | -3.5571 | 2022-02-14 | 20783 | -9.8
8 | 2022-02-27 | 2837.291 | -3.2381 | 2022-02-23 | 19978 | -4.8
9 | 2022-03-06 | 2781.134 | -1.0857 | 2022-02-28 | 19972 | -5.9
10 | 2022-03-13 | 2756.58 | -1.1571 | 2022-03-07 | 18836 | 1
11 | 2022-03-20 | 2567.324 | 5.881 | 2022-03-15 | 17886 | 0.7
12 | 2022-03-27 | 2584.788 | 3.4905 | 2022-03-23 | 17862 | 3.3
13 | 2022-04-03 | 2631.049 | 1.4714 | 2022-03-28 | 18833 | -5.4
14 | 2022-04-10 | 2445.197 | 7.2524 | 2022-04-04 | 16901 | 7.9
15 | 2022-04-17 | 2301.483 | 9.0905 | 2022-04-11 | 16157 | 12.1
16 | 2022-04-24 | 2395.123 | 7.9476 | 2022-04-18 | 16992 | 6.6
17 | 2022-05-01 | 2357.543 | 8.0619 | 2022-04-27 | 16727 | 3.5
18 | 2022-05-08 | 2288.564 | 11.7905 | 2022-05-03 | 16193 | 12.1
19 | 2022-05-15 | 2420.061 | 19.7 | 2022-05-15 | 18286 | 28.9
20 | 2022-05-22 | 2336.128 | 16.7381 | 2022-05-20 | 16239 | 23.6
21 | 2022-05-29 | 2332.369 | 18.0952 | 2022-05-26 | 17195 | 26.6
22 | 2022-06-05 | 2537.915 | 21.119 | 2022-05-31 | 21305 | 32.2
23 | 2022-06-12 | 2378.093 | 18.9286 | 2022-06-08 | 16558 | 22.2
24 | 2022-06-19 | 2555.752 | 21.0762 | 2022-06-16 | 21211 | 32.2
25 | 2022-06-26 | 2850.099 | 25.3667 | 2022-06-22 | 21826 | 34.6
26 | 2022-07-03 | 2545.54 | 21.8905 | 2022-06-30 | 19242 | 25.7
27 | 2022-07-10 | 2636.564 | 22.2286 | 2022-07-07 | 19479 | 25
28 | 2022-07-17 | 2778.325 | 23.5238 | 2022-07-11 | 20476 | 30.8
29 | 2022-07-24 | 3097.347 | 27.8333 | 2022-07-19 | 22713 | 34.2
30 | 2022-07-31 | 2766.036 | 22.7381 | 2022-07-28 | 20533 | 28.7
31 | 2022-08-07 | 2984.792 | 25.8476 | 2022-08-06 | 21622 | 31.1
32 | 2022-08-14 | 2741.31 | 22.4857 | 2022-08-08 | 21426 | 30.9
33 | 2022-08-21 | 2837.659 | 23.4476 | 2022-08-18 | 20733 | 27.4
34 | 2022-08-28 | 2803.392 | 22.6286 | 2022-08-24 | 21399 | 28.7
35 | 2022-09-04 | 2768.199 | 22.619 | 2022-08-29 | 21697 | 30.5
36 | 2022-09-11 | 2631.655 | 21.2905 | 2022-09-09 | 19909 | 26.5
37 | 2022-09-18 | 2530.077 | 19.6905 | 2022-09-12 | 18941 | 23.7
38 | 2022-09-25 | 2440.529 | 17.8238 | 2022-09-19 | 18808 | 27.5
39 | 2022-10-02 | 2329.524 | 13.3095 | 2022-09-27 | 16395 | 16.5
40 | 2022-10-09 | 2357.445 | 12.8333 | 2022-10-05 | 16565 | 21.6
41 | 2022-10-16 | 2313.652 | 13.2667 | 2022-10-13 | 16252 | 14.8
42 | 2022-10-23 | 2388.92 | 9.681 | 2022-10-20 | 16960 | 6.8
43 | 2022-10-30 | 2366.94 | 10.3714 | 2022-10-27 | 16629 | 9.9
44 | 2022-11-06 | 2383.733 | 13.8714 | 2022-11-02 | 16690 | 14.1
45 | 2022-11-13 | 2451.794 | 8.7333 | 2022-11-08 | 17636 | 9.1
46 | 2022-11-20 | 2743.599 | -0.90476 | 2022-11-20 | 19100 | -3.6
47 | 2022-11-27 | 2668.657 | 4.4095 | 2022-11-21 | 19219 | 7.2
48 | 2022-12-04 | 2720.887 | 2.5619 | 2022-12-01 | 19285 | 1.4
49 | 2022-12-11 | 2390.011 | 1.8667 | 2022-12-09 | 19209 | 0.5
50 | 2022-12-18 | 2877.925 | -1.3429 | 2022-12-12 | 20246 | -2
51 | 2022-12-24 | 2498.242 | -3.5286 | 2022-12-19 | 19892 | 0.8
52 | 2023-01-01 | 3352.878 | 3.9429 | 2022-12-27 | 18647 | -2.7
1 | 2023-01-08 | 2758.054 | 9.2381 | 2023-01-08 | 19145 | 10
2 | 2023-01-15 | 2902.869 | 7.1905 | 2023-01-11 | 19834 | 10
3 | 2023-01-22 | 2848.659 | 7.9524 | 2023-01-19 | 19571 | 10
4 | 2023-01-29 | 2860.668 | 8.8571 | 2023-01-25 | 19602 | 5
5 | 2023-02-05 | 3028.967 | -2.8048 | 2023-02-03 | 21301 | -15.5
6 | 2023-02-12 | 2754.954 | 2.0381 | 2023-02-06 | 19595 | -1.7
7 | 2023-02-19 | 2695.121 | 2.6905 | 2023-02-17 | 19439 | -5
8 | 2023-02-26 | 2840.656 | -2.381 | 2023-02-23 | 20084 | -4.6
9 | 2023-03-05 | 2772.582 | 0.56667 | 2023-02-27 | 19616 | -1.3
10 | 2023-03-12 | 2715.289 | -0.8381 | 2023-03-10 | 18544 | -0.1
11 | 2023-03-19 | 2703.566 | 0.76667 | 2023-03-13 | 18389 | -0.4
12 | 2023-03-26 | 2614.795 | 4.5857 | 2023-03-24 | 17653 | 2.4
13 | 2023-04-02 | 2614.37 | 3.2333 | 2023-03-29 | 17965 | 8.3
14 | 2023-04-09 | 2451.281 | 6.4557 | 2023-04-05 | 17392 | 6.95
15 | 2023-04-16 | 2319.164 | 19.8643 | 2023-04-13 | 16537 | 28.95
16 | 2023-04-23 | 2410.193 | 7.6952 | 2023-04-18 | 16640 | 4.05
17 | 2023-04-30 | 2431.248 | 7.969 | 2023-04-24 | 16656 | 9.05
18 | 2023-05-07 | 2379.279 | 9.5762 | 2023-05-02 | 16484 | 6.5
19 | 2023-05-14 | 2309.979 | 17.3333 | 2023-05-12 | 16648 | 27
20 | 2023-05-21 | 2298.549 | 14.4571 | 2023-05-17 | 15971 | 11
21 | 2023-05-28 | 2277.446 | 15.9619 | 2023-05-28 | 16518 | 27.6
22 | 2023-06-04 | 2714.703 | 23.0333 | 2023-06-02 | 21527 | 31.6
23 | 2023-06-11 | 2434.275 | 18.8905 | 2023-06-05 | 17730 | 24.3
24 | 2023-06-18 | 2430.125 | 18.0333 | 2023-06-18 | 16916 | 24.3
25 | 2023-06-25 | 2777.778 | 22.5524 | 2023-06-21 | 20337 | 26.8
26 | 2023-07-02 | 2730.731 | 22.0952 | 2023-06-30 | 19792 | 25.2
27 | 2023-07-09 | 2919.107 | 24.15 | 2023-07-05 | 22682 | 30.95
28 | 2023-07-16 | 2786.581 | 22.7476 | 2023-07-10 | 21118 | 28.35
29 | 2023-07-23 | 2788.889 | 22.8048 | 2023-07-20 | 20656 | 27
30 | 2023-07-30 | 2930.606 | 24.1381 | 2023-07-27 | 21516 | 29
31 | 2023-08-06 | 2711.472 | 22.0286 | 2023-08-03 | 21295 | 29.1
32 | 2023-08-13 | 2738.292 | 22.9905 | 2023-08-09 | 21125 | 28.2
33 | 2023-08-20 | 2677.927 | 21.3571 | 2023-08-16 | 20821 | 26.8
34 | 2023-08-27 | 2651.031 | 20.1952 | 2023-08-21 | 19471 | 24
35 | 2023-09-03 | 2592.702 | 20.0905 | 2023-09-03 | 19526 | 31.1
36 | 2023-09-10 | 2918.15 | 23.681 | 2023-09-05 | 23559 | 32.1
37 | 2023-09-17 | 2488.632 | 18.1476 | 2023-09-11 | 18965 | 23
38 | 2023-09-24 | 2424.984 | 17.5857 | 2023-09-21 | 17280 | 21.9
39 | 2023-10-01 | 2475.184 | 18.5333 | 2023-10-01 | 17311 | 26.9
40 | 2023-10-08 | 2592.116 | 19.0714 | 2023-10-03 | 20766 | 30
41 | 2023-10-15 | 2404.223 | 10.6143 | 2023-10-10 | 16894 | 12.8
42 | 2023-10-22 | 2435.498 | 11.381 | 2023-10-16 | 16869 | 11.5
43 | 2023-10-29 | 2447.685 | 14.281 | 2023-10-23 | 17013 | 13.7
44 | 2023-11-05 | 2589.671 | 6.2857 | 2023-11-01 | 18170 | 4.4
45 | 2023-11-12 | 2661.355 | 5.2762 | 2023-11-08 | 19366 | 0.6
46 | 2023-11-19 | 2605.763 | 7.1476 | 2023-11-14 | 18301 | 9.1
47 | 2023-11-26 | 2779.011 | 2.1381 | 2023-11-20 | 19479 | 0.4
48 | 2023-12-03 | 2834.018 | 1.181 | 2023-11-28 | 20269 | -1.5
49 | 2023-12-10 | 2834.801 | 3.7381 | 2023-12-06 | 19991 | 0.2
50 | 2023-12-17 | 2375.44 | 3.3714 | 2023-12-13 | 19925 | 3
51 | 2023-12-24 | 3225.166 | 1.119 | 2023-12-19 | 19702 | -0.9
52 | 2023-12-31 | 2549.777 | 4.4571 | 2023-12-30 | 18241 | 0.2
1 | 2024-01-07 | 2849.764 | -1.4905 | 2024-01-04 | 20109 | -3.1
2 | 2024-01-14 | 2902.584 | 0.1381 | 2024-01-09 | 19874 | 2.2
3 | 2024-01-21 | 3119.757 | -8.9571 | 2024-01-15 | 21081 | -9
4 | 2024-01-28 | 2918.879 | 1.0667 | 2024-01-22 | 20456 | -1.2
5 | 2024-02-04 | 2831.597 | 1.5333 | 2024-01-30 | 19523 | 1.9
6 | 2024-02-11 | 2726.211 | 3.6762 | 2024-02-05 | 19112 | 3.1
7 | 2024-02-18 | 2880.556 | -1.9381 | 2024-02-16 | 19521 | -1
8 | 2024-02-25 | 2756.548 | 0.65714 | 2024-02-20 | 19025 | 3.2
9 | 2024-03-03 | 2696.804 | 4.4714 | 2024-02-29 | 19624 | -3
10 | 2024-03-10 | 2565.62 | 7.0524 | 2024-03-10 | 17541 | -0.6
11 | 2024-03-17 | 2534.182 | 7.4952 | 2024-03-11 | 17323 | 7.4
12 | 2024-03-24 | 2779.916 | -2.0095 | 2024-03-21 | 18902 | -1.8
13 | 2024-03-31 | 2532.722 | 5.8857 | 2024-03-27 | 17508 | 10.9
14 | 2024-04-07 | 2543.842 | 6.3429 | 2024-04-03 | 17947 | 6.1
15 | 2024-04-14 | 2412.129 | 11.3762 | 2024-04-11 | 16619 | 12.9
16 | 2024-04-21 | 2435.482 | 9.7095 | 2024-04-19 | 16584 | 14.9
17 | 2024-04-28 | 2396.297 | 10.1905 | 2024-04-25 | 16506 | 7.9
18 | 2024-05-05 | 2359.978 | 14.4286 | 2024-04-29 | 16329 | 9.9
19 | 2024-05-12 | 2327.749 | 14.3762 | 2024-05-08 | 15988 | 20
20 | 2024-05-19 | 2416.477 | 18.1333 | 2024-05-16 | 16619 | 20.9
21 | 2024-05-26 | 2591.702 | 21.6048 | 2024-05-22 | 20402 | 29.1
22 | 2024-06-02 | 2405.724 | -2.25 | 2024-05-27 | 17291 | 24.2
23 | 2024-06-09 | 2598.025 | 19.8381 | 2024-06-04 | 20692 | 26.8
24 | 2024-06-16 | 2526.989 | 18.9429 | 2024-06-13 | 20220 | 30.1
25 | 2024-06-23 | 3110.749 | 25.1476 | 2024-06-19 | 23803 | 34.2
26 | 2024-06-30 | 2666.331 | 21.3905 | 2024-06-24 | 20982 | 28.1
27 | 2024-07-07 | 2847.757 | 23.4619 | 2024-07-05 | 21578 | 27.9
28 | 2024-07-14 | 3022.439 | 24.0048 | 2024-07-08 | 21979 | 29
29 | 2024-07-21 | 2875.998 | 23.0381 | 2024-07-15 | 21430 | 23.8
30 | 2024-07-28 | 2910.273 | 23.4857 | 2024-07-28 | 21710 | 28.2
31 | 2024-08-04 | 3254.234 | 26.4238 | 2024-07-31 | 23206 | 31.1
32 | 2024-08-11 | 2751.129 | 21.4048 | 2024-08-09 | 20784 | 27.2
33 | 2024-08-18 | 2901.005 | 22.8524 | 2024-08-15 | 21982 | 27.9
34 | 2024-08-25 | 2605.803 | 19.519 | 2024-08-25 | 20707 | 27.1
35 | 2024-09-01 | 2935.475 | 23.1095 | 2024-08-27 | 22503 | 31.1
36 | 2024-09-08 | 2504.95 | 17.9238 | 2024-09-05 | 19873 | 24.2
37 | 2024-09-15 | 2678.865 | 20.381 | 2024-09-15 | 20402 | 27.1
38 | 2024-09-22 | 2801.838 | 21.5381 | 2024-09-16 | 21643 | 28
39 | 2024-09-29 | 2595.066 | 20.181 | 2024-09-26 | 18357 | 24
40 | 2024-10-06 | 2493.17 | 17.5476 | 2024-09-30 | 18453 | 22.8
41 | 2024-10-13 | 2457.04 | 12.0524 | 2024-10-10 | 17159 | 14.2
42 | 2024-10-20 | 2448.06 | 10.6952 | 2024-10-16 | 17205 | 10.2
43 | 2024-10-27 | 2498.609 | 12.8571 | 2024-10-21 | 17209 | 26
44 | 2024-11-03 | 2540.856 | 11.4381 | 2024-10-28 | 17591 | 9.8
45 | 2024-11-10 | 2533.01 | 12.1333 | 2024-11-04 | 17812 | 14.1
46 | 2024-11-17 | 2641.032 | 7.1095 | 2024-11-14 | 18497 | 8.9
47 | 2024-11-24 | 2663.051 | 6.5429 | 2024-11-21 | 18481 | 5.1
48 | 2024-11-30 | 2406.491 | 1.4476 | 2024-12-01 | 19212 | 0.8
49 | 2024-12-08 | 3401.395 | -0.49048 | 2024-12-06 | 20421 | -2
50 | 2024-12-15 | 3408.632 | -0.40952 | 2024-12-12 | 20991 | -4.8
51 | 2024-12-22 | 2989.209 | -2.1143 | 2024-12-22 | 21016 | -10.5
52 | 2024-12-29 | 2783.16 | 1.2048 | 2024-12-23 | 20350 | -0.6
1 | 2025-01-05 | 2425.874 | -0.4 | 2025-01-05 | 20647 | -1
2 | 2025-01-12 | 3122.446 | -5.7095 | 2025-01-08 | 21504 | -6.6
3 | 2025-01-19 | 3073.46 | -3.7238 | 2025-01-16 | 21103 | -4.9
4 | 2025-01-26 | 3205.609 | -8.319 | 2025-01-22 | 22058 | -12
5 | 2025-02-02 | 3099.635 | -4.4762 | 2025-01-28 | 21092 | -5.1
6 | 2025-02-09 | 3112.475 | -3.5952 | 2025-02-05 | 20917 | -5.1
7 | 2025-02-16 | 3116.52 | -5.6286 | 2025-02-12 | 21115 | -6
8 | 2025-02-23 | 3096.877 | -7.2286 | 2025-02-19 | 21399 | -6.9
9 | 2025-03-02 | 2911.95 | -0.36667 | 2025-03-02 | 20232 | -5.3
10 | 2025-03-09 | 2836.548 | 1.5381 | 2025-03-03 | 19553 | 2.8
11 | 2025-03-16 | 2636.842 | 6.4333 | 2025-03-12 | 18720 | 0.9
12 | 2025-03-23 | 2626.909 | 5.7762 | 2025-03-17 | 18437 | 5.1
13 | 2025-03-30 | 2740.993 | 2.6714 | 2025-03-26 | 18565 | 3.8
14 | 2025-04-06 | 2616.332 | 5.5143 | 2025-04-02 | 19271 | 0.1
15 | 2025-04-13 | 2656.301 | 3.5143 | 2025-04-08 | 18508 | 1.1
16 | 2025-04-20 | 2463.399 | 9.6571 | 2025-04-16 | 17570 | 5.8
17 | 2025-04-27 | 2431.357 | 12.9714 | 2025-04-23 | 16501 | 15
18 | 2025-05-04 | 2422.202 | 12.2143 | 2025-05-01 | 16635 | 9.1
19 | 2025-05-11 | 2401.107 | 14.1952 | 2025-05-07 | 16320 | 23
20 | 2025-05-18 | 2500.327 | 18.5476 | 2025-05-16 | 18190 | 27.1
21 | 2025-05-25 | 2409.852 | 10.9952 | 2025-05-22 | 16664 | 10.8
22 | 2025-06-01 | 2412.068 | 15.2714 | 2025-05-28 | 16694 | 15.8
23 | 2025-06-08 | 2536.713 | 20.9333 | 2025-06-04 | 19623 | 31
24 | 2025-06-15 | 2531.677 | 19.9048 | 2025-06-11 | 18815 | 28
25 | 2025-06-22 | 2906.411 | 23.4048 | 2025-06-22 | 23182 | 34.8
26 | 2025-06-29 | 3142.408 | 25.1905 | 2025-06-24 | 24775 | 34.9
27 | 2025-07-06 | 3012.732 | 25.3048 | 2025-07-06 | 22563 | 34.2
28 | 2025-07-13 | 3222.327 | 26.0905 | 2025-07-12 | 22876 | 33.9
29 | 2025-07-20 | 3088.335 | 24.581 | 2025-07-16 | 23555 | 32.2
30 | 2025-07-27 | 3108.112 | 24.7048 | 2025-07-24 | 24399 | 33.2
31 | 2025-08-03 | 3042.594 | 24.8095 | 2025-07-28 | 24287 | 33
32 | 2025-08-10 | 3177.885 | 26.0238 | 2025-08-10 | 23996 | 32
33 | 2025-08-17 | 3311.213 | 26.2333 | 2025-08-11 | 24500 | 32.2
34 | 2025-08-24 | 2778.805 | 20.8857 | 2025-08-22 | 21032 | 26
35 | 2025-08-31 | 2507.418 | 17.1143 | 2025-08-25 | 17829 | 20.1
36 | 2025-09-07 | 2556.472 | 18.8238 | 2025-09-03 | 19590 | 26.8
37 | 2025-09-14 | 2598.283 | 19.419 | 2025-09-11 | 18587 | 24.9
38 | 2025-09-21 | 2652.341 | 19.8714 | 2025-09-18 | 19991 | 29.2
39 | 2025-09-28 | 2718.456 | 20.881 | 2025-09-23 | 19440 | 25
40 | 2025-10-05 | 2579.618 | 18.7238 | 2025-10-05 | 19379 | 26.9
41 | 2025-10-12 | 2545.678 | 14.9476 | 2025-10-06 | 20310 | 28
42 | 2025-10-19 | 2471.523 | 14.3762 | 2025-10-14 | 17088 | 21.2
43 | 2025-10-26 | 2571.18 | 9.4429 | 2025-10-23 | 17344 | 12.2
44 | 2025-11-02 | 2635.246 | 7.1714 | 2025-10-30 | 17825 | 7.9
45 | 2025-11-09 | 2719.497 | 6.3333 | 2025-11-09 | 19023 | -1.1
46 | 2025-11-16 | 2837.142 | 3.0476 | 2025-11-10 | 19827 | -2.9
47 | 2025-11-23 | 2844.141 | 3.9286 | 2025-11-17 | 19615 | 4.2
48 | 2025-11-30 | 2893.457 | -2.25 | 2025-11-27 | 19546 | 3
49 | 2025-12-07 | 3100.884 | -2.7762 | 2025-12-04 | 21541 | -4.9
50 | 2025-12-13 | 3648.047 | -5.1524 | 2025-12-08 | 21364 | -3.9
51 | 2025-12-21 | 3515.775 | -0.66667 | 2025-12-15 | 21321 | -4.8
52 | 2025-12-28 | 2119.727 | -1.6 | 2025-12-22 | 20284 | 3.2
1 | 2026-01-04 | 3046.55 | -5.1524 | 2026-01-04 | 20788 | -1.2
2 | 2026-01-11 | 3001.914 | 1.9048 | 2026-01-05 | 20994 | -0.1
3 | 2026-01-18 | 3110.401 | -2.7905 | 2026-01-15 | 21534 | -11
4 | 2026-01-25 | 3290.768 | -9.981 | 2026-01-25 | 22064 | -11
5 | 2026-02-01 | 3303.21 | -11.7571 | 2026-01-29 | 22022 | -12
6 | 2026-02-08 | 3258.679 | -9.3952 | 2026-02-08 | 21644 | -13.2
7 | 2026-02-15 | 3105.124 | -3.5476 | 2026-02-09 | 21821 | -8.1
8 | 2026-02-22 | 2957.738 | 0.87143 | 2026-02-18 | 20456 | -0.2
9 | 2026-02-28 | 2603.031 | -2.25 | 2026-02-24 | 20716 | -4.2
Back to main menu

## Table 1.4.2
Back to main menu
Table 1.4.2: Monthly Weather and Demand History
Month | Energy Demand (GWh) | Reported Embedded Generation (GWh) | Peak Demand (MW) | Average Hour (MW) | Minimum Hour (MW) | 90th Percentile (MW) | # of Hours Above 20,000MW (hrs) | Average Temperature (°C) | Weather Corrected Energy (GWh) | Forecasted Energy (GWh) | Energy Forecast MAPE | Peak Temperature (°C) | Weather Corrected Peak (MW) | Forecasted Peak (MW) | Peak Forecast MAPE
2002-05-31 | 11874.901 |  | 20068 | 15960.8884 | 12092 | 18344.4 | 1 | 12.4667 | 11661.943 | 11525.8367 | 1.167% | 27.9 | 20244.5263 | 19777 | 2.309%
2002-06-30 | 12185.238 |  | 23578 | 16923.9417 | 11537 | 20698 | 97 | 20.19 | 12055.7597 | 11830.544 | 1.868% | 30.7 | 23272.9209 | 21897 | 5.912%
2002-07-31 | 14033.343 |  | 25226 | 18862.0202 | 12348 | 23309.7 | 261 | 25.514 | 13532.3366 | 12956.0938 | 4.258% | 34.7 | 23653.7174 | 23007.2548 | 2.733%
2002-08-31 | 13748.878 |  | 25414 | 18479.6747 | 13077 | 22694.7 | 207 | 23.8785 | 13322.4613 | 12822.9862 | 3.749% | 33.4 | 24272.2514 | 22720.1818 | 6.394%
2002-09-30 | 12593.138 |  | 25062 | 17490.4694 | 12409 | 20801 | 114 | 21.43 | 12144.4221 | 11393.0328 | 6.187% | 33.5 | 21739.209 | 21099.9455 | 2.941%
2002-10-31 | 12397.839 |  | 21216 | 16663.7621 | 12244 | 19077.2 | 25 | 9.8516 | 12155.0684 | 12042.8325 | 0.9234% | 28.8 | 19901.5621 | 20319.2849 | 2.099%
2002-11-30 | 12655.667 |  | 21862 | 17577.3153 | 12709 | 20027.2 | 75 | 3.7489 | 12836.1101 | 12370.454 | 3.628% | 0.1 | 22314.4629 | 22421.8556 | 0.4813%
2002-12-31 | 13483.864 |  | 23334 | 18070.6062 | 13057 | 21021.7 | 197 | -1.2538 | 13500.9659 | 13362.8148 | 1.023% | -1.2 | 23550.9979 | 23522.7043 | 0.1201%
2003-01-31 | 14486.674 |  | 24158 | 19471.336 | 13236 | 22223.4 | 346 | -7.272 | 14211.1695 | 13919.5093 | 2.052% | -13.4 | 23893.0266 | 23850.0397 | 0.1799%
2003-02-28 | 13122.529 |  | 23469 | 19527.5729 | 14523 | 21982.3 | 315 | -6.0738 | 12808.0447 | 12426.863 | 2.976% | -10 | 22949.8962 | 23272.5444 | 1.406%
2003-03-31 | 13414.004 |  | 23117 | 18029.5753 | 13289 | 20781.2 | 142 | 0.44409 | 13159.4331 | 12901.8683 | 1.957% | -14.3 | 21751.8023 | 22090.2796 | 1.556%
2003-04-30 | 12097.332 |  | 21010 | 16801.85 | 12290 | 19540.6 | 53 | 6.7444 | 12069.9486 | 11760.2993 | 2.565% | -1.8 | 20846.9119 | 19850.9002 | 4.778%
2003-05-31 | 11627.445 |  | 18741 | 15628.2863 | 11604 | 17985.6 | 0 | 13.2559 | 11741.5567 | 11691.2195 | 0.4287% | 13.1 | 19844.7318 | 19853.0281 | 0.04181%
2003-06-30 | 11884.956 |  | 24753 | 16506.8833 | 11821 | 19404.9 | 58 | 19.6744 | 11841.7488 | 12214.3634 | 3.147% | 33.3 | 23523.3557 | 22798.6336 | 3.081%
2003-07-31 | 12897.586 |  | 23175 | 17335.4651 | 11957 | 20680.5 | 139 | 22.7849 | 12968.9604 | 13433.0128 | 3.578% | 31.3 | 23762.5491 | 23684.1903 | 0.3298%
2003-08-31 | 12514.308 |  | 23891 | 16820.3065 | 2270 | 21000.8 | 144 | 22.5495 | 12171.8874 | 13155.7383 | 8.083% | 31 | 23561.0011 | 23347.1957 | 0.9075%
2003-09-30 | 11794.469 |  | 20700 | 16381.2069 | 11802 | 19023.3 | 14 | 18.04 | 11779.2706 | 11789.027 | 0.08283% | 26.8 | 20307.2007 | 21599.7344 | 6.365%
2003-10-31 | 12159.932 |  | 20408 | 16343.9946 | 11941 | 18583.6 | 4 | 9.9935 | 12134.778 | 12368.2786 | 1.924% | 9.7 | 21259.1741 | 20666.6154 | 2.787%
2003-11-30 | 12389.858 |  | 21584 | 17208.1361 | 12724 | 19670.3 | 54 | 5.4578 | 12865.0242 | 12585.1188 | 2.176% | 13.4 | 22716.1034 | 22681.1697 | 0.1538%
2003-12-31 | 13327.663 |  | 22798 | 17779.9919 | 12550 | 20959.3 | 165 | 0.45591 | 13534.0494 | 13768.4138 | 1.732% | -5.6 | 23431.3362 | 23858.3895 | 1.823%
2004-01-31 | 14767.413 |  | 24937 | 19848.6734 | 13219 | 22977 | 399 | -8.5817 | 14323.0642 | 14191.7421 | 0.9169% | -19.7 | 24408.7438 | 24078.4061 | 1.353%
2004-02-29 | 13088.075 |  | 22608 | 18804.7055 | 14243 | 21145.5 | 249 | -2.554 | 13173.0548 | 13033.9545 | 1.056% | -3.9 | 23057.4279 | 23556.2598 | 2.163%
2004-03-31 | 13224.641 |  | 21634 | 17775.0551 | 13238 | 20123.3 | 84 | 2.9398 | 13203.0654 | 13279.366 | 0.5779% | -3.1 | 21870.1159 | 22452.4608 | 2.663%
2004-04-30 | 11792.132 |  | 19911 | 16377.9611 | 12427 | 18638.3 | 0 | 7.9389 | 11874.9664 | 11891.0349 | 0.1353% | 3.2 | 20525.8394 | 19942.5254 | 2.842%
2004-05-31 | 11835.269 |  | 20327 | 15907.6196 | 11983 | 18401.3 | 4 | 14.3634 | 11790.5055 | 11844.4455 | 0.4575% | 27.3 | 20053.0994 | 20166.6217 | 0.5661%
2004-06-30 | 12045.885 |  | 23163 | 16730.3958 | 12059 | 19989.2 | 72 | 18.8211 | 12217.9222 | 12553.0052 | 2.743% | 31.3 | 23163 | 23585.4466 | 1.824%
2004-07-31 | 12769.985 |  | 23976 | 17163.9583 | 12385 | 20583.8 | 94 | 21.7398 | 12930.3649 | 13366.3211 | 3.372% | 30.1 | 24618.2502 | 23677.3092 | 3.822%
2004-08-31 | 12746.297 |  | 23159 | 17132.1183 | 12223 | 20350.3 | 97 | 20.7581 | 12964.5229 | 13300.7716 | 2.594% | 28.6 | 23229.7881 | 23298.2624 | 0.2948%
2004-09-30 | 12369.687 |  | 21911 | 17180.1208 | 12285 | 20296.4 | 102 | 19.7733 | 12205.4933 | 11892.6387 | 2.563% | 25.8 | 20958.8749 | 21881.4147 | 4.402%
2004-10-31 | 12215.166 |  | 19829 | 16418.2339 | 12343 | 18770.5 | 0 | 11.7656 | 12456.5009 | 12357.6295 | 0.7937% | 8.8 | 20925.8279 | 21212.056 | 1.368%
2004-11-30 | 12601.008 |  | 22066 | 17501.4 | 12969 | 19980.6 | 71 | 5.8989 | 13148.5344 | 12864.0567 | 2.164% | 5 | 23333.9595 | 22748.6257 | 2.509%
2004-12-31 | 13981.717 |  | 24979 | 18705.2554 | 14169 | 21867.1 | 261 | -2.0914 | 13836.9923 | 13651.944 | 1.337% | -12.3 | 24073.4484 | 23404.0469 | 2.781%
2005-01-31 | 14619.18 |  | 24362 | 19649.4355 | 13545 | 22555.1 | 356 | -6.0849 | 14521.4247 | 14269.3901 | 1.736% | -14.5 | 24173.3301 | 23890.98 | 1.168%
2005-02-28 | 12731.835 |  | 22322 | 18946.183 | 14854 | 21241.5 | 249 | -2.7 | 12865.7476 | 12795.0929 | 0.5492% | -3.9 | 22791.1102 | 23507.03 | 3.141%
2005-03-31 | 13494.28 |  | 22724 | 18137.4731 | 13959 | 20632.1 | 143 | -0.29892 | 13288.2099 | 13401.8026 | 0.8548% | -8.5 | 22667.3301 | 22370.34 | 1.31%
2005-04-30 | 11827.861 |  | 19343 | 16427.5847 | 12279 | 18455.1 | 0 | 9.0533 | 12209.0045 | 12063.7878 | 1.189% | 10.9 | 20931.6333 | 20760.1 | 0.8195%
2005-05-31 | 11744.825 |  | 19007 | 15786.0551 | 11950 | 18139.5 | 0 | 13.2495 | 11734.2216 | 11928.3062 | 1.654% | 22.3 | 18687.7703 | 20306.03 | 8.659%
2005-06-30 | 13499.266 |  | 26157 | 18748.9806 | 12066 | 23349.8 | 260 | 23.7111 | 12679.5247 | 12284.376 | 3.116% | 31.6 | 24410.9107 | 23402.64 | 4.13%
2005-07-31 | 14094.375 |  | 26160 | 18944.0524 | 12109 | 23810.9 | 277 | 25.2505 | 13572.7661 | 13233.9731 | 2.496% | 34.6 | 25823.1716 | 23820.5 | 7.755%
2005-08-31 | 14031.29 |  | 25816 | 18859.2608 | 13487 | 22804.3 | 274 | 23.672 | 13565.2965 | 13465.8968 | 0.7327% | 32.9 | 24779.5218 | 23372.48 | 5.678%
2005-09-30 | 12552.618 |  | 23914 | 17434.1917 | 12541 | 20722.2 | 140 | 20.12 | 12367.9416 | 12151.9814 | 1.746% | 30.1 | 21719.6272 | 22078.34 | 1.652%
2005-10-31 | 12187.328 |  | 20752 | 16380.8172 | 12112 | 18944.1 | 22 | 11.9323 | 12126.6613 | 12472.8188 | 2.855% | 25.8 | 21108.1878 | 20922.81 | 0.8782%
2005-11-30 | 12440.55 |  | 22564 | 17278.5417 | 12548 | 20020.1 | 74 | 5.5967 | 12682.2654 | 12867.08 | 1.457% | -6.3 | 22614.2615 | 22937.6 | 1.43%
2005-12-31 | 13745.639 |  | 23766 | 18422.0914 | 12673 | 21484.9 | 250 | -2.7237 | 13620.1354 | 13796.3409 | 1.294% | -4.8 | 24097.0219 | 23641.84 | 1.889%
2006-01-31 | 13596.17 |  | 23052 | 18274.4207 | 13644 | 20907.3 | 189 | 0.7957 | 14274.4358 | 14424.4515 | 1.051% | -5 | 24238.2139 | 24284.96 | 0.1929%
2006-02-28 | 12568.25 | 196.7766 | 22321 | 18702.753 | 14051 | 20957.7 | 220 | -3.0024 | 12600.0722 | 12948.2914 | 2.764% | -0.9 | 22387.273 | 23800.5 | 6.313%
2006-03-31 | 13199.998 | 174.9678 | 21772 | 17741.9341 | 13274 | 20091.1 | 83 | 2.3215 | 13175.0216 | 13634.8299 | 3.49% | -2.2 | 22053.7104 | 22821.37 | 3.481%
2006-04-30 | 11512.852 | 209.6124 | 19582 | 15990.0722 | 12020 | 18469.4 | 0 | 9.45 | 11956.204 | 12047.9755 | 0.7676% | 3.7 | 20333.283 | 20910.04 | 2.837%
2006-05-31 | 11927.478 | 182.5572 | 24857 | 16031.5565 | 11812 | 18116.3 | 42 | 15.6548 | 11823.8872 | 12279.9916 | 3.857% | 32.8 | 21889.4457 | 21678.33 | 0.9645%
2006-06-30 | 12541.936 | 156.8548 | 23349 | 17419.3556 | 11957 | 20688.4 | 143 | 20.8756 | 12477.8857 | 12623.9122 | 1.17% | 30.6 | 23612.7463 | 23998.72 | 1.635%
2006-07-31 | 13853.619 | 105.9768 | 26092 | 18620.4556 | 12470 | 22948.8 | 269 | 24.6108 | 13347.7145 | 13679.2646 | 2.484% | 33.6 | 25257.3418 | 25397.46 | 0.5548%
2006-08-31 | 13308.1 | 102.0594 | 27005 | 17887.2312 | 12545 | 21104.2 | 172 | 22.2785 | 13263.4984 | 13630.8008 | 2.769% | 36.4 | 23880.5188 | 24805.29 | 3.872%
2006-09-30 | 11521.035 | 75.3164 | 19976 | 16001.4375 | 11796 | 18524.1 | 0 | 16.6411 | 11661.5416 | 12254.9406 | 5.089% | 28 | 21526.7648 | 23566.96 | 9.477%
2006-10-31 | 11962.307 | 112.2613 | 19590 | 16078.3696 | 11621 | 18409.9 | 0 | 9.7226 | 11803.3843 | 12521.8009 | 6.087% | 13.5 | 20459.0154 | 21498.15 | 5.079%
2006-11-30 | 12178.739 | 217.4506 | 21267 | 16914.9153 | 12720 | 19351.1 | 30 | 5.9711 | 12633.6484 | 12892.685 | 2.05% | 1.5 | 22968.2115 | 23080.82 | 0.4903%
2006-12-31 | 12884.176 | 213.476 | 22941 | 18010.0014 | 12246 | 20322.4 | 107 | 2.4269 | 13331.6936 | 13800.6488 | 3.518% | -5.5 | 23625.9393 | 24123.74 | 2.107%
2007-01-31 | 13758.097 | 206.1901 | 23537 | 17914.1888 | 12941 | 21448 | 243 | -2.2806 | 14060.0462 | 14347.6006 | 2.045% | -13.1 | 23776.8339 | 24407.33 | 2.652%
2007-02-28 | 13037.578 | 188.1128 | 23935 | 19401.1577 | 14894 | 21908 | 280 | -7.169 | 12657.9939 | 12799.7079 | 1.12% | -14 | 23053.0639 | 23805.23 | 3.263%
2007-03-31 | 13192.72 | 130.1285 | 22969 | 17732.1519 | 13331 | 20433.1 | 121 | 1.6097 | 13158.0262 | 13334.4268 | 1.341% | -12.5 | 22680.4017 | 22410.89 | 1.188%
2007-04-30 | 11827.647 | 154.9039 | 20016 | 16427.2875 | 11819 | 18975.2 | 1 | 7.2678 | 11883.5165 | 11833.3207 | 0.4224% | 4.1 | 21218.7001 | 20306.68 | 4.298%
2007-05-31 | 11818.634 | 186.5976 | 21490 | 15885.2608 | 11814 | 18653.5 | 33 | 15.9075 | 11715.6686 | 11997.9552 | 2.409% | 27.5 | 18881.5106 | 20882.55 | 10.6%
2007-06-30 | 12692.547 | 117.2711 | 25737 | 17628.5375 | 11699 | 21772.7 | 166 | 22.0044 | 12370.1039 | 12397.7724 | 0.2237% | 34.2 | 24968.2328 | 24501.25 | 1.87%
2007-07-31 | 12840.811 | 117.543 | 24561 | 17259.1546 | 11710 | 21065 | 133 | 22.6237 | 13020.6286 | 13470.8252 | 3.458% | 32.6 | 24937.0822 | 25524.57 | 2.356%
2007-08-31 | 13454.57 | 94.9993 | 25584 | 18084.0995 | 12293 | 22075.9 | 206 | 23.614 | 13116.9687 | 13368.0197 | 1.914% | 34.5 | 24566.9071 | 24734.55 | 0.6824%
2007-09-30 | 11916.219 | 59.8788 | 24046 | 16550.3042 | 11867 | 19637 | 51 | 19.5556 | 11730.0385 | 11853.5568 | 1.053% | 32.9 | 20976.0219 | 22636.33 | 7.915%
2007-10-31 | 11908.105 | 93.128 | 19233 | 16005.5175 | 11788 | 18411.2 | 0 | 15.0344 | 12052.1085 | 12419.5501 | 3.049% | 24.3 | 19607.6114 | 21554.34 | 9.928%
2007-11-30 | 12350.431 | 133.6983 | 21814 | 17153.3764 | 12371 | 19847.5 | 60 | 3.4744 | 12534.9107 | 12719.7604 | 1.475% | -0.3 | 22401.7023 | 22807.03 | 1.809%
2007-12-31 | 13407.761 | 151.2253 | 22935 | 17932.1102 | 13146 | 20760.6 | 189 | -1.8172 | 13302.9248 | 13588.2725 | 2.145% | -3.4 | 23142.7472 | 24122.74 | 4.235%
2008-01-31 | 13609.986 | 192.7611 | 22782 | 18292.9919 | 13556 | 20970.1 | 196 | -1.6978 | 13996.4363 | 13978.7473 | 0.1264% | -8 | 23324.016 | 23839.9286 | 2.212%
2008-02-29 | 12896.823 | 182.6809 | 23054 | 18529.9167 | 14295 | 21007 | 204 | -4.3287 | 12775.3563 | 12968.8203 | 1.514% | -9.3 | 22662.4184 | 23331.2989 | 2.951%
2008-03-31 | 13003.771 | 195.6356 | 20990 | 17478.1868 | 13902 | 19568.2 | 31 | -0.62903 | 12635.3784 | 12970.3688 | 2.651% | -1.6 | 21209.0269 | 21883.6734 | 3.181%
2008-04-30 | 11520.396 | 175.7789 | 19512 | 16000.55 | 11571 | 18116.5 | 0 | 10.6456 | 11872.3822 | 11698.943 | 1.461% | 14.1 | 21077.4953 | 20048.0315 | 4.884%
2008-05-31 | 11407.14 | 182.8544 | 18650 | 15332.1774 | 11465 | 17575.7 | 0 | 12.972 | 11443.4889 | 11735.9553 | 2.556% | 26.9 | 20139.9842 | 20210.7676 | 0.3515%
2008-06-30 | 12189.13 | 160.4473 | 24195 | 16929.3472 | 11764 | 20433.6 | 101 | 20.7033 | 11982.089 | 12103.6774 | 1.015% | 33.1 | 23724.3431 | 23892.0192 | 0.7068%
2008-07-31 | 13155.66 | 136.1417 | 23787 | 17682.3387 | 12035 | 21319.6 | 176 | 22.9054 | 13123.8184 | 13161.835 | 0.2897% | 30 | 24987.592 | 25231.8939 | 0.9777%
2008-08-31 | 12548.525 | 152.1998 | 22707 | 16866.297 | 11986 | 19786.9 | 65 | 20.6624 | 12703.1866 | 12926.0971 | 1.755% | 26.1 | 23579.6573 | 24477.7753 | 3.809%
2008-09-30 | 11793.462 | 123.1236 | 22975 | 16379.8083 | 12061 | 18964.3 | 41 | 18.1289 | 11692.7164 | 11529.5318 | 1.396% | 30.3 | 21404.2678 | 22290.904 | 4.142%
2008-10-31 | 11634.137 | 132.3682 | 19366 | 15637.2809 | 11450 | 17924.4 | 0 | 10.0656 | 11691.8059 | 12044.3073 | 3.015% | 4.8 | 19511.6562 | 20907.5479 | 7.154%
2008-11-30 | 11828.99 | 145.2536 | 21279 | 16429.1528 | 11881 | 19036.5 | 24 | 3.7756 | 12095.7719 | 12262.6183 | 1.379% | 3.8 | 22489.0231 | 22119.6095 | 1.643%
2008-12-31 | 13087.707 | 170.3211 | 22541 | 17555.7755 | 11992 | 20509.2 | 121 | -2.4763 | 12907.8943 | 13264.4707 | 2.762% | -3.7 | 22164.6447 | 23154.6001 | 4.466%
2009-01-31 | 13730.291 | 169.634 | 22983 | 18454.6922 | 13872 | 21036.7 | 199.392 | -7.6344 | 13535.4467 | 13686.8304 | 1.118% | -11.3 | 22667.0788 | 23813.0998 | 5.056%
2009-02-28 | 11697.974 | 165.2381 | 22110 | 17407.6994 | 13312 | 19675.5 | 47.712 | -2.5405 | 11749.4678 | 12296.9476 | 4.66% | -13.1 | 21808.7203 | 23220.5185 | 6.474%
2009-03-31 | 12166.882 | 173.3939 | 21466 | 16353.336 | 11855 | 18906.8 | 20.832 | 2.143 | 12165.27 | 12746.6818 | 4.779% | -9.6 | 20868.6368 | 21914.9455 | 5.014%
2009-04-30 | 10746.635 | 180.7399 | 18744 | 14925.8819 | 10790 | 17106.2 | 0 | 8.7178 | 10901.2606 | 11354.7401 | 4.16% | -0.5 | 20344.9145 | 20074.7226 | 1.328%
2009-05-31 | 10504.201 | 197.5122 | 17560 | 14118.5497 | 10794 | 16433.1 | 0 | 14.7226 | 10536.0659 | 11416.2719 | 8.354% | 28.6 | 18785.4908 | 20357.5736 | 8.369%
2009-06-30 | 10884.323 | 147.3338 | 22540 | 15117.1153 | 10678 | 17997.5 | 34.56 | 18.4178 | 11161.8895 | 11587.9581 | 3.817% | 30.7 | 23485.0159 | 23172.7205 | 1.33%
2009-07-31 | 11315.411 | 141.1481 | 20011 | 15208.8858 | 10786 | 18132.3 | 0.744 | 20.3344 | 12091.706 | 12626.1861 | 4.42% | 27.4 | 22352.287 | 24350.6569 | 8.94%
2009-08-31 | 12225.812 | 143.9902 | 24380 | 16432.543 | 11040 | 20682.7 | 122.016 | 21.8935 | 12113.2789 | 12370.0057 | 2.119% | 31.2 | 24120.5582 | 23669.6928 | 1.869%
2009-09-30 | 10931.831 | 112.68 | 19731 | 15183.0986 | 10890 | 18072.2 | 0 | 17.9767 | 10838.0625 | 10978.4771 | 1.296% | 25.1 | 19977.6676 | 21055.1421 | 5.393%
2009-10-31 | 11181.875 | 146.4268 | 18420 | 15029.4019 | 11295 | 17250.6 | 0 | 9.3043 | 11214.1928 | 11567.95 | 3.155% | 4.1 | 19464.8512 | 20214.6873 | 3.852%
2009-11-30 | 11112.909 | 186.1543 | 19710 | 15434.5958 | 11333 | 17812.7 | 0 | 6.9422 | 11605.7866 | 11858.5268 | 2.178% | 3.7 | 21501.2294 | 21361.9788 | 0.6476%
2009-12-31 | 12688.573 | 197.3074 | 21831 | 17054.5336 | 12293 | 19724.4 | 55.8 | -1.4763 | 12677.5761 | 12693.1919 | 0.1232% | -6.7 | 21730.9099 | 21919.3561 | 0.8672%
2010-01-31 | 13145.438 | 206.3791 | 22045 | 17668.5995 | 13075 | 20120.3 | 84.072 | -4.2796 | 13227.8161 | 13097.6605 | 0.984% | -7.3 | 22297.8804 | 22717.3216 | 1.881%
2010-02-28 | 11751.752 | 175.9426 | 21367 | 17487.7262 | 13243 | 19687.6 | 45.696 | -2.644 | 11777.6488 | 11804.099 | 0.2246% | -3.6 | 22020.4448 | 22459.742 | 1.995%
2010-03-31 | 11686.054 | 96.5068 | 19393 | 15707.0618 | 11951 | 17744.6 | 0 | 5.5548 | 12010.9613 | 12430.8985 | 3.496% | 2 | 21346.0734 | 21309.448 | 0.1716%
2010-04-30 | 10474.752 | 174.4465 | 17398 | 14548.2667 | 10618 | 16556.5 | 0 | 11.8533 | 10898.0905 | 10857.612 | 0.3714% | 3.6 | 19258.6821 | 18770.6298 | 2.534%
2010-05-31 | 11368.031 | 153.2328 | 22904 | 15279.6116 | 10914 | 18075.7 | 43.896 | 17.0323 | 10951.2917 | 10814.7613 | 1.247% | 31.4 | 21295.2011 | 18843.502 | 11.51%
2010-06-30 | 11555.961 | 145.4928 | 21527 | 16049.9458 | 11506 | 19165.4 | 43.92 | 20.2422 | 11538.1526 | 11411.3572 | 1.099% | 28.3 | 22474.9206 | 22550.9548 | 0.3383%
2010-07-31 | 13307.242 | 172.6285 | 25075 | 17886.078 | 11400 | 22219.6 | 223.944 | 24.5226 | 12903.2908 | 12442.4622 | 3.571% | 33.3 | 24049.6327 | 23498.3733 | 2.292%
2010-08-31 | 12921.565 | 148.0201 | 24917 | 17367.6949 | 11813 | 21949.3 | 154.752 | 23.5247 | 12462.2289 | 12301.8326 | 1.287% | 32.9 | 24202.4847 | 22972.5225 | 5.082%
2010-09-30 | 11049.081 | 177.8492 | 24444 | 15345.9458 | 11124 | 17783.9 | 34.56 | 17.6822 | 10949.8132 | 11055.5026 | 0.9652% | 32.4 | 21702.065 | 21442.7835 | 1.195%
2010-10-31 | 10929.335 | 220.7635 | 17704 | 14689.9664 | 10816 | 16634.7 | 0 | 11.3839 | 10983.9114 | 11228.8238 | 2.23% | 11.4 | 19199.6083 | 18855.0679 | 1.795%
2010-11-30 | 11303.778 | 237.219 | 19970 | 15699.6917 | 11584 | 17896.8 | 0 | 5.0711 | 11457.171 | 11620.4239 | 1.425% | 4.2 | 20712.8718 | 20717.7815 | 0.0237%
2010-12-31 | 12694.155 | 264.8843 | 22114 | 17062.0363 | 12614 | 19769 | 55.8 | -3.1946 | 12581.1214 | 12708.2117 | 1.01% | -11.6 | 21966.6139 | 21580.6272 | 1.757%
2011-01-31 | 13301.687 | 252.0926 | 22733 | 17878.6116 | 11835 | 20361.5 | 113.832 | -6.0312 | 13237.9305 | 13343.9086 | 0.8006% | -9 | 22876.7298 | 22270.5192 | 2.65%
2011-02-28 | 11775.464 | 233.9528 | 21871 | 17523.0119 | 13358 | 19879.6 | 53.088 | -4.0107 | 11710.5829 | 11979.6008 | 2.297% | -7.7 | 21660.2043 | 21982.186 | 1.487%
2011-03-31 | 12352.443 | 266.6101 | 20667 | 16602.746 | 12736 | 18528.7 | 8.184 | 0.46559 | 12318.7834 | 12467.2468 | 1.205% | -4.3 | 21179.9192 | 20550.1632 | 2.973%
2011-04-30 | 10789.012 | 282.9928 | 17945 | 14984.7389 | 11276 | 17112.6 | 0 | 7.8011 | 11022.5512 | 10965.5571 | 0.5171% | 5.2 | 19571.3477 | 18195.8466 | 7.028%
2011-05-31 | 10781.74 | 261.12 | 20847 | 14491.586 | 10799 | 16552 | 8.928 | 15.1258 | 10594.0641 | 10934.6882 | 3.215% | 29.3 | 18742.8072 | 18515.1791 | 1.214%
2011-06-30 | 11238.277 | 218.9465 | 22765 | 15608.7181 | 10890 | 18748.6 | 18 | 20.4978 | 11253.6631 | 11593.1744 | 3.017% | 33.3 | 22294.084 | 23107.108 | 3.647%
2011-07-31 | 13298.189 | 200.5274 | 25450 | 17873.9099 | 11529 | 21827.5 | 190.464 | 25.7946 | 12809.1348 | 12517.8651 | 2.274% | 37.5 | 23631.2692 | 23538.8355 | 0.3911%
2011-08-31 | 12531.706 | 189.0822 | 22051 | 16843.6909 | 12205 | 20167.4 | 84.072 | 23.0892 | 12292.4814 | 12538.1515 | 1.999% | 31.3 | 22208.747 | 23196.6756 | 4.448%
2011-09-30 | 11144.546 | 169.0598 | 21552 | 15478.5361 | 11300 | 18071.9 | 23.76 | 18.6522 | 11031.1087 | 10964.8288 | 0.6008% | 28.3 | 21317.1824 | 21238.6927 | 0.3682%
2011-10-31 | 11012.737 | 211.1046 | 18234 | 14802.0659 | 11124 | 16971.2 | 0 | 11.6097 | 10973.2195 | 11154.7901 | 1.655% | 4.7 | 18168.0995 | 18437.0481 | 1.48%
2011-11-30 | 11116.536 | 267.3446 | 19673 | 15439.6333 | 11284 | 17789 | 0 | 7.6078 | 11452.4357 | 11622.5291 | 1.485% | 5.6 | 21347.2844 | 20747.3335 | 2.81%
2011-12-31 | 12121.895 | 278.8385 | 20204 | 16292.8696 | 11974 | 18901.5 | 4.464 | 1.3043 | 12314.3757 | 12864.6619 | 4.469% | -1.3 | 20772.1165 | 21942.4375 | 5.634%
2012-01-31 | 12715.234 | 290.1431 | 21847 | 17090.3683 | 12439 | 19422.5 | 31.248 | -0.83763 | 12932.2873 | 13280.0235 | 2.689% | -14.3 | 22084.7322 | 22160.0997 | 0.3413%
2012-02-29 | 11610.18 | 259.7219 | 19956 | 16681.2931 | 13228 | 18709 | 0 | 0.41839 | 11380.2015 | 12202.5791 | 7.226% | 1.3 | 20756.8677 | 21813.8691 | 5.092%
2012-03-31 | 11487.527 | 304.436 | 20332 | 15440.2245 | 11250 | 17580.1 | 2.232 | 7.8925 | 11726.1779 | 12264.8125 | 4.593% | -2.8 | 20595.0545 | 20708.9072 | 0.5528%
2012-04-30 | 10641.371 | 287.2476 | 17874 | 14779.6819 | 11248 | 16598.3 | 0 | 8.6278 | 10883.4994 | 10866.5786 | 0.1555% | 4.1 | 19830.1533 | 18745.092 | 5.472%
2012-05-31 | 11136.995 | 273.7978 | 21106 | 14969.0793 | 10998 | 17581 | 13.392 | 18.0011 | 10838.5019 | 10943.6824 | 0.9704% | 28.6 | 19736.9901 | 19038.2309 | 3.54%
2012-06-30 | 11800.326 | 280.2738 | 24107 | 16389.3417 | 11017 | 20405.4 | 93.6 | 21.7878 | 11511.081 | 11398.2442 | 0.9802% | 34.2 | 22832.4909 | 22569.1521 | 1.153%
2012-07-31 | 13456.845 | 224.7422 | 24636 | 18087.1573 | 12425 | 22075.1 | 212.04 | 25.5516 | 13057.6199 | 12319.3311 | 5.654% | 36.2 | 23630.2664 | 23298.1422 | 1.406%
2012-08-31 | 12632.817 | 218.4517 | 23188 | 16979.5927 | 11676 | 20667.4 | 109.368 | 22.9667 | 12373.2613 | 12419.0386 | 0.37% | 30.1 | 22726.501 | 22956.5741 | 1.012%
2012-09-30 | 11040.767 | 215.7734 | 21183 | 15334.3986 | 11012 | 18710.3 | 23.04 | 17.5778 | 10900.4102 | 10811.3017 | 0.8175% | 27.1 | 20370.1157 | 20506.0631 | 0.6674%
2012-10-31 | 11141.991 | 278.1392 | 18829 | 14975.7944 | 11436 | 16974.5 | 0 | 11.0935 | 11149.8822 | 11199.8353 | 0.448% | 4.3 | 18684.153 | 18345.9037 | 1.81%
2012-11-30 | 11487.169 | 271.2616 | 20144 | 15954.4014 | 11824 | 18349.8 | 2.16 | 4.2867 | 11663.449 | 11629.6439 | 0.2898% | -3.7 | 20258.2258 | 20571.5606 | 1.547%
2012-12-29 | 12156.557 | 285.1456 | 20382 | 17466.3175 | 12670 | 18764.9 | 9.672 | 1.4419 | 12306.8289 | 12612.0073 | 2.48% | -1 | 20910.8981 | 21693.287 | 3.742%
2013-01-31 | 12889.507 | 301.2556 | 22610 | 16274.6301 | 12270 | 20123.6 | 83.328 | -1.7989 | 13061.0693 | 13314.3055 | 1.939% | -11.6 | 22610 | 22013.997 | 2.636%
2013-02-28 | 11742.246 | 289.301 | 21426 | 17473.5804 | 13638 | 19632.9 | 38.976 | -3.6452 | 11668.8474 | 11819.7381 | 1.293% | -5.8 | 21333.0082 | 21773.6201 | 2.065%
2013-03-31 | 11958.319 | 350.9198 | 19825 | 16073.0094 | 11963 | 18101.1 | 0 | 0.98602 | 11869.9986 | 12283.0437 | 3.48% | -1.8 | 20784.4526 | 20634.9497 | 0.7193%
2013-04-30 | 10944.906 | 354.007 | 18854 | 15201.2583 | 11209 | 17185.7 | 0 | 6.9567 | 11090.2932 | 11018.1303 | 0.6507% | 2.3 | 19284.8182 | 18492.3312 | 4.109%
2013-05-31 | 10785.424 | 362.6957 | 20488 | 14496.5376 | 10765 | 16610.7 | 4.464 | 16.5247 | 10533.5712 | 10932.3105 | 3.785% | 29.9 | 18341.9804 | 19100.9692 | 4.138%
2013-06-30 | 11174.679 | 290.1226 | 22662 | 15520.3875 | 10816 | 18354.4 | 43.2 | 19.9844 | 11283.4325 | 11406.4319 | 1.09% | 31.6 | 22719.4401 | 22499.2459 | 0.9692%
2013-07-31 | 12722.707 | 357.4735 | 24927 | 17100.4126 | 11506 | 21288 | 122.76 | 23.2097 | 12736.3503 | 12479.5529 | 2.016% | 34.3 | 24352.1456 | 23212.9348 | 4.678%
2013-08-31 | 12100.351 | 398.7601 | 22833 | 16263.9126 | 11139 | 20243.4 | 84.816 | 22.1183 | 12084.9413 | 12227.7513 | 1.182% | 28.2 | 23255.371 | 22359.7987 | 3.851%
2013-09-30 | 10837.167 | 336.0942 | 22682 | 15051.6208 | 11003 | 17399.6 | 20.88 | 17.26 | 10767.0057 | 11015.3041 | 2.306% | 33.9 | 20422.3176 | 20513.3592 | 0.4458%
2013-10-31 | 11135.689 | 352.2154 | 18445 | 14967.3239 | 11018 | 17040.1 | 0 | 11.7849 | 11114.0467 | 11279.1846 | 1.486% | 6.6 | 18981.007 | 18388.3002 | 3.123%
2013-11-30 | 11640.948 | 422.4146 | 20615 | 16167.9833 | 11571 | 18660.2 | 8.64 | 2.53 | 11709.7788 | 11686.9287 | 0.1951% | -3.3 | 20034.8189 | 20326.4941 | 1.456%
2013-12-31 | 12702.006 | 329.2647 | 21964 | 17072.5887 | 12626 | 19937.2 | 66.216 | -3.5086 | 12528.9266 | 12699.9803 | 1.365% | -8.3 | 21184.5386 | 21395.0558 | 0.9937%
2014-01-31 | 13613.596 | 400.6012 | 22774 | 18297.8441 | 13381 | 20167.4 | 87.048 | -7.8516 | 13409.7767 | 13356.427 | 0.3978% | -17.4 | 22043.8439 | 22319.8106 | 1.252%
2014-02-28 | 12067.276 | 336.7994 | 21905 | 17957.256 | 13981 | 20340.8 | 109.536 | -7.1464 | 11812.9441 | 11748.3799 | 0.5466% | -12.2 | 21218.2216 | 20964.0592 | 1.198%
2014-03-31 | 12672.074 | 436.3629 | 21656 | 17032.3575 | 13296 | 18156.7 | 8.928 | -2.8688 | 12242.1563 | 12054.5719 | 1.532% | -12.1 | 20728.4579 | 19906 | 3.968%
2014-04-30 | 10836.804 | 477.6859 | 18557 | 15051.1167 | 11944 | 16454 | 0 | 7.3289 | 11038.5265 | 10731.1367 | 2.785% | -0.9 | 19249.9632 | 17649 | 8.317%
2014-05-31 | 10642.583 | 485.0087 | 18844 | 14304.547 | 10719 | 16623.2 | 0 | 15.3871 | 10546.4252 | 10790.2174 | 2.312% | 29.4 | 18750.4605 | 18964 | 1.139%
2014-06-30 | 11228.548 | 467.8886 | 20807 | 15595.2056 | 10723 | 17232.9 | 0 | 21.0889 | 11140.5499 | 11346.2756 | 1.847% | 30.3 | 20705.1957 | 22469.55 | 8.521%
2014-07-31 | 11717.444 | 448.354 | 21300 | 15749.2527 | 11321 | 19790.1 | 63.984 | 21.471 | 12324.9268 | 12360.0815 | 0.2852% | 29.8 | 22294.8035 | 22948.69 | 2.933%
2014-08-31 | 11718.183 | 386.2556 | 21363 | 15750.246 | 11362 | 19044 | 47.616 | 21.3172 | 11819.2371 | 11992.5131 | 1.466% | 31.3 | 21644.3547 | 21403.44 | 1.113%
2014-09-30 | 10836.546 | 423.8321 | 21123 | 15050.7583 | 11112 | 19853.4 | 61.2 | 17.9967 | 10671.4853 | 10579.5258 | 0.8617% | 31.4 | 19449.0766 | 19023.2704 | 2.189%
2014-10-31 | 10819.853 | 438.5968 | 17784 | 14542.8132 | 10769 | 16432.6 | 0 | 11.6849 | 10814.1957 | 11126.7565 | 2.89% | 9.1 | 18447.2196 | 18638.7361 | 1.038%
2014-11-30 | 11487.634 | 407.9288 | 20102 | 15955.0472 | 12082 | 17109.3 | 0 | 2.2756 | 11410.1121 | 11497.4835 | 0.7657% | 0.8 | 19923.2587 | 20302.34 | 1.903%
2014-12-31 | 12131.525 | 425.9567 | 20938 | 16305.8132 | 11398 | 17611.5 | 0 | 0.52366 | 12256.0958 | 12769.4956 | 4.189% | -1.2 | 21582.6701 | 21237.74 | 1.598%
2015-01-31 | 13119.979 | 462.7948 | 21814 | 17634.3804 | 13344 | 19048.7 | 26.784 | -6.6624 | 12937.1182 | 13068.9431 | 1.019% | -15.7 | 21503.4489 | 22293.59 | 3.674%
2015-02-28 | 12302.278 | 399.7277 | 21494 | 18306.9613 | 14588 | 18778.7 | 5.376 | -11.4369 | 11740.7311 | 11528.5197 | 1.807% | -15.8 | 19709.6284 | 21016.81 | 6.632%
2015-03-31 | 12044.976 | 495.7729 | 20827 | 16189.4839 | 12675 | 18117.4 | 5.208 | -0.59892 | 11748.227 | 11856.8161 | 0.9243% | -9.6 | 20109.8817 | 19840.93 | 1.337%
2015-04-30 | 10404.962 | 653.4141 | 18462 | 14451.3361 | 10975 | 16390.3 | 0 | 8.6044 | 10624.618 | 10542.0267 | 0.7774% | 2.4 | 19362.8308 | 18121.2 | 6.412%
2015-05-31 | 10547.132 | 529.8747 | 19158 | 14176.2527 | 10657 | 16587.6 | 0 | 17.772 | 10231.5964 | 10635.9243 | 3.952% | 28.8 | 17881.7583 | 19370.33 | 8.325%
2015-06-30 | 10624.316 | 577.9038 | 19339 | 14755.9944 | 10804 | 17220.7 | 0 | 18.9767 | 10908.724 | 11410.2692 | 4.598% | 25.5 | 20554.6293 | 22276.64 | 8.378%
2015-07-31 | 12105.066 | 521.3404 | 22516 | 16270.25 | 11010 | 19756.8 | 61.752 | 23.0602 | 12273.6405 | 12174.2184 | 0.81% | 32.5 | 22638.5319 | 22888.49 | 1.104%
2015-08-31 | 11797.099 | 472.2223 | 22383 | 15856.3159 | 11414 | 19007.1 | 46.872 | 21.8011 | 11782.7212 | 11821.2763 | 0.3272% | 32.1 | 22383 | 21463.69 | 4.107%
2015-09-30 | 11361.901 | 503.8076 | 22063 | 15780.4181 | 10927 | 19812.8 | 61.92 | 20.7778 | 10718.9879 | 10512.648 | 1.925% | 32.6 | 19299.6325 | 18485 | 4.221%
2015-10-31 | 10687.264 | 497.6939 | 17667 | 14364.6022 | 10539 | 16384.2 | 0 | 10.829 | 10731.7474 | 11150.1256 | 3.899% | 13.1 | 18444.3181 | 18339 | 0.571%
2015-11-30 | 10681.592 | 477.3161 | 19239 | 14835.5444 | 11338 | 17157.4 | 0 | 7.5422 | 10867.5486 | 11595.0899 | 6.695% | 1.9 | 19631.9089 | 20306 | 3.434%
2015-12-31 | 11313.857 | 435.4307 | 19161 | 15206.797 | 10811 | 17642 | 0 | 4.8495 | 11784.7123 | 12611.2501 | 7.014% | 6.8 | 20418.0801 | 21160.04 | 3.634%
2016-01-31 | 12384.867 | 471.7938 | 20836 | 16646.3266 | 12116 | 19066 | 24.552 | -2.6 | 12523.599 | 12982.1466 | 3.661% | -11.8 | 21249.7402 | 22360.24 | 5.226%
2016-02-29 | 11471.763 | 474.1135 | 20766 | 16482.4181 | 12533 | 18707.5 | 4.872 | -1.2391 | 11502.97 | 11806.8997 | 2.642% | -10 | 20194.6163 | 20985.25 | 3.915%
2016-03-31 | 11302.963 | 530.5494 | 20063 | 15192.1546 | 11717 | 17387.3 | 0.744 | 3.6194 | 11445.7227 | 11758.7447 | 2.735% | -7.9 | 20324.618 | 20075.21 | 1.227%
2016-04-30 | 10409.92 | 661.3944 | 17821 | 14458.2222 | 11286 | 16583.2 | 0 | 5.97 | 10578.9099 | 10309.6515 | 2.545% | 0.6 | 18912.1728 | 17405.08 | 7.969%
2016-05-31 | 10470.808 | 665.3817 | 19885 | 14073.6667 | 10461 | 17171.1 | 0 | 15.9602 | 10115.8584 | 10530.0143 | 4.094% | 27.2 | 19707.6447 | 19235.65 | 2.395%
2016-06-30 | 11101.521 | 613.5199 | 21692 | 15418.7792 | 10596 | 18447.4 | 24.48 | 21.52 | 11141.3797 | 11378.6081 | 2.129% | 34 | 21568.912 | 22315.7305 | 3.462%
2016-07-31 | 12497.616 | 548.7117 | 22659 | 16797.871 | 10985 | 20860.1 | 143.592 | 25.0882 | 12345.0421 | 11896.1402 | 3.636% | 35 | 22288.7672 | 22599.9414 | 1.396%
2016-08-31 | 13113.359 | 534.2805 | 23100 | 17625.4825 | 12287 | 21278.8 | 183.768 | 25.4183 | 12295.9028 | 11771.834 | 4.262% | 34.8 | 22375.997 | 21440.3166 | 4.182%
2016-09-30 | 11072.26 | 523.2114 | 23213 | 15378.1389 | 10855 | 18825.3 | 42.48 | 20.6733 | 10659.2295 | 10401.8861 | 2.414% | 34.5 | 19712.7154 | 18289 | 7.222%
2016-10-31 | 10518.677 | 417.6305 | 18189 | 14138.0067 | 10663 | 16351 | 0 | 12.6344 | 10453.1463 | 10947.5325 | 4.73% | 5.2 | 18394.9922 | 18079 | 1.718%
2016-11-30 | 10697.637 | 418.8378 | 19369 | 14857.8292 | 11211 | 17154.5 | 0 | 7.5167 | 10913.6011 | 11524.026 | 5.593% | 0.2 | 19544.7667 | 20296 | 3.844%
2016-12-31 | 11978.041 | 435.9647 | 20688 | 16099.5175 | 11684 | 18666.1 | 10.416 | -1.129 | 11950.5536 | 12430.7427 | 4.018% | -8.1 | 20286.7849 | 20888 | 2.964%
2017-01-31 | 12108.005 | 463.9501 | 20372 | 16274.2003 | 12246 | 18425.1 | 2.232 | -1.1495 | 12369.7298 | 12818.8508 | 3.631% | -3.3 | 20965.9674 | 21913.73 | 4.52%
2017-02-28 | 10607.563 | 490.9519 | 19838 | 15785.064 | 11867 | 18064.6 | 0 | 0.47143 | 10787.4931 | 11294.713 | 4.702% | -1.1 | 20379.4501 | 20966.2287 | 2.879%
2017-03-31 | 11591.031 | 560.1987 | 19174 | 15579.3427 | 12158 | 17608.2 | 0 | 0.46667 | 11413.3465 | 11824.0632 | 3.599% | -8.1 | 18692.3503 | 20137.3 | 7.73%
2017-04-30 | 9788.616 | 594.6314 | 17349 | 13595.3 | 10167 | 15576.2 | 0 | 10.6278 | 10105.7565 | 10366.7129 | 2.582% | 7.3 | 18482.7844 | 17969.79 | 2.776%
2017-05-31 | 10153.182 | 619.1188 | 17738 | 13646.75 | 10249 | 15622.5 | 0 | 13.4538 | 10012.8427 | 10576.9018 | 5.633% | 29.6 | 18260.3078 | 19193.19 | 5.109%
2017-06-30 | 10657.08 | 578.0093 | 21168 | 14801.5 | 10518 | 17663.4 | 7.2 | 20.6422 | 10682.999 | 11159.3312 | 4.459% | 32.4 | 21144.8187 | 22454.87 | 6.196%
2017-07-31 | 11587.63 | 582.9578 | 20627 | 15574.7715 | 10806 | 19028.7 | 17.112 | 22.8473 | 11851.6211 | 11984.7355 | 1.123% | 31.5 | 22152.8524 | 22492.73 | 1.534%
2017-08-31 | 11350.012 | 559.5215 | 20158 | 15255.3925 | 10829 | 18577.9 | 5.208 | 21.228 | 11513.597 | 12105.5471 | 5.141% | 30 | 21323.3584 | 22376.43 | 4.939%
2017-09-30 | 10679.393 | 484.1858 | 21786 | 14832.4903 | 10487 | 18795.6 | 25.2 | 19.9789 | 10155.927 | 10494.2948 | 3.332% | 31.3 | 17821.4732 | 19490.21 | 9.364%
2017-10-31 | 10339.329 | 532.8493 | 17418 | 13896.9476 | 10534 | 15857.7 | 0 | 14.4925 | 10260.3837 | 10942.7953 | 6.651% | 26.5 | 17407.7858 | 18030.62 | 3.578%
2017-11-30 | 10955.909 | 497.8786 | 19115 | 15216.5403 | 11199 | 17381.1 | 0 | 4.6056 | 10946.7668 | 11371.7451 | 3.882% | 3 | 19195.4397 | 20230.97 | 5.395%
2017-12-31 | 12338.893 | 402.8257 | 20306 | 16584.5336 | 12093 | 18875.6 | 5.952 | -4.1731 | 12096.0133 | 12303.6865 | 1.717% | -4.1 | 21439.6493 | 20901.44 | 2.51%
2018-01-31 | 12700.826 | 533.4365 | 20906 | 17071.0027 | 12453 | 19337.8 | 14.88 | -4.6452 | 12679.8037 | 12685.9178 | 0.04822% | -15.2 | 20177.5339 | 21618.93 | 7.144%
2018-02-28 | 10951.065 | 496.4596 | 20076 | 16296.2277 | 12716 | 18608.6 | 1.344 | -0.70714 | 11081.1365 | 11074.1738 | 0.06283% | -8.2 | 20042.2165 | 20242.21 | 0.9979%
2018-03-31 | 11372.42 | 596.6609 | 18462 | 15285.5108 | 12158 | 17159.9 | 0 | 0.8828 | 11267.3415 | 11423.555 | 1.386% | 0.2 | 19330.8728 | 19551.97 | 1.144%
2018-04-30 | 10578.368 | 586.9588 | 18011 | 14692.1778 | 11497 | 16647.2 | 0 | 4.37 | 10586.2978 | 10157.8502 | 4.047% | 2.4 | 18107.9593 | 17669.81 | 2.42%
2018-05-31 | 10421.469 | 664.6636 | 20473 | 14007.3508 | 10541 | 16770.4 | 10.416 | 18.4376 | 10081.137 | 10289.6502 | 2.068% | 30.7 | 19262.1307 | 18817.47 | 2.308%
2018-06-30 | 10923.446 | 602.8769 | 21369 | 15171.4528 | 10698 | 18437.3 | 37.44 | 20.7522 | 10980.4534 | 10863.4062 | 1.066% | 30.2 | 20626.9619 | 21890.0001 | 6.123%
2018-07-31 | 12685.981 | 517.157 | 22909 | 17051.0497 | 11413 | 20705.3 | 140.616 | 24.6247 | 12483.776 | 11652.7714 | 6.657% | 33.2 | 22409.0792 | 22076.0001 | 1.486%
2018-08-31 | 12688.795 | 531.4383 | 21990 | 17054.832 | 11966 | 20622.8 | 120.528 | 24.1731 | 12040.5393 | 11685.5744 | 2.948% | 31.7 | 21385.6483 | 21946.0001 | 2.62%
2018-09-30 | 11147.31 | 480.938 | 23240 | 15482.375 | 10701 | 19596.5 | 56.88 | 19.9011 | 10579.1906 | 10189.9802 | 3.679% | 33.9 | 19505.5646 | 19019 | 2.494%
2018-10-31 | 10717.348 | 485.4689 | 18205 | 14405.0376 | 10847 | 16419.1 | 0 | 9.9258 | 10526.7735 | 10750.0648 | 2.121% | 26.1 | 17751.4152 | 17788 | 0.2061%
2018-11-30 | 11360.321 | 423.7495 | 20152 | 15778.2236 | 11765 | 17927.3 | 0.72 | 2.12 | 11184.9393 | 11170.7506 | 0.1269% | -6.6 | 19266.3918 | 19828 | 2.915%
2018-12-31 | 11938.614 | 407.6369 | 19891 | 16046.5242 | 12284 | 18215.4 | 0 | 0.47097 | 12019.553 | 12007.3958 | 0.1011% | -1.4 | 20375.1864 | 20503 | 0.6273%
2019-01-31 | 12777.216 | 463.966 | 21525 | 17173.6774 | 12291 | 19588.2 | 41.664 | -5.9118 | 12688.8389 | 12973.2132 | 2.241% | -11.8 | 21058.2817 | 21506 | 2.126%
2019-02-28 | 11291.744 | 455.9299 | 20500 | 16803.1905 | 13041 | 19051 | 8.736 | -3.4405 | 11212.4836 | 11162.2057 | 0.4484% | -10.1 | 20420.3692 | 20008 | 2.019%
2019-03-31 | 11658.678 | 588.34 | 20263 | 15670.2661 | 12210 | 17519 | 2.232 | -0.036022 | 11458.0531 | 11522.1982 | 0.5598% | -9 | 19573.6921 | 19457 | 0.5962%
2019-04-30 | 10264.505 | 597.1531 | 17645 | 14256.2569 | 11079 | 16133.5 | 0 | 7.3189 | 10432.2785 | 10252.9314 | 1.719% | 2.8 | 18796.3299 | 17548 | 6.641%
2019-05-31 | 10219.56 | 574.423 | 16784 | 13735.9677 | 10328 | 15586.7 | 0 | 13.0312 | 10218.7126 | 10412.0446 | 1.892% | 8.2 | 17977.0308 | 18663 | 3.816%
2019-06-30 | 10365.619 | 600.8034 | 20248 | 14396.6931 | 10564 | 17336.5 | 2.88 | 19.5056 | 10608.5215 | 10939.3571 | 3.119% | 28.9 | 21239.1838 | 21623 | 1.807%
2019-07-31 | 12792.766 | 606.5726 | 21791 | 17194.578 | 11565 | 20646.4 | 145.824 | 24.6344 | 12446.1887 | 11763.9974 | 5.481% | 31.4 | 21120.5208 | 22061 | 4.453%
2019-08-31 | 11825.052 | 555.2842 | 21354 | 15893.8871 | 11280 | 19305.9 | 40.92 | 22.4419 | 11798.5843 | 11598.2109 | 1.698% | 30.2 | 22490.4547 | 21200 | 5.738%
2019-09-30 | 10318.533 | 482.8673 | 19717 | 14331.2958 | 10477 | 16722 | 0 | 18.74 | 10167.6302 | 10564.4926 | 3.903% | 28.6 | 18958.9757 | 19469.84 | 2.695%
2019-10-31 | 10351.05 | 505.1513 | 18329 | 13912.7016 | 10739 | 15950.2 | 0 | 11.7903 | 10446.8836 | 10788.0047 | 3.265% | 31.2 | 18814.592 | 17559 | 6.674%
2019-11-30 | 11255.325 | 452.3729 | 19625 | 15632.3958 | 11711 | 17850 | 0 | 1.6178 | 11094.2081 | 11194.6524 | 0.9054% | -4.1 | 19001.8635 | 19597 | 3.132%
2019-12-31 | 11997.095 | 447.2177 | 20974 | 16125.1277 | 11787 | 18657.6 | 11.16 | -0.23333 | 12094.1802 | 12086.6766 | 0.06204% | -7.8 | 20974 | 20307 | 3.18%
2020-01-31 | 12178.575 | 426.7563 | 19928 | 16369.0524 | 12353 | 18557.8 | 0 | -0.75161 | 12460.9405 | 12859.4588 | 3.198% | -8.5 | 21137.8728 | 21185.0004 | 0.223%
2020-02-29 | 11239.82 | 490.212 | 19630 | 16149.1667 | 12683 | 18163 | 0 | -1.9977 | 11253.1814 | 11586.6754 | 2.964% | -10.4 | 19776.0281 | 19917.0004 | 0.7128%
2020-03-31 | 10989.389 | 585.8152 | 18183 | 14770.6841 | 11120 | 16702.6 | 0 | 4.1634 | 11058.3098 | 11522.322 | 4.196% | 5.4 | 19680.948 | 19377.0004 | 1.544%
2020-04-30 | 9282.854 | 642.7441 | 15350 | 12892.8528 | 10379 | 14231.4 | 0 | 7.01 | 9383.3554 | 10229.1483 | 9.014% | 4.4 | 16515.7848 | 17302.0004 | 4.76%
2020-05-31 | 9642.117 | 671.1773 | 20649 | 12959.8347 | 9831 | 15246.8 | 3.72 | 13.3968 | 9306.4436 | 9434.378 | 1.375% | 30.6 | 18761.2836 | 17426 | 7.117%
2020-06-30 | 10800.015 | 634.4604 | 21292 | 15000.0208 | 10340 | 18996.7 | 20.88 | 22.0667 | 10596.6512 | 10274.389 | 3.041% | 31.2 | 20741.8718 | 20034 | 3.413%
2020-07-31 | 13202.706 | 617.8423 | 24446 | 17745.5726 | 12154 | 21827.4 | 188.232 | 26.2043 | 12529.7172 | 11731.6936 | 6.369% | 34 | 24057.7367 | 22364.4404 | 7.038%
2020-08-31 | 12081.08 | 578.6123 | 23823 | 16238.0108 | 11221 | 20133.6 | 82.584 | 23.2366 | 12338.1938 | 11441.5908 | 7.267% | 31.9 | 25317.7535 | 21631.4406 | 14.56%
2020-09-30 | 10114.374 | 551.2872 | 20225 | 14047.7417 | 10834 | 16340.6 | 1.44 | 17.9378 | 10011.2355 | 10356.1124 | 3.445% | 27.4 | 19254.2062 | 20312.4408 | 5.496%
2020-10-31 | 10339.39 | 528.3272 | 17679 | 13897.0296 | 10645 | 16042.5 | 0 | 10.371 | 10349.5982 | 10040.7873 | 2.984% | 7 | 17587.3164 | 17039.9727 | 3.112%
2020-11-30 | 10529.032 | 524.2466 | 19147 | 14623.6556 | 10808 | 17008.6 | 0 | 7.763 | 10693.8532 | 10531.6058 | 1.517% | 0.1 | 19416.1975 | 18891.9134 | 2.7%
2020-12-31 | 11811.675 | 485.452 | 20738 | 15875.9073 | 12389 | 18200.4 | 3.72 | 0.31505 | 11932.8039 | 11815.0887 | 0.9865% | -6.8 | 20975.3455 | 19805.1651 | 5.579%
2021-01-31 | 12105.158 | 409.653 | 20150 | 16270.3737 | 12798 | 18344.9 | 1.488 | -1.9591 | 12307.6071 | 12539.1611 | 1.881% | -8.4 | 20951.6431 | 21176.0005 | 1.071%
2021-02-28 | 11233.123 | 456.7989 | 20318 | 16715.9568 | 13200 | 18799.9 | 3.36 | -4.306 | 11144.3783 | 11073.4765 | 0.6362% | -6.9 | 20175.4672 | 20760.0005 | 2.897%
2021-03-31 | 11101.706 | 690.6151 | 19344 | 14921.6478 | 11659 | 16933 | 0 | 4.6086 | 11249.5616 | 11497.7125 | 2.206% | -0.8 | 19868.2566 | 19384.0005 | 2.437%
2021-04-30 | 9781.57 | 596.9459 | 16644 | 13585.5139 | 10498 | 15264.1 | 0 | 8.98 | 10097.7166 | 10244.8035 | 1.457% | 4.8 | 17618.7846 | 17070.0009 | 3.115%
2021-05-31 | 10086.333 | 622.8177 | 19443 | 13556.8992 | 10782 | 15777.1 | 0 | 15.1602 | 9986.9371 | 10152.0681 | 1.653% | 31.6 | 18021.5172 | 18055.3342 | 0.1876%
2021-06-30 | 11262.474 | 611.5113 | 22258 | 15642.325 | 11304 | 19635.9 | 59.76 | 22.9889 | 10840.8856 | 10747.5852 | 0.8606% | 31.6 | 21528.4908 | 22162.0009 | 2.943%
2021-07-31 | 11636.443 | 611.3859 | 21655 | 15640.3804 | 11108 | 19487.8 | 49.848 | 22.2151 | 11970.9832 | 11806.5074 | 1.374% | 31.7 | 22251.4821 | 22413.0005 | 0.7259%
2021-08-31 | 12856.511 | 581.7597 | 22986 | 17280.2567 | 10853 | 21313.1 | 188.976 | 24.7634 | 12072.0791 | 11706.2663 | 3.03% | 33.1 | 21854.4728 | 22235.0005 | 1.741%
2021-09-30 | 10389.017 | 544.7746 | 18769 | 14429.1903 | 10426 | 16782 | 0 | 18.74 | 10401.3058 | 10472.6839 | 0.6862% | 26 | 18979.8917 | 21212.0005 | 11.76%
2021-10-31 | 10516.14 | 524.146 | 17312 | 14134.5968 | 10779 | 16116.7 | 0 | 14.3432 | 10429.4829 | 10365.0376 | 0.6179% | 21.95 | 17606.8602 | 17270.7147 | 1.909%
2021-11-30 | 10956.602 | 515.9736 | 19644 | 15217.5028 | 11605 | 17496.4 | 0 | 4.74 | 11017.3258 | 10886.7659 | 1.185% | 0.15 | 19684.7166 | 19227.38 | 2.323%
2021-12-31 | 11969.602 | 476.8031 | 20455 | 16088.1747 | 12517 | 18342.8 | 2.976 | 2.0215 | 12185.9418 | 11984.4925 | 1.653% | -2.3 | 21331.5579 | 20088.8968 | 5.825%
2022-01-31 | 13085.388 | 489.3876 | 21349 | 17587.8871 | 12491 | 19796.7 | 55.056 | -7.0054 | 12928.5532 | 12536.9576 | 3.029% | -12.1 | 21334.1018 | 20983.6671 | 1.643%
2022-02-28 | 11487.734 | 515.5153 | 20918 | 17094.8423 | 13761 | 19171.3 | 14.112 | -3.5488 | 11400.5165 | 11208.712 | 1.682% | -9.8 | 20782.3287 | 20446.0004 | 1.618%
2022-03-31 | 11816.835 | 611.8729 | 19763 | 15882.8427 | 12285 | 17932.4 | 0 | 1.929 | 11793.6956 | 11617.5125 | 1.494% | -5.2 | 19941.2707 | 19401.3338 | 2.708%
2022-04-30 | 10265.047 | 646.6282 | 17256 | 14257.0097 | 11430 | 16016.1 | 0 | 7.5244 | 10311.1592 | 10239.112 | 0.6987% | 6.6 | 17752.3935 | 17251.0005 | 2.824%
2022-05-31 | 10469.914 | 677.424 | 21292 | 14072.4651 | 10485 | 16297 | 8.928 | 17.0151 | 10137.6947 | 10372.2878 | 2.314% | 32.2 | 20136.0014 | 18269.0005 | 9.272%
2022-06-30 | 10929.858 | 654.792 | 21954 | 15180.3583 | 10627 | 18994.9 | 43.2 | 21.0744 | 11002.2267 | 10967.9836 | 0.3112% | 34.6 | 22101.7092 | 22161.0005 | 0.2683%
2022-07-31 | 12343.623 | 588.0453 | 22607 | 16590.8911 | 11449 | 20039.3 | 77.376 | 24.086 | 12411.016 | 11893.9057 | 4.167% | 34.2 | 22484.9516 | 22542.0005 | 0.2537%
2022-08-31 | 12624.254 | 603.8346 | 21871 | 16968.0833 | 11830 | 20450 | 99.696 | 23.6763 | 11998.9314 | 12028.3221 | 0.2449% | 30.5 | 23477.9346 | 22430.0005 | 4.463%
2022-09-30 | 10814.096 | 493.97 | 20350 | 15019.5778 | 11082 | 17965.3 | 2.88 | 18.7344 | 10678.4907 | 10551.0851 | 1.193% | 29.2 | 20446.2276 | 21489.0005 | 5.1%
2022-10-31 | 10384.167 | 567.3429 | 17294 | 13957.2137 | 10820 | 15961.1 | 0 | 11.6301 | 10447.0825 | 10603.0084 | 1.493% | 8.9 | 17724.6236 | 17559.0005 | 0.9344%
2022-11-30 | 11044.181 | 489.5672 | 19441 | 15339.1403 | 10931 | 17734 | 0 | 6.0933 | 11128.3255 | 11151.0711 | 0.2044% | -3.6 | 19389.6575 | 19812.0005 | 2.178%
2022-12-31 | 12273.23 | 460.9624 | 20173 | 16496.2769 | 12417 | 18629 | 2.232 | 0.16129 | 12412.7534 | 12191.9609 | 1.779% | 0.8 | 20584.5241 | 20241.0005 | 1.669%
2023-01-31 | 12519.712 | 376.932 | 20486 | 16827.5699 | 12603 | 18821.9 | 4.464 | 8.3011 | 13052.768 | 12663.6554 | 2.981% | 8 | 21435.1399 | 21170.3338 | 1.235%
2023-02-28 | 11225.17 | 505.7145 | 21388 | 16704.122 | 12990 | 19014 | 10.08 | -0.72976 | 11325.8235 | 11375.0622 | 0.4347% | -15.5 | 20433.0112 | 20892.3338 | 2.248%
2023-03-31 | 11846.269 | 623.4296 | 18811 | 15922.4046 | 12940 | 17656 | 0 | 1.6882 | 11814.7494 | 11846.6528 | 0.27% | -0.1 | 19000.8853 | 19701.0485 | 3.685%
2023-04-30 | 10271.638 | 587.4763 | 17547 | 14266.1639 | 11117 | 15920.1 | 0 | 10.0774 | 10374.8437 | 10349.2653 | 0.2465% | 5.4 | 19103.3719 | 17785.9996 | 6.896%
2023-05-31 | 10356.75 | 675.0171 | 20787 | 13920.3629 | 10859 | 15783.1 | 5.208 | 15.1742 | 10473.6584 | 10418.8057 | 0.5237% | 29.9 | 18001.5877 | 18869.9996 | 4.824%
2023-06-30 | 11119.814 | 599.2129 | 21463 | 15444.1861 | 11438 | 18666.1 | 23.04 | 20.5444 | 11230.6805 | 10652.496 | 5.148% | 31.6 | 22417.4764 | 21884.9996 | 2.375%
2023-07-31 | 12507.785 | 591.493 | 22686 | 16811.539 | 11987 | 20318.4 | 102.672 | 23.3629 | 12455.0186 | 11858.9002 | 4.786% | 30.95 | 23368.3724 | 22445.9996 | 3.947%
2023-08-31 | 11828.62 | 564.0255 | 21364 | 15898.6828 | 11629 | 18779.7 | 17.856 | 21.272 | 12005.3253 | 12249.9171 | 2.037% | 29.1 | 21865.1956 | 22396.9996 | 2.432%
2023-09-30 | 10997.556 | 494.2157 | 23713 | 15274.3833 | 11402 | 18088.3 | 43.92 | 19.6733 | 10685.1004 | 10718.9739 | 0.317% | 32.1 | 21317.3942 | 21479.9996 | 0.7628%
2023-10-31 | 10932.34 | 461.1476 | 20849 | 14694.0054 | 11260 | 16853.6 | 5.952 | 13.4688 | 10757.1302 | 10593.967 | 1.517% | 30 | 19208.5675 | 17668.0452 | 8.02%
2023-11-30 | 11456.562 | 454.778 | 20579 | 15911.8917 | 12555 | 18103 | 2.88 | 4.66 | 11478.5016 | 11007.299 | 4.105% | -1.5 | 20453.2108 | 19742.0453 | 3.477%
2023-12-31 | 12065.5 | 427.7837 | 20004 | 16217.0699 | 12029 | 18506.6 | 0.744 | 3.0699 | 12384.2261 | 12018.94 | 2.95% | 3 | 21211.1571 | 20346.0453 | 4.079%
2024-01-31 | 13036.084 | 436.2955 | 21081 | 17521.6183 | 13750 | 19526.1 | 26.04 | -1.8882 | 13208.8176 | 12929.406 | 2.115% | -9 | 21405.4347 | 21418.2553 | 0.05989%
2024-02-29 | 11516.766 | 515.0876 | 19624 | 16547.0776 | 12975 | 18418 | 0 | 1.231 | 11729.9509 | 11956.6273 | 1.932% | -3 | 20022.691 | 20987.7553 | 4.82%
2024-03-31 | 11542.29 | 590.9683 | 18902 | 15513.8306 | 12598 | 17286.8 | 0 | 4.7065 | 11632.2959 | 11836.2413 | 1.753% | -1.8 | 18939.8337 | 19645.2454 | 3.724%
2024-04-30 | 10489.417 | 651.5238 | 17947 | 14568.6347 | 11368 | 16245.8 | 0 | 9.56 | 10650.6806 | 10616.6408 | 0.3196% | 6.1 | 18586.0743 | 17839.6154 | 4.016%
2024-05-31 | 10735.152 | 649.7686 | 20402 | 14428.9677 | 11280 | 16339.7 | 6.696 | 17.5914 | 10640.585 | 10660.6544 | 0.1886% | 29.1 | 19498.7984 | 19148.7554 | 1.795%
2024-06-30 | 11566.905 | 625.1741 | 23803 | 16065.1458 | 11298 | 19934.3 | 69.84 | 21.0956 | 11334.1111 | 10892.6773 | 3.895% | 34.2 | 22585.2284 | 22502.1655 | 0.3678%
2024-07-31 | 13072.592 | 622.0428 | 23206 | 17570.6882 | 11159 | 21098.8 | 184.512 | 23.7667 | 12956.8035 | 12334.9116 | 4.8% | 31.1 | 23182.1746 | 22729.3704 | 1.953%
2024-08-31 | 12666.051 | 541.4969 | 23110 | 17024.2621 | 12063 | 20495.1 | 113.832 | 22.3538 | 12419.372 | 12432.5962 | 0.1065% | 29.1 | 22518.533 | 22592.9271 | 0.3304%
2024-09-30 | 11321.751 | 509.8347 | 21643 | 15724.6542 | 11633 | 18533 | 14.4 | 20.0589 | 10932.1478 | 11042.347 | 1.008% | 28 | 21462.7165 | 21998.022 | 2.494%
2024-10-31 | 10992.867 | 533.6771 | 18117 | 14775.3589 | 11730 | 16621.4 | 0 | 13.2301 | 11048.6213 | 11073.6096 | 0.2262% | 21.2 | 18603.2901 | 17976.8176 | 3.368%
2024-11-30 | 11312.89 | 458.6703 | 19212 | 15712.3472 | 12378 | 17631.1 | 0 | 7.1389 | 11494.5336 | 11500.099 | 0.04842% | 5.8 | 19942.2233 | 20217.9361 | 1.383%
2024-12-31 | 12959.601 | 445.067 | 21016 | 17418.8185 | 13155 | 19552.8 | 34.968 | -0.25484 | 13046.7703 | 12626.6472 | 3.22% | -10.5 | 21342.8087 | 21036.6297 | 1.435%
2025-01-31 | 13668.714 | 511.7658 | 22058 | 18371.9274 | 13626 | 20564 | 148.056 | -4.7839 | 13661.657 | 13253.9945 | 2.984% | -12 | 22379.5336 | 21835.8361 | 2.429%
2025-02-28 | 12278.547 | 424.9022 | 21399 | 16503.4234 | 14670 | 20182.3 | 96.096 | -4.2048 | 12130.7045 | 11671.9004 | 3.782% | -6.9 | 21116.0479 | 21259.4124 | 0.6789%
2025-03-31 | 12057.659 | 627.9253 | 20232 | 16206.5309 | 12515 | 18017.4 | 2.232 | 3.3323 | 12091.2745 | 12058.4394 | 0.2716% | -5.3 | 19614.4739 | 20000.0174 | 1.966%
2025-04-30 | 10837.309 | 643.6038 | 19271 | 14566.2755 | 11805 | 16902.1 | 0 | 8.5978 | 10891.1786 | 10619.601 | 2.494% | 0.1 | 19246.3001 | 18154.8411 | 5.671%
2025-05-31 | 10784.244 | 639.538 | 18190 | 14494.9516 | 11648 | 16270.8 | 0 | 14.3613 | 10886.6628 | 10649.1943 | 2.181% | 27.1 | 18891.1849 | 19064.5516 | 0.9177%
2025-06-30 | 11845.624 | 633.9965 | 24775 | 15921.5376 | 11639 | 20141.9 | 77.04 | 22.01 | 11544.6629 | 11223.7937 | 2.779% | 34.9 | 22678.4237 | 22279.0506 | 1.761%
2025-07-31 | 13905.926 | 604.4885 | 24399 | 18690.7608 | 12762 | 22537.1 | 279 | 25.4108 | 13471.3387 | 12424.9641 | 7.767% | 33.2 | 23249.8525 | 23168.1551 | 0.3514%
2025-08-31 | 12930.485 | 545.7734 | 24500 | 17379.6841 | 12184 | 22130.4 | 155.496 | 22.5892 | 12734.6294 | 12363.8608 | 2.911% | 32.2 | 23530.1953 | 22782.3554 | 3.178%
2025-09-30 | 11276.887 | 458.924 | 19991 | 15157.1062 | 12093 | 18262.3 | 0 | 19.7033 | 11125.7506 | 11069.0052 | 0.51% | 29.2 | 21192.8937 | 21288.0486 | 0.449%
2025-10-31 | 11319.417 | 481.3716 | 20310 | 15214.2702 | 11805 | 17125.2 | 1.488 | 12.943 | 11323.7934 | 11076.979 | 2.18% | 28 | 18572.3296 | 18320.7967 | 1.354%
2025-11-30 | 12026.73 | 415.8447 | 19827 | 16164.9597 | 13242 | 18499.4 | 0 | 4.2522 | 12004.1764 | 11562.3458 | 3.681% | -2.9 | 19963.3073 | 20153.1936 | 0.9512%
2025-12-31 | 13676.513 | 407.8892 | 21541 | 18382.4099 | 14548 | 20160.6 | 97.464 | -2.686 | 13529.2595 | 12900.8568 | 4.645% | -4.9 | 21487.8851 | 21447.1157 | 0.1897%
2026-01-31 | 14011.783 | 468.9634 | 22064 | 18833.0417 | 14781 | 20879.6 | 220.224 | -5.5957 | 13936.0376 | 13826.1993 | 0.7882% | -11 | 22160.5721 | 22550.57 | 1.76%
2026-02-28 | 12373.552 | 382.2628 | 21821 | 16631.1183 | 14595 | 20375.4 | 110.88 | -3.8238 | 12322.8763 | 12168.7162 | 1.251% | -8.1 | 21428.1773 | 21686.2 | 1.204%
Back to main menu

## Table 1.4.3
Back to main menu
Table 1.4.3: Monthly Consumption by Market Participant Type
| Monthly Energy Demand (GWh) |  |  |  |  | Monthly Peak Demand (MW)
Month | Energy Demand | LDC Consumption | Wholesale Consumption | Generator Consumption | Losses | Peak Demand | LDC Consumption | Wholesale Consumption | Generator Consumption | Losses
2002-05-31 | 11874.901 | 9466.601 | 2081.739 | 140.146 | 186.415 | 20068 | 16707.96 | 2841.338 | 157.638 | 361.064
2002-06-30 | 12185.238 | 9864.032 | 2012.067 | 134.504 | 174.635 | 23578 | 20428.91 | 2643.003 | 137.661 | 368.426
2002-07-31 | 14033.343 | 11576.297 | 2018.911 | 150.335 | 287.8 | 25226 | 22063.8 | 2415.473 | 134.548 | 612.179
2002-08-31 | 13748.878 | 11167.443 | 2096.774 | 176.548 | 308.113 | 25414 | 21694.54 | 2594.581 | 196.459 | 928.42
2002-09-30 | 12593.138 | 10114.337 | 2050.509 | 142.07 | 286.222 | 25062 | 21577.29 | 2561.387 | 144.599 | 778.724
2002-10-31 | 12397.839 | 9862.483 | 2137.213 | 149.407 | 248.736 | 21216 | 17642.04 | 2820.526 | 141.773 | 611.661
2002-11-30 | 12655.667 | 10127.444 | 2112.743 | 143.845 | 271.635 | 21862 | 18381.47 | 2755.733 | 168.79 | 556.007
2002-12-31 | 13483.864 | 11037.036 | 2023.317 | 170.222 | 253.289 | 23334 | 19815.43 | 2740.625 | 146.763 | 631.182
2003-01-31 | 14486.674 | 11888.726 | 2187.64 | 167.688 | 242.62 | 24158 | 20778.8 | 2817.494 | 154.589 | 407.117
2003-02-28 | 13122.529 | 10715.513 | 1981.331 | 156.006 | 269.679 | 23469 | 20024.81 | 2805.901 | 215.791 | 422.498
2003-03-31 | 13414.004 | 10768.113 | 2192.28 | 167.167 | 286.444 | 23117 | 19689.78 | 2885.733 | 187.437 | 354.05
2003-04-30 | 12097.332 | 9624.429 | 2088.532 | 161.837 | 222.534 | 21010 | 17771.1 | 2657.654 | 196.626 | 384.62
2003-05-31 | 11627.445 | 9165.532 | 2114.832 | 143.984 | 203.097 | 18741 | 15387.78 | 2817.187 | 186.956 | 349.077
2003-06-30 | 11884.956 | 9582.859 | 1921.764 | 167.923 | 212.41 | 24753 | 21586.53 | 2263.442 | 188.539 | 714.489
2003-07-31 | 12897.586 | 10664.835 | 1835.72 | 158.334 | 238.697 | 23175 | 20435.12 | 2212.712 | 162.441 | 364.727
2003-08-31 | 12514.308 | 10340.948 | 1783.823 | 170.359 | 219.178 | 23891 | 20915.12 | 2358.598 | 184.046 | 433.236
2003-09-30 | 11794.469 | 9431.235 | 1977.11 | 167.921 | 218.203 | 20700 | 17454.71 | 2612.308 | 163.716 | 469.266
2003-10-31 | 12159.932 | 9686.179 | 2067.456 | 198.093 | 208.204 | 20408 | 16887.17 | 2775.37 | 298.908 | 446.552
2003-11-30 | 12389.858 | 9948.111 | 2036.796 | 175.8 | 229.151 | 21584 | 17991.12 | 2782.01 | 190.243 | 620.627
2003-12-31 | 13327.663 | 10932.665 | 1969.767 | 183.865 | 241.366 | 22798 | 19265.16 | 2834.078 | 176.349 | 522.413
2004-01-31 | 14767.413 | 12198.477 | 2104.447 | 198.64 | 265.849 | 24937 | 21481.3 | 2721.368 | 264.033 | 470.299
2004-02-29 | 13088.075 | 10672.632 | 1970.306 | 177.544 | 267.593 | 22608 | 19037.09 | 2699.003 | 255.4771 | 616.4299
2004-03-31 | 13224.641 | 10655.46 | 2122.051 | 169.56 | 277.57 | 21634 | 18016.84 | 2626.161 | 277.468 | 713.531
2004-04-30 | 11792.132 | 9440.718 | 1965.52 | 135.051 | 250.843 | 19911 | 16643.61 | 2707.734 | 178.464 | 381.192
2004-05-31 | 11835.269 | 9342.564 | 2043.903 | 155.45 | 293.352 | 20327 | 17063.54 | 2516.653 | 165.742 | 581.065
2004-06-30 | 12045.885 | 9547.152 | 2052.914 | 164.35 | 281.469 | 23163 | 19707.77 | 2663.11 | 157.95 | 634.17
2004-07-31 | 12769.985 | 10306.992 | 1967.079 | 177.05 | 318.864 | 23976 | 20506.23 | 2491.816 | 166.45 | 811.504
2004-08-31 | 12746.297 | 10241.325 | 2047.405 | 178.064 | 279.503 | 23159 | 19644.67 | 2631.637 | 186.377 | 696.316
2004-09-30 | 12369.687 | 9861.224 | 2065.015 | 156.763 | 286.685 | 21911 | 18334.65 | 2713.43 | 146.421 | 716.499
2004-10-31 | 12215.166 | 9633.603 | 2153.798 | 167.2 | 260.565 | 19829 | 16245.53 | 2899.387 | 159.471 | 524.612
2004-11-30 | 12601.008 | 10046.497 | 2070.218 | 187.926 | 296.367 | 22066 | 18138.28 | 2941.28 | 297.978 | 688.462
2004-12-31 | 13981.717 | 11434.513 | 2017.175 | 194.386 | 335.643 | 24979 | 21447.05 | 2662.278 | 196.875 | 672.797
2005-01-31 | 14619.18 | 12016.966 | 2090.334 | 198.56 | 313.32 | 24362 | 21030.26 | 2558.497 | 208.777 | 564.466
2005-02-28 | 12731.835 | 10393.346 | 1913.32 | 153.437 | 271.732 | 22322 | 18828.79 | 2715.305 | 226.273 | 551.632
2005-03-31 | 13494.28 | 10952.794 | 2055.749 | 195.636 | 290.101 | 22724 | 19266.54 | 2706.327 | 202.516 | 548.617
2005-04-30 | 11827.861 | 9388.13 | 1980.341 | 188.9 | 270.49 | 19343 | 15820.59 | 2789.575 | 261.253 | 471.582
2005-05-31 | 11744.825 | 9333.369 | 1989.317 | 174.521 | 247.618 | 19007 | 15617.54 | 2700.374 | 152.414 | 536.672
2005-06-30 | 13499.266 | 11095.068 | 1907.147 | 169.877 | 327.174 | 26157 | 22535.89 | 2563.391 | 200.283 | 857.436
2005-07-31 | 14094.375 | 11641.796 | 1878.941 | 191.549 | 382.089 | 26160 | 22580.23 | 2333.553 | 242.33 | 1003.887
2005-08-31 | 14031.29 | 11407.667 | 2030.291 | 207.892 | 385.44 | 25816 | 22243.61 | 2430.247 | 216.422 | 925.721
2005-09-30 | 12552.618 | 10024.722 | 1983.19 | 197.067 | 347.639 | 23914 | 20335.88 | 2512.888 | 216.241 | 848.991
2005-10-31 | 12187.328 | 9837.039 | 1904.417 | 177.228 | 268.644 | 20752 | 17598.01 | 2427.417 | 178.481 | 548.092
2005-11-30 | 12440.55 | 10179.434 | 1831.654 | 164.858 | 264.604 | 22564 | 19415.04 | 2459.517 | 173.174 | 516.269
2005-12-31 | 13745.639 | 11400.567 | 1858.136 | 196.651 | 290.285 | 23766 | 20461.34 | 2428.282 | 252.777 | 623.601
2006-01-31 | 13596.17 | 11188.909 | 1905.583 | 187.931 | 313.747 | 23052 | 19542.59 | 2540.335 | 211.234 | 757.841
2006-02-28 | 12568.25 | 10421.74 | 1719.011 | 163.583 | 263.916 | 22321 | 18801.15 | 2538.497 | 239.103 | 742.25
2006-03-31 | 13199.998 | 10803.314 | 1939.387 | 173.782 | 283.515 | 21772 | 18543.05 | 2487.994 | 178.339 | 562.617
2006-04-30 | 11512.852 | 9215.929 | 1861.338 | 153.612 | 281.973 | 19582 | 16298.82 | 2556.562 | 160.219 | 566.399
2006-05-31 | 11927.478 | 9647.028 | 1867.851 | 176.75 | 235.849 | 24857 | 21656.22 | 2407.501 | 238.276 | 555.003
2006-06-30 | 12541.936 | 10215.528 | 1875.843 | 193.439 | 257.126 | 23349 | 20111.81 | 2383.145 | 176.614 | 677.431
2006-07-31 | 13853.619 | 11539.169 | 1830.002 | 187.291 | 297.157 | 26092 | 22600.56 | 2398.848 | 185.769 | 906.823
2006-08-31 | 13308.1 | 10969.255 | 1903.683 | 161.696 | 273.466 | 27005 | 23709.23 | 2399.945 | 170.879 | 724.946
2006-09-30 | 11521.035 | 9386.092 | 1789.232 | 159.352 | 186.359 | 19976 | 16932.17 | 2457.453 | 175.436 | 410.941
2006-10-31 | 11962.307 | 9829.599 | 1745.321 | 150.308 | 237.079 | 19590 | 16650.66 | 2371.199 | 188.448 | 379.693
2006-11-30 | 12178.739 | 10018.7 | 1734.991 | 163.953 | 261.095 | 21267 | 18187.39 | 2295.35 | 204.2 | 580.06
2006-12-31 | 12884.176 | 10733.116 | 1708.01 | 162.411 | 280.639 | 22941 | 19873.93 | 2164.479 | 207.483 | 695.108
2007-01-31 | 13758.097 | 11458.472 | 1823.005 | 161.93 | 314.69 | 23537 | 20372.37 | 2394.209 | 185.55 | 584.871
2007-02-28 | 13037.578 | 11013.358 | 1619.551 | 142.892 | 261.777 | 23935 | 20829.21 | 2384.199 | 165.209 | 556.382
2007-03-31 | 13192.72 | 10931.852 | 1833.514 | 178.988 | 248.366 | 22969 | 19865.96 | 2417.187 | 260.159 | 425.694
2007-04-30 | 11827.647 | 9668.557 | 1776.836 | 165.698 | 216.556 | 20016 | 16660.53 | 2684.113 | 161.312 | 510.045
2007-05-31 | 11818.634 | 9589.524 | 1804.081 | 202.45 | 222.579 | 21490 | 18256.83 | 2306.318 | 236.902 | 689.95
2007-06-30 | 12692.547 | 10502.573 | 1730.187 | 186.088 | 273.699 | 25737 | 22461.02 | 2385.343 | 177.232 | 713.405
2007-07-31 | 12840.811 | 10640.371 | 1719.629 | 188.169 | 292.642 | 24561 | 21500.94 | 2264.306 | 200.085 | 595.669
2007-08-31 | 13454.57 | 11202.657 | 1742.24 | 199.774 | 309.899 | 25584 | 22471.59 | 2135.841 | 233.451 | 743.118
2007-09-30 | 11916.219 | 9815.422 | 1676.489 | 184.25 | 240.058 | 24046 | 20805.99 | 2324.986 | 195.763 | 719.261
2007-10-31 | 11908.105 | 9825.783 | 1715.497 | 148.482 | 218.343 | 19233 | 16516.44 | 2203.376 | 131.916 | 381.268
2007-11-30 | 12350.431 | 10287.772 | 1677.403 | 169.532 | 215.724 | 21814 | 19071.32 | 2102.755 | 159.15 | 480.775
2007-12-31 | 13407.761 | 11284.385 | 1674.218 | 171.179 | 277.979 | 22935 | 19842.07 | 2253.562 | 206.111 | 633.257
2008-01-31 | 13609.986 | 11443.712 | 1728.704 | 166.817 | 270.753 | 22782 | 19743.18 | 2259.941 | 188.114 | 590.765
2008-02-29 | 12896.823 | 10838.401 | 1633.662 | 147.825 | 276.935 | 23054 | 19969.28 | 2349.389 | 165.128 | 570.203
2008-03-31 | 13003.771 | 10838.211 | 1720.417 | 173.083 | 272.06 | 20990 | 17994.66 | 2205.371 | 217.193 | 572.776
2008-04-30 | 11520.396 | 9367.341 | 1699.281 | 151.486 | 302.288 | 19512 | 16522.2 | 2326.748 | 194.598 | 468.454
2008-05-31 | 11407.14 | 9211.31 | 1732.848 | 162.026 | 300.956 | 18650 | 15591.79 | 2431.522 | 170.796 | 455.892
2008-06-30 | 12189.13 | 9970.632 | 1736.46 | 170.098 | 311.94 | 24195 | 21012.33 | 2343.515 | 181.583 | 657.572
2008-07-31 | 13155.66 | 10881.08 | 1770.797 | 177.722 | 326.061 | 23787 | 20810.26 | 2200.689 | 153.239 | 622.812
2008-08-31 | 12548.525 | 10286.646 | 1787.408 | 173.04 | 301.431 | 22707 | 19448.08 | 2289.167 | 231.554 | 738.199
2008-09-30 | 11793.462 | 9611.373 | 1755.254 | 170.494 | 256.341 | 22975 | 20077.14 | 2198.497 | 161.722 | 537.641
2008-10-31 | 11634.137 | 9611.594 | 1645.026 | 164.976 | 212.541 | 19366 | 16642.02 | 2071.701 | 179.135 | 473.144
2008-11-30 | 11828.99 | 9989.561 | 1418.322 | 179.317 | 241.79 | 21279 | 18309.22 | 1826.499 | 227.767 | 915.514
2008-12-31 | 13087.707 | 11170.594 | 1413.875 | 191.224 | 312.014 | 22541 | 19782.98 | 1874.284 | 198.588 | 685.148
2009-01-31 | 13730.291 | 11751.74 | 1506.224 | 184.672 | 287.655 | 22983 | 19479.27 | 1824.502 | 239.3108 | 1439.9172
2009-02-28 | 11697.974 | 10037.791 | 1242.672 | 159.759 | 257.752 | 22110 | 18884.05 | 1763.431 | 255.6966 | 1206.8224
2009-03-31 | 12166.882 | 10357.06 | 1375.926 | 158.075 | 275.821 | 21466 | 16832.38 | 1780.814 | 221.7559 | 2631.0501
2009-04-30 | 10746.635 | 9088.459 | 1224.828 | 201.2 | 232.148 | 18744 | 15030.25 | 1775.23 | 295.5305 | 1642.9895
2009-05-31 | 10504.201 | 8780.168 | 1251.811 | 206.235 | 265.987 | 17560 | 20038.81 | 1886.091 | 227.77 | -4592.671
2009-06-30 | 10884.323 | 9216.895 | 1206.297 | 188.948 | 272.183 | 22540 | 19081.86 | 1829.943 | 141.6956 | 1486.5014
2009-07-31 | 11315.411 | 9620.536 | 1210.339 | 221.321 | 263.215 | 20011 | 22713.48 | 1581.902 | 158.5048 | -4442.8868
2009-08-31 | 12225.812 | 10434.537 | 1301.835 | 211.757 | 277.683 | 24380 | 22057.34 | 1746.493 | 229.3842 | 346.7828
2009-09-30 | 10931.831 | 9277.913 | 1239.615 | 177.855 | 236.448 | 19731 | 21922.34 | 1687.679 | 239.7521 | -4118.7711
2009-10-31 | 11181.875 | 9508.079 | 1259.913 | 179.112 | 234.771 | 18420 | 15363.31 | 1932.541 | 233.1459 | 891.0031
2009-11-30 | 11112.909 | 9475.052 | 1262.265 | 173.551 | 202.041 | 19710 | 17340.45 | 1920.156 | 233.9333 | 215.4607
2009-12-31 | 12688.573 | 10946.598 | 1225.323 | 204.103 | 312.549 | 21831 | 19729.84 | 1749.27 | 252.1934 | 99.6966
2010-01-31 | 13145.438 | 11330.024 | 1308.6 | 224.973 | 281.841 | 22045 | 19479.27 | 1824.502 | 239.3108 | 501.9172
2010-02-28 | 11751.752 | 10068.441 | 1247.677 | 172.272 | 263.362 | 21367 | 18884.05 | 1763.431 | 255.6966 | 463.8224
2010-03-31 | 11686.054 | 9927.551 | 1346.685 | 178.911 | 232.907 | 19393 | 16832.38 | 1780.814 | 221.7559 | 558.0501
2010-04-30 | 10474.752 | 8748.214 | 1305.947 | 201.493 | 219.098 | 17398 | 15030.25 | 1775.23 | 295.5305 | 296.9895
2010-05-31 | 11368.031 | 9536.118 | 1350.434 | 184.847 | 296.632 | 22904 | 20038.81 | 1886.091 | 227.77 | 751.329
2010-06-30 | 11555.961 | 9797.61 | 1334.971 | 175.296 | 248.084 | 21527 | 19081.86 | 1829.943 | 141.6956 | 473.5014
2010-07-31 | 13307.242 | 11457.602 | 1358.685 | 196.219 | 294.736 | 25075 | 22713.48 | 1581.902 | 158.5048 | 621.1132
2010-08-31 | 12921.565 | 11046.524 | 1379.923 | 227.005 | 268.113 | 24917 | 22057.34 | 1746.493 | 229.3842 | 883.7828
2010-09-30 | 11049.081 | 9272.091 | 1363.8 | 223.294 | 189.896 | 24444 | 21922.34 | 1687.679 | 239.7521 | 594.2289
2010-10-31 | 10929.335 | 9166.553 | 1415.512 | 194.924 | 152.346 | 17704 | 15363.31 | 1932.541 | 233.1459 | 175.0031
2010-11-30 | 11303.778 | 9631.649 | 1343.104 | 197.012 | 132.013 | 19970 | 17340.45 | 1920.156 | 233.9333 | 475.4607
2010-12-31 | 12694.155 | 10967.855 | 1333.472 | 213.793 | 179.035 | 22114 | 19729.84 | 1749.27 | 252.1934 | 382.6966
2011-01-31 | 13301.687 | 11430.562 | 1397.349 | 228.348 | 245.428 | 22733 | 19938.47 | 1797.701 | 258.0538 | 738.7752
2011-02-28 | 11775.464 | 10128.289 | 1258.023 | 199.187 | 189.965 | 21871 | 19081.88 | 1931.922 | 277.2781 | 579.9199
2011-03-31 | 12352.443 | 10487.541 | 1406.471 | 201.955 | 256.476 | 20667 | 17995.89 | 1925.285 | 237.1581 | 508.6669
2011-04-30 | 10789.012 | 9101.443 | 1313.581 | 194.8 | 179.188 | 17945 | 15411.63 | 1836.07 | 292.9127 | 404.3873
2011-05-31 | 10781.74 | 9046.905 | 1316.588 | 204.821 | 213.426 | 20847 | 18580.71 | 1504.528 | 253.6881 | 508.0739
2011-06-30 | 11238.277 | 9544.739 | 1219.471 | 194.518 | 279.549 | 22765 | 20342.47 | 1415.288 | 252.5383 | 754.7037
2011-07-31 | 13298.189 | 11448.888 | 1312.715 | 207.837 | 328.749 | 25450 | 23322.88 | 1198.084 | 203.9427 | 725.0933
2011-08-31 | 12531.706 | 10718.286 | 1371.117 | 191.542 | 250.761 | 22051 | 19562.88 | 1720.727 | 249.3743 | 518.0187
2011-09-30 | 11144.546 | 9376.834 | 1367.366 | 174.416 | 225.93 | 21552 | 19043.84 | 1747.319 | 185.7929 | 575.0481
2011-10-31 | 11012.737 | 9287.2 | 1366.261 | 151.445 | 207.831 | 18234 | 15871.5 | 1827.09 | 177.9033 | 357.5067
2011-11-30 | 11116.536 | 9428.401 | 1307.621 | 148.173 | 232.341 | 19673 | 17154.6 | 1837.406 | 218.8018 | 462.1922
2011-12-31 | 12121.895 | 10412.869 | 1295.596 | 184.83 | 228.6 | 20204 | 17925.51 | 1726.402 | 223.1266 | 328.9614
2012-01-31 | 12715.234 | 10948.174 | 1362.721 | 185.799 | 218.54 | 21847 | 19150.62 | 1791.478 | 308.8587 | 596.0433
2012-02-29 | 11610.18 | 9922.71 | 1283.368 | 163.061 | 241.041 | 19956 | 17273.85 | 1856.136 | 237.3638 | 588.6502
2012-03-31 | 11487.527 | 9660.31 | 1405.691 | 196.881 | 224.645 | 20332 | 17720.09 | 1987.229 | 260.8596 | 363.8214
2012-04-30 | 10641.371 | 8873.913 | 1365.573 | 191.349 | 210.536 | 17874 | 15231.22 | 1915.3 | 237.3826 | 490.0974
2012-05-31 | 11136.995 | 9304.02 | 1413.625 | 203.936 | 215.414 | 21106 | 18637.39 | 1687.272 | 242.2982 | 539.0398
2012-06-30 | 11800.326 | 10038.614 | 1338.673 | 178.791 | 244.248 | 24107 | 21813.12 | 1275.996 | 181.9566 | 835.9274
2012-07-31 | 13456.845 | 11552.619 | 1422.06 | 191.485 | 290.681 | 24636 | 22490.51 | 1276.191 | 198.1912 | 671.1078
2012-08-31 | 12632.817 | 10729.711 | 1428.622 | 212.649 | 261.835 | 23188 | 20435.58 | 1870.187 | 259.9366 | 622.2964
2012-09-30 | 11040.767 | 9271.502 | 1330.396 | 211.341 | 227.528 | 21183 | 18728.86 | 1751.122 | 241.4408 | 461.5772
2012-10-31 | 11141.991 | 9297.822 | 1426.415 | 176.549 | 241.205 | 18829 | 16008.33 | 2069.298 | 235.9358 | 515.4362
2012-11-30 | 11487.169 | 9711.027 | 1408.816 | 158.8 | 208.526 | 20144 | 17569.58 | 1922.144 | 212.0993 | 440.1767
2012-12-29 | 12156.557 | 10354.012 | 1377.79 | 173.831 | 250.924 | 20382 | 18041.85 | 1839.009 | 197.6117 | 303.5293
2013-01-31 | 12889.507 | 11003.972 | 1469.787 | 173.53 | 242.218 | 22610 | 19640.28 | 2147.084 | 197.0555 | 625.5805
2013-02-28 | 11742.246 | 9983.339 | 1377.594 | 153.907 | 227.406 | 21426 | 18759.8 | 2044.78 | 262.5673 | 358.8527
2013-03-31 | 11958.319 | 10134.187 | 1438.761 | 184.656 | 200.715 | 19825 | 17448.6 | 1936.126 | 222.6267 | 217.6473
2013-04-30 | 10944.906 | 9160.548 | 1366.503 | 212.478 | 205.377 | 18854 | 16176.39 | 2065.198 | 293.6076 | 318.8044
2013-05-31 | 10785.424 | 8990.721 | 1394.035 | 183.639 | 217.029 | 20488 | 18010.02 | 1884.409 | 199.7068 | 393.8642
2013-06-30 | 11174.679 | 9355.295 | 1365.081 | 163.498 | 290.805 | 22662 | 20486.94 | 1445.578 | 196.7334 | 532.7486
2013-07-31 | 12722.707 | 10867.174 | 1383.961 | 174.841 | 296.731 | 24927 | 22682.78 | 1267.167 | 241.1029 | 735.9501
2013-08-31 | 12100.351 | 10221.728 | 1420.874 | 179.937 | 277.812 | 22833 | 20219.6 | 1889.837 | 209.7228 | 513.8402
2013-09-30 | 10837.167 | 9076.722 | 1392.777 | 156.459 | 211.209 | 22682 | 20068.89 | 1821.304 | 205.8435 | 585.9625
2013-10-31 | 11135.689 | 9198.19 | 1502.292 | 176.758 | 258.449 | 18445 | 15816.3 | 2025.741 | 254.2856 | 348.6734
2013-11-30 | 11640.948 | 9790.636 | 1461.583 | 148.408 | 240.321 | 20615 | 18030.36 | 1922.273 | 267.9082 | 394.4588
2013-12-31 | 12702.006 | 10912.622 | 1447.614 | 188.083 | 153.687 | 21964 | 19570.07 | 2142.251 | 274.6158 | -22.9368
2014-01-31 | 13613.596 | 11658.477 | 1476.947 | 190.578 | 287.594 | 22774 | 20229.64 | 1760.07 | 276.9846 | 507.3054
2014-02-28 | 12067.276 | 10225.218 | 1395.693 | 206.555 | 239.81 | 21905 | 18798.24 | 2082.484 | 434.6011 | 589.6749
2014-03-31 | 12672.074 | 10666.474 | 1546.683 | 198.863 | 260.054 | 21656 | 18943.11 | 1956.483 | 351.4494 | 404.9576
2014-04-30 | 10836.804 | 8962.645 | 1460.568 | 212.109 | 201.482 | 18557 | 15838.52 | 2088.889 | 359.4376 | 270.1534
2014-05-31 | 10642.583 | 8790.577 | 1448.055 | 189.754 | 214.197 | 18844 | 16340.76 | 1952.935 | 239.5254 | 310.7796
2014-06-30 | 11228.548 | 9412.544 | 1454.421 | 166.33 | 195.253 | 20807 | 18622.91 | 1656.722 | 247.2939 | 280.0741
2014-07-31 | 11717.444 | 9845.802 | 1478.577 | 165.739 | 227.326 | 21300 | 19331.84 | 1234.529 | 223.8554 | 509.7756
2014-08-31 | 11718.183 | 9805.466 | 1488.258 | 173.903 | 250.556 | 21363 | 19501.8 | 1280.928 | 252.222 | 328.05
2014-09-30 | 10836.546 | 9080.103 | 1437.045 | 139.093 | 180.305 | 21123 | 19361.88 | 1344.12 | 216.4065 | 200.5935
2014-10-31 | 10819.853 | 9041.876 | 1446.698 | 151.093 | 180.186 | 17784 | 15264.16 | 1959.928 | 218.3104 | 341.6016
2014-11-30 | 11487.634 | 9707.192 | 1437.231 | 142.519 | 200.692 | 20102 | 17733.74 | 1806.566 | 246.3103 | 315.3837
2014-12-31 | 12131.525 | 10359.109 | 1425.828 | 154.903 | 191.685 | 20938 | 18328.41 | 1917.17 | 241.7382 | 450.6818
2015-01-31 | 13119.979 | 11250.337 | 1432.84 | 164.562 | 272.24 | 21814 | 19647.04 | 1319.941 | 240.0045 | 607.0145
2015-02-28 | 12302.278 | 10600.396 | 1335.858 | 142.772 | 223.252 | 21494 | 19379.05 | 1447.463 | 235.947 | 431.54
2015-03-31 | 12044.976 | 10212.786 | 1453.153 | 161.032 | 218.005 | 20827 | 18298.38 | 1955.219 | 289.3311 | 284.0699
2015-04-30 | 10404.962 | 8679.37 | 1405.231 | 151.615 | 168.746 | 18462 | 15708.66 | 1925.434 | 271.1328 | 556.7732
2015-05-31 | 10547.132 | 8798.507 | 1412.842 | 170.524 | 165.259 | 19158 | 16907.98 | 1888.851 | 228.6186 | 132.5504
2015-06-30 | 10624.316 | 8942.283 | 1351.048 | 148.015 | 182.97 | 19339 | 16892.13 | 1861.715 | 253.0514 | 332.1036
2015-07-31 | 12105.066 | 10312.467 | 1395.071 | 169.088 | 228.44 | 22516 | 20656.56 | 1189.704 | 228.4097 | 441.3263
2015-08-31 | 11797.099 | 9965.934 | 1418.277 | 166.564 | 246.324 | 22383 | 20498.96 | 1201.994 | 203.3686 | 478.6774
2015-09-30 | 11361.901 | 9625.828 | 1369.332 | 184.574 | 182.167 | 22063 | 19973.68 | 1257.934 | 211.4512 | 619.9348
2015-10-31 | 10687.264 | 8878.974 | 1453.202 | 194.589 | 160.499 | 17667 | 15013.54 | 1992.14 | 298.4092 | 362.9108
2015-11-30 | 10681.592 | 8963.684 | 1381.098 | 147.434 | 189.376 | 19239 | 16530.39 | 1927.785 | 302.168 | 478.657
2015-12-31 | 11313.857 | 9546.732 | 1393.262 | 167.618 | 206.245 | 19161 | 16555.58 | 1828.622 | 286.6657 | 490.1323
2016-01-31 | 12384.867 | 10508.333 | 1440.227 | 155.238 | 281.069 | 20836 | 18202.71 | 1838.962 | 317.9757 | 476.3523
2016-02-29 | 11471.763 | 9726.471 | 1372.476 | 150.337 | 222.479 | 20766 | 18094.22 | 1993.201 | 286.9147 | 391.6643
2016-03-31 | 11302.963 | 9496.261 | 1451.793 | 148.34 | 206.569 | 20063 | 17468.06 | 1861.963 | 293.4842 | 439.4928
2016-04-30 | 10409.92 | 8680.447 | 1436.773 | 153.646 | 139.054 | 17821 | 15610.16 | 1907.108 | 284.1523 | 19.5797
2016-05-31 | 10470.808 | 8757.947 | 1400.24 | 152.605 | 160.016 | 19885 | 17239.79 | 1934.375 | 353.4562 | 357.3788
2016-06-30 | 11101.521 | 9374.678 | 1386.493 | 146.615 | 193.735 | 21692 | 19702.23 | 1369.924 | 204.5618 | 415.2842
2016-07-31 | 12497.616 | 10733.656 | 1374.658 | 138.773 | 250.529 | 22659 | 20955.64 | 1104.207 | 161.3168 | 437.8362
2016-08-31 | 13113.359 | 11248.853 | 1404.99 | 164.839 | 294.677 | 23100 | 21332.92 | 1122.548 | 195.706 | 448.826
2016-09-30 | 11072.26 | 9296.858 | 1377.715 | 140.375 | 257.312 | 23213 | 21260.85 | 1152.819 | 142.8112 | 656.5198
2016-10-31 | 10518.677 | 8755.244 | 1410.365 | 158.328 | 194.74 | 18189 | 15451.67 | 1927.67 | 270.9776 | 538.6824
2016-11-30 | 10697.637 | 8920.356 | 1404.427 | 165.552 | 207.302 | 19369 | 16599.65 | 2002.135 | 266.5365 | 500.6785
2016-12-31 | 11978.041 | 10093.776 | 1403.94 | 191.718 | 288.607 | 20688 | 18146.04 | 1877.911 | 358.1404 | 305.9086
2017-01-31 | 12108.005 | 10235.721 | 1426.113 | 167.231 | 278.94 | 20372 | 17605.02 | 1903.952 | 284.0204 | 579.0076
2017-02-28 | 10607.563 | 8932.522 | 1327.331 | 157.939 | 189.771 | 19838 | 16763.11 | 2026.818 | 334.4528 | 713.6192
2017-03-31 | 11591.031 | 9770.579 | 1477.122 | 159.279 | 184.051 | 19174 | 16538.62 | 2020.879 | 270.5038 | 343.9972
2017-04-30 | 9788.616 | 8175.766 | 1362.45 | 157.307 | 93.093 | 17349 | 14585.55 | 2041.365 | 287.8311 | 434.2539
2017-05-31 | 10153.182 | 8442.449 | 1391.732 | 178.48 | 140.521 | 17738 | 15261.02 | 1979.705 | 284.9445 | 212.3305
2017-06-30 | 10657.08 | 8977.237 | 1340.846 | 158.409 | 180.588 | 21168 | 18975.18 | 1556.569 | 230.3528 | 405.8982
2017-07-31 | 11587.63 | 9826.461 | 1377.59 | 151.2 | 232.379 | 20627 | 18563.72 | 1412.149 | 207.7732 | 443.3578
2017-08-31 | 11350.012 | 9622.113 | 1359.22 | 157.201 | 211.478 | 20158 | 18606.52 | 1077.556 | 200.8482 | 273.0758
2017-09-30 | 10679.393 | 9122.15 | 1230.396 | 145.584 | 181.263 | 21786 | 20018.32 | 1007.671 | 215.3174 | 544.6916
2017-10-31 | 10339.329 | 8601.176 | 1426.975 | 139.553 | 171.625 | 17418 | 15048.39 | 1943.664 | 223.0329 | 202.9131
2017-11-30 | 10955.909 | 9213.777 | 1408.105 | 157.772 | 176.255 | 19115 | 16384.24 | 2051.185 | 276.3474 | 403.2276
2017-12-31 | 12338.893 | 10436.662 | 1408.63 | 196.667 | 296.934 | 20306 | 17882.19 | 1752.098 | 348.8256 | 322.8864
2018-01-31 | 12700.826 | 10882.596 | 1418.086 | 184.612 | 215.532 | 20906 | 18729.15 | 1274.496 | 374.7405 | 527.6135
2018-02-28 | 10951.065 | 9286.31 | 1323.263 | 160.19 | 181.302 | 20076 | 17391.54 | 1864.722 | 311.1241 | 508.6139
2018-03-31 | 11372.42 | 9566.427 | 1481.01 | 151.405 | 173.578 | 18462 | 15935.17 | 1911.541 | 271.1181 | 344.1709
2018-04-30 | 10578.368 | 8906.101 | 1368.878 | 139.08 | 164.309 | 18011 | 15475.92 | 1864.188 | 260.0555 | 410.8365
2018-05-31 | 10421.469 | 8725.155 | 1401.01 | 144.713 | 150.591 | 20473 | 18194.47 | 1599.295 | 211.7844 | 467.4506
2018-06-30 | 10923.446 | 9205.996 | 1373.762 | 146.9 | 196.788 | 21369 | 19090.62 | 1289.531 | 204.4922 | 784.3568
2018-07-31 | 12685.981 | 10951.054 | 1361.765 | 156.277 | 216.885 | 22909 | 21057.29 | 1149.358 | 275.492 | 426.86
2018-08-31 | 12688.795 | 10901.079 | 1390.079 | 149.133 | 248.504 | 21990 | 20345.65 | 1147.967 | 182.3349 | 314.0481
2018-09-30 | 11147.31 | 9441.469 | 1367.583 | 123.823 | 214.435 | 23240 | 21307.89 | 1121.28 | 169.2054 | 641.6246
2018-10-31 | 10717.348 | 9029.399 | 1440.57 | 138.254 | 109.125 | 18205 | 16055.12 | 1996.924 | 203.89 | -50.934
2018-11-30 | 11360.321 | 9612.505 | 1412.934 | 141.553 | 193.329 | 20152 | 17440.76 | 1925.193 | 292.2894 | 493.7576
2018-12-31 | 11938.614 | 10066.572 | 1439.964 | 165.292 | 266.786 | 19891 | 17186.14 | 1853.428 | 293.5 | 557.932
2019-01-31 | 12777.216 | 10984.339 | 1424.631 | 157.579 | 210.667 | 21525 | 18834.82 | 1824.973 | 233.4161 | 631.7909
2019-02-28 | 11291.744 | 9679.029 | 1303.065 | 132.852 | 176.798 | 20500 | 17986.65 | 1882.421 | 243.2612 | 387.6678
2019-03-31 | 11658.678 | 9872.263 | 1444.563 | 151.489 | 190.363 | 20263 | 17522.65 | 2049.826 | 239.7963 | 450.7277
2019-04-30 | 10264.505 | 8608.974 | 1338.349 | 170.596 | 146.586 | 17645 | 14956.61 | 2012.241 | 273.7595 | 402.3895
2019-05-31 | 10219.56 | 8467.021 | 1405.277 | 177.012 | 170.25 | 16784 | 14068.65 | 1848.762 | 312.4022 | 554.1858
2019-06-30 | 10365.619 | 8681.844 | 1388.098 | 145.5 | 150.177 | 20248 | 18015.36 | 1545.989 | 210.2323 | 476.4187
2019-07-31 | 12792.766 | 11052.777 | 1356.389 | 147.863 | 235.737 | 21791 | 20077.9 | 1055.989 | 181.1607 | 475.9503
2019-08-31 | 11825.052 | 10103.635 | 1379.382 | 141.201 | 200.834 | 21354 | 19286.97 | 1418.286 | 163.5032 | 485.2408
2019-09-30 | 10318.533 | 8735.445 | 1286.871 | 129.154 | 167.063 | 19717 | 17232.99 | 1865.817 | 179.2536 | 438.9394
2019-10-31 | 10351.05 | 8695.342 | 1377.19 | 133.423 | 145.095 | 18329 | 15858.72 | 1799.031 | 169.3067 | 501.9423
2019-11-30 | 11255.325 | 9566.229 | 1344.964 | 144.138 | 199.994 | 19625 | 17204.45 | 1869.312 | 264.8378 | 286.4002
2019-12-31 | 11997.095 | 10167.965 | 1390.827 | 185.248 | 253.055 | 20974 | 18132.44 | 1886.516 | 329.041 | 626.003
2020-01-31 | 12178.575 | 10383.457 | 1421.435 | 154.804 | 218.879 | 19928 | 17248.55 | 2038.156 | 255.5653 | 385.7287
2020-02-29 | 11239.82 | 9622.815 | 1333.64 | 130.239 | 153.126 | 19630 | 17209.54 | 1932.968 | 256.8344 | 230.6576
2020-03-31 | 10989.389 | 9283.197 | 1393.918 | 146.703 | 165.571 | 18183 | 15475.37 | 1969.849 | 270.2771 | 467.5039
2020-04-30 | 9282.854 | 7848.11 | 1153.337 | 156.852 | 124.555 | 15350 | 13280.69 | 1582.584 | 267.4529 | 219.2731
2020-05-31 | 9642.117 | 8168.463 | 1164.589 | 179.62 | 129.445 | 20649 | 18503.86 | 1386.916 | 269.737 | 488.487
2020-06-30 | 10800.015 | 9266.452 | 1204.421 | 158.555 | 170.587 | 21292 | 19034.88 | 1670.309 | 214.578 | 372.233
2020-07-31 | 13202.706 | 11611.332 | 1217.734 | 133.797 | 239.843 | 24446 | 22412.78 | 1343.705 | 211.87 | 477.645
2020-08-31 | 12081.08 | 10404.924 | 1293.469 | 146.854 | 235.833 | 23823 | 21283.78 | 1752.135 | 160.3762 | 626.7088
2020-09-30 | 10114.374 | 8539.376 | 1272.232 | 155.933 | 146.833 | 20225 | 17908.17 | 1726.147 | 208.4155 | 382.2675
2020-10-31 | 10339.39 | 8709.182 | 1346.746 | 136.399 | 147.063 | 17679 | 15258.76 | 1701.44 | 205.3914 | 513.4086
2020-11-30 | 10529.032 | 8952.778 | 1298.175 | 117.956 | 160.123 | 19147 | 16766.96 | 1779.029 | 198.332 | 402.679
2020-12-31 | 11811.675 | 10133.006 | 1324.33 | 159.628 | 194.711 | 20738 | 18149.66 | 1713.527 | 257.8595 | 616.9535
2021-01-31 | 12105.158 | 10361.393 | 1380.422 | 146.481 | 216.862 | 20150 | 17617.05 | 1904.916 | 201.7136 | 426.3204
2021-02-28 | 11233.123 | 9628.043 | 1286.376 | 128.04 | 190.664 | 20318 | 17713.35 | 1954.603 | 223.5765 | 426.4705
2021-03-31 | 11101.706 | 9383.05 | 1403.012 | 168.316 | 147.328 | 19344 | 16809.63 | 2016.47 | 209.1617 | 308.7383
2021-04-30 | 9781.57 | 8232.163 | 1334.867 | 145.429 | 69.111 | 16644 | 14263.1 | 1961.507 | 260.3496 | 159.0434
2021-05-31 | 10086.333 | 8498.898 | 1381.951 | 153.836 | 51.648 | 19443 | 17017.05 | 1789.111 | 185.9648 | 450.8742
2021-06-30 | 11262.474 | 9735.938 | 1259.332 | 132.576 | 134.628 | 22258 | 20483.21 | 1053.779 | 173.4785 | 547.5325
2021-07-31 | 11636.443 | 10067.983 | 1281.389 | 140.02 | 147.051 | 21655 | 20129.06 | 1024.867 | 174.991 | 326.082
2021-08-31 | 12856.511 | 11257.223 | 1276.353 | 145.534 | 177.401 | 22986 | 21152.87 | 1128.732 | 185.5447 | 518.8533
2021-09-30 | 10389.017 | 8816.858 | 1282.526 | 133.464 | 156.169 | 18769 | 16537.54 | 1688.898 | 169.64 | 372.922
2021-10-31 | 10516.14 | 8812.988 | 1349.298 | 146.187 | 207.667 | 17312 | 14836.55 | 1808.165 | 181.1434 | 486.1416
2021-11-30 | 10956.602 | 9289.843 | 1330.551 | 131.91 | 204.298 | 19644 | 17057.11 | 1886.821 | 179.7903 | 520.2787
2021-12-31 | 11969.602 | 10162.622 | 1393.558 | 150.401 | 263.021 | 20455 | 17758.36 | 1898.71 | 182.8977 | 615.0323
2022-01-31 | 13085.388 | 11309.713 | 1429.374 | 141.901 | 204.4 | 21349 | 18872.96 | 1818.319 | 192.0121 | 465.7089
2022-02-28 | 11487.734 | 9868.554 | 1279.543 | 139.57 | 200.067 | 20918 | 18284.47 | 1830.206 | 189.9149 | 613.4091
2022-03-31 | 11816.835 | 10021.983 | 1420.351 | 166.958 | 207.543 | 19763 | 17226.22 | 1876.425 | 246.9115 | 413.4435
2022-04-30 | 10265.047 | 8643.765 | 1301.591 | 139.261 | 180.43 | 17256 | 14635.63 | 1914.953 | 182.8324 | 522.5846
2022-05-31 | 10469.914 | 8743.427 | 1411.702 | 163.924 | 150.861 | 21292 | 19075.72 | 1585.076 | 182.1273 | 449.0767
2022-06-30 | 10929.858 | 9321.502 | 1299.146 | 148.831 | 160.379 | 21954 | 20047.8 | 1088.784 | 246.9046 | 570.5114
2022-07-31 | 12343.623 | 10601.099 | 1341.868 | 144.639 | 256.017 | 22607 | 21008.88 | 1021.468 | 156.3699 | 420.2821
2022-08-31 | 12624.254 | 10830.757 | 1351.532 | 144.462 | 297.503 | 21871 | 19879.56 | 1139.376 | 178.3511 | 673.7129
2022-09-30 | 10814.096 | 9116.212 | 1329.888 | 135.217 | 232.779 | 20350 | 17812.02 | 1857.612 | 220.7457 | 459.6223
2022-10-31 | 10384.167 | 8716.711 | 1336.906 | 114.553 | 215.997 | 17294 | 14671.49 | 1804.303 | 147.6571 | 670.5499
2022-11-30 | 11044.181 | 9332.357 | 1358.357 | 150.022 | 203.445 | 19441 | 16685.5 | 1963.331 | 221.7309 | 570.4381
2022-12-31 | 12273.23 | 10425.209 | 1423.836 | 177.746 | 246.439 | 20173 | 17611.79 | 1854.189 | 279.0826 | 427.9384
2023-01-31 | 12519.712 | 10663.9284 | 1442.7604 | 147.6643 | 265.3589 | 20486 | 17788.22 | 1880.245 | 189.9117 | 627.6233
2023-02-28 | 11225.17 | 9600.1488 | 1293.0651 | 135.588 | 196.3681 | 21388 | 18906.97 | 1669.987 | 182.8198 | 628.2232
2023-03-31 | 11846.269 | 10020.4543 | 1460.0804 | 185.4365 | 180.2977 | 18811 | 16110.98 | 1876.802 | 245.219 | 577.999
2023-04-30 | 10271.638 | 8627.354 | 1342.3702 | 129.821 | 172.0928 | 17547 | 14996.01 | 1623.887 | 195.8285 | 731.2745
2023-05-31 | 10356.75 | 8683.1386 | 1389.07 | 150.1265 | 134.4149 | 20787 | 18609.24 | 1622.633 | 190.6279 | 364.4991
2023-06-30 | 11119.814 | 9405.7355 | 1361.0294 | 177.7235 | 175.3256 | 21463 | 19512.09 | 1275.405 | 235.6532 | 439.8518
2023-07-31 | 12507.785 | 10774.2868 | 1327.9647 | 198.4082 | 207.1253 | 22686 | 20840.57 | 904.1759 | 297.5355 | 643.7186
2023-08-31 | 11828.62 | 10023.4866 | 1395.9442 | 179.0739 | 230.1152 | 21364 | 19051.29 | 1542.652 | 220.7961 | 549.2619
2023-09-30 | 10997.556 | 9302.3516 | 1313.7649 | 153.072 | 228.3675 | 23713 | 21787.11 | 917.0429 | 198.5693 | 810.2778
2023-10-31 | 10932.34 | 9206.3755 | 1385.768 | 125.7878 | 214.4087 | 20849 | 18263.33 | 1804.525 | 147.9438 | 633.2012
2023-11-30 | 11456.562 | 9679.0271 | 1398.5566 | 132.3457 | 246.6327 | 20579 | 17750.2 | 1866.194 | 194.518 | 768.088
2023-12-31 | 12065.5 | 10241.9514 | 1447.2337 | 146.7123 | 229.6026 | 20004 | 17492.49 | 1921.522 | 198.1631 | 391.8249
2024-01-31 | 13036.084 | 11101.9147 | 1422.9814 | 144.7408 | 366.4471 | 21081 | 18633 | 1745 | 183 | 520
2024-02-29 | 11516.766 | 9706.5825 | 1363.2675 | 141.9094 | 305.0065 | 19624 | 17059 | 1856 | 158 | 551
2024-03-31 | 11542.29 | 9662.1438 | 1438.1805 | 143.1947 | 298.7711 | 18902 | 16343 | 1919 | 176 | 464
2024-04-30 | 10489.417 | 8729.9908 | 1352.5452 | 150.6011 | 256.2799 | 17947 | 15250 | 1833 | 219 | 645
2024-05-31 | 10735.152 | 8909.3306 | 1386.8118 | 153.3365 | 285.6731 | 20402 | 17955 | 1893 | 137 | 417
2024-06-30 | 11566.905 | 9793.673 | 1359.5387 | 146.7093 | 266.984 | 23803 | 21929 | 1044 | 137 | 693
2024-07-31 | 13072.592 | 11226.5508 | 1335.3985 | 156.2716 | 354.3711 | 23206 | 21321 | 1003 | 155 | 727
2024-08-31 | 12666.051 | 10757.4773 | 1389.3925 | 161.2831 | 357.8981 | 23110 | 21255 | 995 | 149 | 711
2024-09-30 | 11321.751 | 9503.453 | 1328.4107 | 153.2011 | 336.6863 | 21643 | 18979 | 1901 | 147 | 616
2024-10-31 | 10992.867 | 9093.3198 | 1422.713 | 180.517 | 296.3173 | 18117 | 15554 | 1936 | 161 | 466
2024-11-30 | 11312.89 | 9428.8016 | 1419.4526 | 169.3167 | 295.3191 | 19212 | 16505 | 1973 | 175 | 559
2024-12-31 | 12959.601 | 10870.5236 | 1482.7244 | 147.4629 | 458.8901 | 21016 | 18161 | 1987 | 146 | 722
2025-01-31 | 13668.714 | 11640.674 | 1492.7451 | 125.8563 | 409.4386 | 22058 | 19455.51 | 1697.669 | 126.31 | 778.511
2025-02-28 | 12278.547 | 10423.565 | 1347.7547 | 150.2559 | 356.9713 | 21399 | 18634.07 | 1887.744 | 218.4029 | 658.7831
2025-03-31 | 12057.659 | 10104.3239 | 1508.986 | 134.0913 | 310.2578 | 20232 | 17493 | 1979.753 | 136.018 | 623.229
2025-04-30 | 10837.309 | 8985.7009 | 1425.0625 | 120.9368 | 305.6088 | 19271 | 16501.89 | 1894.611 | 136.536 | 737.963
2025-05-31 | 10784.244 | 8828.1414 | 1519.7494 | 135.5994 | 300.7538 | 18190 | 15481.69 | 2102.413 | 146.651 | 459.246
2025-06-30 | 11845.624 | 10083.8169 | 1324.7326 | 141.1828 | 295.8917 | 24775 | 22897.3 | 1081.067 | 115.504 | 681.129
2025-07-31 | 13905.926 | 12037.1718 | 1324.2562 | 155.3669 | 389.131 | 24399 | 22476.48 | 1128.796 | 109.015 | 684.709
2025-08-31 | 12930.485 | 10968.0995 | 1432.9397 | 151.2097 | 378.2361 | 24500 | 22472.56 | 1115.856 | 113.484 | 798.1
2025-09-30 | 11276.887 | 9403.587 | 1395.6112 | 153.5059 | 324.1829 | 19991 | 17458.95 | 1835.465 | 136.7489 | 559.8361
2025-10-31 | 11319.417 | 9397.4939 | 1447.8913 | 142.6134 | 331.4184 | 20310 | 17632.92 | 2070.743 | 105.681 | 500.656
2025-11-30 | 12026.73 | 10055.8108 | 1426.633 | 175.429 | 368.8572 | 19827 | 17341.62 | 1844.312 | 156.969 | 484.099
2025-12-31 | 13676.513 | 11582.5877 | 1419.8029 | 185.5518 | 488.5706 | 21541 | 18858.91 | 1805.179 | 144.107 | 732.804
2026-01-31 | 14011.783 | 11974.7559 | 1447.7435 | 166.4039 | 422.8797 | 22064 | 19398.7 | 1870.507 | 130.535 | 664.258
2026-02-28 | 12373.552 | 10536.084 | 1293.2641 | 188.2235 | 355.9804 | 21821 | 19119.64 | 1918.321 | 144.403 | 638.636
Back to main menu

## Table 1.4.4
Back to main menu
Table 1.4.4: Economic Assumptions
Year | Ontario Employment |  | Ontario Housing Starts |  | Ontario Growth Index
| Thousands | Annual Growth (%) | Thousands | Annual Growth (%) | Index | Annual Growth (%)
2011 | 6647.6 |  | 67.801 |  | 1.0465
2012 | 6685.4083 | 0.56875 | 77.387 | 14.1384 | 1.0572 | 1.0192
2013 | 6790.8917 | 1.5778 | 61.076 | -21.0772 | 1.0715 | 1.3499
2014 | 6823.4 | 0.4787 | 58.587 | -4.0753 | 1.0797 | 0.76876
2015 | 6862.7417 | 0.57657 | 68.997 | 17.7684 | 1.0896 | 0.91341
2016 | 6934.525 | 1.046 | 74.748 | 8.3351 | 1.1026 | 1.1958
2017 | 7109.1917 | 2.5188 | 79.876 | 6.8604 | 1.1243 | 1.9702
2018 | 7240.425 | 1.846 | 79.076 | -1.0016 | 1.1425 | 1.6168
2019 | 7412.8583 | 2.3815 | 68.99 | -12.7548 | 1.1628 | 1.7793
2020 | 7043.45 | -4.9833 | 81.237 | 17.7518 | 1.1413 | -1.8483
2021 | 7404.8167 | 5.1305 | 100.425 | 23.6198 | 1.1802 | 3.4097
2022 | 7764.1 | 4.852 | 95.957 | -4.4491 | 1.2182 | 3.2167
2023 | 8006.1333 | 3.1173 | 89.726 | -6.4935 | 1.2461 | 2.2907
2024 | 8146.1417 | 1.7488 | 74.481 | -16.9906 | 1.2644 | 1.4665
2025 | 8226.9583 | 0.99209 | 65.257 | -12.3844 | 1.2771 | 1.0024
2026 (f) | 8268.7065 | 0.50746 | 64.806 | -0.69111 | 1.2873 | 0.80025
2027 (f) | 8325.2523 | 0.68385 | 68.295 | 5.3838 | 1.299 | 0.91183
Back to main menu

## Table 1.4.5
Back to main menu
Table 1.4.5: Estimate of Contracted Embedded Generation Capacity (MW)
| Biogas | Cogeneration | Solar | Hydro | Wind | Total
2007-01-01 | 0 | 0 | 0 | 129.3052 | 0 | 129.3052
2007-02-01 | 0 | 0 | 0 | 130.66 | 0 | 130.66
2007-03-01 | 0.90726 | 0 | 0 | 130.66 | 0 | 131.5673
2007-04-01 | 5.625 | 0 | 0 | 130.66 | 0.34201 | 136.627
2007-05-01 | 9.0176 | 0 | 0 | 132.86 | 5.3585 | 147.236
2007-06-01 | 12.91 | 0 | 0 | 133.76 | 6.5101 | 153.1801
2007-07-01 | 12.91 | 0 | 0 | 133.869 | 6.5101 | 153.2891
2007-08-01 | 12.91 | 0 | 0.031813 | 134.061 | 6.5101 | 153.5129
2007-09-01 | 13.054 | 0 | 0.051979 | 134.19 | 6.5101 | 153.8061
2007-10-01 | 14.69 | 0 | 0.053184 | 134.19 | 6.631 | 155.5642
2007-11-01 | 15.189 | 0 | 0.063105 | 134.834 | 6.7601 | 156.8462
2007-12-01 | 15.6348 | 0 | 0.14466 | 135.4645 | 6.7601 | 158.0041
2008-01-01 | 16.252 | 0 | 0.21996 | 135.859 | 8.9956 | 161.3265
2008-02-01 | 16.3348 | 0 | 0.22307 | 135.859 | 16.6601 | 169.0769
2008-03-01 | 16.352 | 1.5581 | 0.22542 | 135.859 | 22.7569 | 176.7514
2008-04-01 | 16.352 | 2.3 | 0.25899 | 135.859 | 25.6601 | 180.4301
2008-05-01 | 16.352 | 2.3 | 0.29769 | 135.859 | 25.6601 | 180.4688
2008-06-01 | 16.352 | 6.8 | 0.29769 | 135.859 | 38.2002 | 197.5089
2008-07-01 | 16.352 | 7.3 | 0.304 | 135.859 | 45.4602 | 205.2752
2008-08-01 | 16.352 | 7.3 | 0.30791 | 135.9509 | 45.4602 | 205.371
2008-09-01 | 16.352 | 7.3 | 0.31281 | 136.809 | 46.8352 | 207.609
2008-10-01 | 16.352 | 7.6645 | 0.33243 | 136.809 | 56.2651 | 217.423
2008-11-01 | 17.632 | 18.6 | 0.33409 | 140.209 | 69.2203 | 245.9954
2008-12-01 | 19.552 | 18.7129 | 3.2543 | 140.809 | 73.5103 | 255.8385
2009-01-01 | 19.552 | 22.1 | 11.616 | 140.809 | 73.5103 | 267.5873
2009-02-01 | 19.552 | 22.1 | 11.7447 | 140.809 | 73.5103 | 267.716
2009-03-01 | 19.552 | 22.1 | 11.7722 | 140.809 | 73.549 | 267.7822
2009-04-01 | 19.5981 | 22.1 | 11.774 | 140.809 | 74.1103 | 268.3914
2009-05-01 | 19.898 | 22.1 | 11.7776 | 142.68 | 74.1103 | 270.5658
2009-06-01 | 19.898 | 59.9 | 11.7776 | 146.609 | 74.1103 | 312.2949
2009-07-01 | 19.898 | 85.1 | 11.7776 | 146.609 | 74.1103 | 337.4949
2009-08-01 | 19.898 | 85.1 | 11.7776 | 146.609 | 74.1103 | 337.4949
2009-09-01 | 19.898 | 85.1 | 12.7339 | 147.7423 | 74.1103 | 339.5845
2009-10-01 | 19.898 | 85.1 | 21.3408 | 148.609 | 74.1103 | 349.058
2009-11-01 | 19.898 | 85.1 | 23.5917 | 148.609 | 74.1103 | 351.309
2009-12-01 | 19.898 | 85.1 | 33.2809 | 148.8671 | 87.5426 | 374.6885
2010-01-01 | 19.898 | 96.8 | 47.3343 | 189.759 | 104.9039 | 458.6952
2010-02-01 | 19.898 | 96.8 | 53.8468 | 190.281 | 120.7104 | 481.5363
2010-03-01 | 19.898 | 96.8 | 53.8468 | 202.197 | 120.7104 | 493.4523
2010-04-01 | 23.7224 | 96.8 | 53.8468 | 223.2703 | 120.7104 | 518.35
2010-05-01 | 26.977 | 96.8 | 53.8468 | 239.197 | 142.746 | 559.5668
2010-06-01 | 26.977 | 96.8 | 53.8629 | 240.3126 | 160.3106 | 578.2631
2010-07-01 | 28.2931 | 96.8 | 64.8303 | 240.7634 | 160.3106 | 590.9974
2010-08-01 | 33.8764 | 96.8 | 104.3249 | 240.815 | 160.3106 | 636.1268
2010-09-01 | 38.9911 | 96.8 | 121.7581 | 241.505 | 160.3106 | 659.3648
2010-10-01 | 39.224 | 96.8 | 130.6526 | 243.47 | 162.4138 | 672.5603
2010-11-01 | 39.224 | 96.8 | 151.1879 | 243.62 | 175.1106 | 705.9425
2010-12-01 | 39.224 | 96.8 | 166.5989 | 244.22 | 186.9171 | 733.7599
2011-01-01 | 40.1763 | 96.8 | 195.2485 | 248.52 | 204.3365 | 785.0812
2011-02-01 | 40.864 | 96.8 | 209.3405 | 248.52 | 221.1107 | 816.6352
2011-03-01 | 40.864 | 96.8 | 215.1702 | 249.638 | 221.1107 | 823.5829
2011-04-01 | 40.864 | 96.8 | 223.6972 | 249.638 | 221.1107 | 832.1099
2011-05-01 | 40.9608 | 96.8 | 226.8121 | 249.638 | 234.014 | 848.2249
2011-06-01 | 40.964 | 96.8 | 230.5228 | 250.758 | 241.1108 | 860.1556
2011-07-01 | 40.964 | 96.8 | 262.2795 | 250.758 | 241.1108 | 891.9123
2011-08-01 | 40.964 | 96.8 | 289.5469 | 250.758 | 241.1108 | 919.1797
2011-09-01 | 40.9889 | 96.8 | 317.93 | 250.758 | 241.1108 | 947.5877
2011-10-01 | 41.338 | 96.8 | 325.5028 | 250.758 | 241.1108 | 955.5096
2011-11-01 | 41.363 | 96.8 | 330.6216 | 251.223 | 241.1108 | 961.1184
2011-12-01 | 41.6799 | 96.8 | 359.6279 | 251.223 | 241.1108 | 990.4416
2012-01-01 | 44.4734 | 96.8 | 378.2799 | 251.223 | 242.8527 | 1013.629
2012-02-01 | 44.575 | 96.8 | 384.5041 | 251.223 | 250.1108 | 1027.213
2012-03-01 | 44.575 | 96.8 | 442.107 | 251.223 | 265.9625 | 1100.6675
2012-04-01 | 45.8414 | 96.8 | 463.5679 | 251.223 | 287.9109 | 1145.3432
2012-05-01 | 46.4559 | 96.8 | 490.28 | 251.223 | 293.3948 | 1178.1537
2012-06-01 | 47.5397 | 96.8 | 521.2308 | 251.223 | 297.911 | 1214.7045
2012-07-01 | 48.4584 | 96.8 | 526.8559 | 251.223 | 297.911 | 1221.2482
2012-08-01 | 49.1175 | 96.8 | 538.457 | 251.473 | 297.911 | 1233.7585
2012-09-01 | 49.728 | 96.8 | 547.7075 | 251.473 | 301.511 | 1247.2195
2012-10-01 | 49.8409 | 96.8 | 558.4193 | 251.473 | 301.911 | 1258.4442
2012-11-01 | 49.978 | 96.8 | 577.3481 | 251.473 | 301.911 | 1277.5101
2012-12-01 | 50.3167 | 96.8 | 589.1998 | 251.473 | 310.8142 | 1298.6037
2013-01-01 | 51.5379 | 96.8 | 605.9954 | 252.048 | 327.8143 | 1334.1956
2013-02-01 | 54.923 | 96.8 | 649.91 | 254.0123 | 334.9111 | 1390.5563
2013-03-01 | 54.923 | 96.8 | 710.9791 | 259.6581 | 334.9111 | 1457.2713
2013-04-01 | 55.172 | 96.8 | 746.9822 | 260.051 | 334.9111 | 1493.9163
2013-05-01 | 56.6655 | 96.8 | 765.6521 | 265.551 | 334.9111 | 1519.5797
2013-06-01 | 58.1607 | 96.8 | 797.9923 | 271.451 | 334.9111 | 1559.3151
2013-07-01 | 58.269 | 96.8 | 833.6291 | 274.9494 | 334.9111 | 1598.5586
2013-08-01 | 58.269 | 96.8 | 857.21 | 279.901 | 334.9111 | 1627.0911
2013-09-01 | 58.269 | 96.8 | 883.7393 | 280.501 | 334.9111 | 1654.2204
2013-10-01 | 58.4625 | 96.8 | 907.9225 | 285.4687 | 335.0401 | 1683.6939
2013-11-01 | 58.519 | 96.9167 | 917.6386 | 292.601 | 335.4111 | 1701.0864
2013-12-01 | 58.519 | 97.006 | 956.7308 | 292.601 | 335.4111 | 1740.2679
2014-01-01 | 63.76 | 97.006 | 996.6295 | 292.601 | 335.4111 | 1785.4076
2014-02-01 | 68.017 | 97.006 | 1052.981 | 292.601 | 339.9111 | 1850.5161
2014-03-01 | 72.017 | 97.006 | 1131.5585 | 292.601 | 368.5134 | 1961.6959
2014-04-01 | 74.2035 | 97.006 | 1166.2717 | 292.601 | 371.4172 | 2001.4995
2014-05-01 | 74.869 | 97.006 | 1192.1372 | 292.601 | 371.4172 | 2028.0304
2014-06-01 | 74.869 | 97.006 | 1208.0346 | 292.601 | 373.4172 | 2045.9278
2014-07-01 | 74.869 | 97.006 | 1228.7427 | 294.251 | 381.4172 | 2076.2859
2014-08-01 | 74.9013 | 97.006 | 1281.9536 | 294.251 | 386.9218 | 2135.0336
2014-09-01 | 75.119 | 97.006 | 1325.7176 | 294.251 | 395.8973 | 2187.9909
2014-10-01 | 75.119 | 97.006 | 1406.5719 | 294.251 | 410.8993 | 2283.8472
2014-11-01 | 75.119 | 97.006 | 1471.3142 | 294.251 | 415.6827 | 2353.3729
2014-12-01 | 75.119 | 97.006 | 1508.8385 | 294.251 | 425.2494 | 2400.4638
2015-01-01 | 75.119 | 97.006 | 1534.8037 | 294.251 | 425.2494 | 2426.4291
2015-02-01 | 75.119 | 97.006 | 1590.2363 | 294.251 | 425.2494 | 2481.8616
2015-03-01 | 75.119 | 97.006 | 1635.3113 | 294.251 | 425.2494 | 2526.9366
2015-04-01 | 75.269 | 97.006 | 1661.6364 | 294.251 | 425.2494 | 2553.4118
2015-05-01 | 75.369 | 97.006 | 1678.9824 | 294.251 | 425.2494 | 2570.8577
2015-06-01 | 86.6499 | 97.006 | 1702.0977 | 301.513 | 429.7494 | 2617.016
2015-07-01 | 93.7858 | 97.006 | 1725.7316 | 304.762 | 449.5398 | 2670.8252
2015-08-01 | 93.931 | 97.006 | 1747.3995 | 312.373 | 470.714 | 2721.4235
2015-09-01 | 93.931 | 97.006 | 1776.4149 | 312.373 | 483.5495 | 2763.2745
2015-10-01 | 101.1052 | 97.006 | 1800.8333 | 312.373 | 483.5495 | 2794.867
2015-11-01 | 108.049 | 99.4861 | 1828.845 | 312.373 | 483.5495 | 2832.3027
2015-12-01 | 108.966 | 100.922 | 1862.1998 | 313.9214 | 485.0044 | 2871.0135
2016-01-01 | 108.966 | 100.922 | 1873.9655 | 313.973 | 487.6495 | 2885.476
2016-02-01 | 108.966 | 100.922 | 1880.6538 | 313.973 | 489.0289 | 2893.5437
2016-03-01 | 108.966 | 100.922 | 1888.5229 | 313.973 | 497.6496 | 2910.0335
2016-04-01 | 108.966 | 100.922 | 1895.2354 | 313.973 | 497.6496 | 2916.7459
2016-05-01 | 108.966 | 100.922 | 1898.972 | 313.973 | 512.4121 | 2935.2451
2016-06-01 | 108.966 | 100.922 | 1901.0536 | 313.973 | 515.2511 | 2940.1657
2016-07-01 | 108.966 | 100.922 | 1906.6903 | 313.973 | 515.2511 | 2945.8024
2016-08-01 | 109.1621 | 100.922 | 1916.1575 | 313.973 | 515.2511 | 2955.4657
2016-09-01 | 109.346 | 100.922 | 1932.2473 | 313.973 | 521.4011 | 2977.8894
2016-10-01 | 109.3541 | 100.922 | 1940.6332 | 313.973 | 542.4126 | 3007.2948
2016-11-01 | 109.596 | 100.922 | 1948.1572 | 313.973 | 553.9032 | 3026.5514
2016-12-01 | 109.596 | 100.922 | 1956.2489 | 314.038 | 569.1226 | 3049.9275
2017-01-01 | 109.596 | 100.922 | 1960.8591 | 314.038 | 571.7032 | 3057.1183
2017-02-01 | 109.596 | 100.922 | 1965.8379 | 314.038 | 571.7032 | 3062.0972
2017-03-01 | 109.596 | 103.1546 | 1973.0946 | 314.038 | 571.7032 | 3071.5864
2017-04-01 | 109.596 | 104.767 | 1988.9948 | 314.038 | 578.6372 | 3096.033
2017-05-01 | 109.596 | 105.0799 | 2002.7135 | 314.3138 | 579.962 | 3111.6652
2017-06-01 | 109.596 | 108 | 2007.9013 | 315.2713 | 580.2039 | 3120.9725
2017-07-01 | 109.596 | 108 | 2009.7802 | 315.488 | 580.2039 | 3123.0681
2017-08-01 | 109.596 | 109.1472 | 2012.9963 | 328.7428 | 580.2039 | 3140.6863
2017-09-01 | 109.596 | 111.233 | 2018.8565 | 344.838 | 580.2039 | 3164.7274
2017-10-01 | 109.596 | 111.233 | 2023.9425 | 344.838 | 580.2039 | 3169.8134
2017-11-01 | 109.596 | 111.4908 | 2029.5095 | 344.838 | 587.7212 | 3183.1555
2017-12-01 | 109.596 | 113.811 | 2033.6045 | 344.838 | 590.4548 | 3192.3043
2018-01-01 | 109.596 | 113.811 | 2039.7298 | 344.838 | 590.4548 | 3198.4296
2018-02-01 | 109.596 | 113.811 | 2048.0224 | 344.838 | 590.4548 | 3206.7222
2018-03-01 | 109.596 | 113.811 | 2056.2911 | 344.838 | 590.4548 | 3214.9909
2018-04-01 | 109.7793 | 113.811 | 2060.9914 | 344.838 | 590.4548 | 3219.8745
2018-05-01 | 109.846 | 113.811 | 2063.6322 | 344.838 | 590.4548 | 3222.582
2018-06-01 | 109.846 | 113.811 | 2070.0079 | 344.838 | 590.4548 | 3228.9577
2018-07-01 | 110.0718 | 113.811 | 2077.1555 | 344.838 | 590.4548 | 3236.3311
2018-08-01 | 110.596 | 113.811 | 2090.4804 | 344.838 | 590.4548 | 3250.1802
2018-09-01 | 110.671 | 113.811 | 2098.359 | 344.838 | 590.4548 | 3258.1338
2018-10-01 | 110.846 | 113.811 | 2104.2416 | 344.838 | 590.4548 | 3264.1914
2018-11-01 | 110.941 | 113.811 | 2104.8686 | 344.838 | 590.4548 | 3264.9134
2018-12-01 | 111.196 | 113.811 | 2105.7477 | 344.838 | 590.4548 | 3266.0475
2019-01-01 | 111.196 | 113.811 | 2128.1496 | 347.438 | 590.4548 | 3291.0494
2019-02-01 | 111.196 | 113.811 | 2138.3452 | 347.438 | 590.4548 | 3301.245
2019-03-01 | 111.446 | 113.811 | 2145.193 | 347.438 | 590.4548 | 3308.3428
2019-04-01 | 111.6627 | 115.263 | 2148.4854 | 347.438 | 590.4548 | 3313.3039
2019-05-01 | 111.9299 | 115.791 | 2150.6741 | 347.438 | 590.4548 | 3316.2878
2019-06-01 | 111.946 | 115.791 | 2152.1248 | 347.438 | 590.4548 | 3317.7546
2019-07-01 | 111.946 | 115.791 | 2153.0123 | 347.438 | 590.4548 | 3318.6421
2019-08-01 | 111.9702 | 115.791 | 2154.7448 | 347.438 | 590.4548 | 3320.3988
2019-09-01 | 112.3043 | 116.883 | 2157.8404 | 347.438 | 590.4548 | 3324.9205
2019-10-01 | 112.446 | 118.521 | 2158.9011 | 347.438 | 590.4548 | 3327.7609
2019-11-01 | 112.446 | 118.521 | 2160.0341 | 347.438 | 590.4548 | 3328.8939
2019-12-01 | 112.446 | 118.521 | 2160.2149 | 347.438 | 590.4548 | 3329.0747
2020-01-01 | 112.446 | 118.521 | 2160.2149 | 347.438 | 590.4548 | 3329.0747
2020-02-01 | 112.446 | 119.4101 | 2160.2149 | 347.438 | 590.4548 | 3329.9639
2020-03-01 | 112.446 | 123.678 | 2160.2835 | 350.5348 | 590.4548 | 3337.3971
2020-04-01 | 112.446 | 123.678 | 2160.7462 | 351.438 | 590.4548 | 3338.763
2020-05-01 | 112.446 | 123.678 | 2160.7462 | 351.438 | 590.4548 | 3338.763
2020-06-01 | 112.446 | 136.4009 | 2160.7462 | 351.438 | 590.4548 | 3351.4859
2020-07-01 | 112.446 | 151.465 | 2160.7462 | 351.438 | 590.4548 | 3366.55
2020-08-01 | 112.446 | 151.465 | 2160.7462 | 351.438 | 590.4548 | 3366.55
2020-09-01 | 112.446 | 151.465 | 2160.7689 | 351.438 | 590.4548 | 3366.5727
2020-10-01 | 112.6799 | 151.465 | 2165.9933 | 351.438 | 590.4548 | 3372.031
2020-11-01 | 112.696 | 151.465 | 2168.3075 | 356.288 | 590.4548 | 3379.2113
2020-12-01 | 112.696 | 151.465 | 2168.3075 | 356.8364 | 590.4548 | 3379.7597
2021-01-01 | 112.696 | 151.465 | 2170.1708 | 373.288 | 590.4548 | 3398.0746
2021-02-01 | 112.696 | 151.465 | 2170.4665 | 373.288 | 590.4548 | 3398.3703
2021-03-01 | 112.696 | 151.465 | 2170.4665 | 373.288 | 590.4548 | 3398.3703
2021-04-01 | 112.696 | 151.465 | 2170.4665 | 373.288 | 590.4548 | 3398.3703
2021-05-01 | 112.696 | 151.465 | 2170.4665 | 393.3203 | 590.4548 | 3418.4026
2021-06-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-07-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-08-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-09-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-10-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-11-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2021-12-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-01-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-02-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-03-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-04-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-05-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-06-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-07-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-08-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-09-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-10-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-11-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2022-12-01 | 112.696 | 151.465 | 2170.4665 | 400.288 | 590.4548 | 3425.3703
2023-01-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-02-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-03-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-04-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-05-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-06-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-07-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-08-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-09-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-10-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-11-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2023-12-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2024-01-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2024-02-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2024-03-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2024-04-01 | 112.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3435.3703
2024-05-01 | 117.3412 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3440.0155
2024-06-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-07-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-08-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-09-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-10-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-11-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2024-12-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-01-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-02-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-03-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-04-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-05-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-06-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-07-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-08-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-09-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-10-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-11-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2025-12-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-01-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-02-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-03-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-04-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-05-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-06-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-07-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-08-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-09-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-10-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-11-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2026-12-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-01-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-02-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-03-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-04-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-05-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-06-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-07-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-08-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
2027-09-01 | 120.696 | 151.465 | 2170.4665 | 410.288 | 590.4548 | 3443.3703
Back to main menu

## Table 2.1
Back to main menu
Table 2.1: Existing Grid-Connected Resource Capacity
Fuel Type | Total Installed Capacity (MW) | Forecast Capability at 2026 Summer Peak [Firm] (MW) | Forecast Capability at 2026 Summer Peak [Planned] (MW) | Number of Stations | Change in Number of Stations | Change in Installed Capacity (MW)
Nuclear | 12184.2 | 10363 | 10363 | 4 | 0 | 0
Hydroelectric | 8865.9044 | 5406.0808 | 5406.0808 | 76 | 0 | 0
Gas/Oil | 10550.7233 | 9838.5767 | 9915.1767 | 30 | 0 | 0
Wind | 4942.811 | 735.454 | 735.454 | 42 | 0 | 0
Biofuel | 286.8 | 205 | 205 | 4 | 0 | 0
Solar | 478.04 | 65.851 | 65.851 | 10 | 0 | 0
Storage | 451.247 | 570.479 | 825.965 | 4 | 0 | 0
Demand Measures | - | 1088.4245 | 1088.4245 | - | - | -
Firm Imports (+) / Exports (-) (MW) | - | 900 | 900 | - | - | -
Total | 37759.7257 | 29172.8659 | 29504.9519 | 170 | 0 | 0
Back to main menu

## Table 2.2
Back to main menu
Table 2.2: Committed Generation and Electricity Storage Resources Status over the 18-month Reliability Outlook Period
|  |  | Estimated |  | Capacity Considered
Project Name | Zone | Fuel Type | Effective Date | Project Status | Firm (MW) | Planned (MW)
Same Technology Upgrade (STU) Projects | Ontario | Gas | 2026-Q1 to Q2 | Commercial Operation | 23 | 142
Brighton Beach Upgrade | West | Gas | 2026-Q1 | Commercial Operation | 43 | 43
Expedited Long-Term 1 (E-LT1) Projects | Various | Various | 2025-Q4 to 2026-Q1 | Commercial Operation | 593 | 593
Expedited Long-Term 1 (E-LT1) Projects | Various | Various | 2026-Q1 to Q4 | Under Development | 0 | 471
Long-Term 1 (LT1) Projects (within next 18-months) | Various | Various | 2026-Q2 | Under Development | 0 | 32.28
Pickering B | Toronto | Nuclear | 2026-Q4 | Facility OOS | -2064 | -2064
Total |  |  |  |  | -1405 | -783
Back to main menu

## Table 2.3
Back to main menu
Table 2.3: Monthly Historical Hydroelectric Median Values for Expected Weather Conditions
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Historical Hydroelectric Median Contribution (MW) | 6067.522 | 5995.3981 | 5786.458 | 5857.7321 | 5929.2001 | 5647.3216 | 5516.2125 | 5216.289 | 4999.8535 | 5330.9398 | 5603.9885 | 6076.1939
Historical Hydroelectric Median Contribution without Outages (MW) | 6609.5164 | 6569.6292 | 6366.0623 | 6388.7289 | 6382.953 | 6189.814 | 6088.2378 | 5867.2897 | 5909.5059 | 6179.6674 | 6392.6176 | 6580.022
Back to main menu

## Table 2.4
Back to main menu
Table 2.4: Monthly Wind Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Wind Capacity Contribution (% of Installed Capacity) | 39.89% | 39.89% | 40.78% | 29.47% | 21.3% | 14.88% | 14.88% | 14.88% | 16.21% | 31.18% | 39.09% | 39.89%
Back to main menu

## Table 2.5
Back to main menu
Table 2.5: Monthly Solar Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Solar Capacity Contribution (% of Installed Capacity) | 0% | 0% | 0.1592% | 1.159% | 2.727% | 13.78% | 13.78% | 13.78% | 8.456% | 2.223% | 0% | 0%
Back to main menu

## Table 2.6
Back to main menu
Table 2.6: Monthly Off-Peak Wind Capacity Contribution Values
Month | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Off-Peak WCC (% of Installed Capacity) | 41.3% | 41.3% | 41.6% | 33.5% | 27.9% | 17% | 17% | 17% | 20.3% | 33.9% | 40.4% | 41.3%
Back to main menu

## Table 2.7
Back to main menu
Table 2.7: Summary of Available Resources under Expected Weather
| Description [Normal] | Summer Peak 2026 |  | Winter Peak 2027 |  | Summer Peak 2027
# |  | Firm Scenario | Planned Scenario | Firm Scenario | Planned Scenario | Firm Scenario | Planned Scenario
1 | Installed Resources (MW) | 38418.5 | 38901.48 | 36354.5 | 36953.46 | 36354.5 | 36953.46
2 | Total Reductions in Resources (MW) | 11243 | 11394 | 10985 | 11283 | 12573 | 12756
3 | Demand Measures (MW) | 1088.4245 | 1088.4245 | 715.7142 | 715.7142 | 2041.4667 | 2041.4667
4 | Firm Imports (+) / Exports (-) (MW) | 900 | 900 | 0 | 0 | 0 | 0
5 | Available Resources (MW) | 29163.9245 | 29495.9045 | 26085.2143 | 26386.1743 | 25822.9667 | 26238.9267
6 | Bottling | 8.5942 | 8.5942 | 501.794 | 559.794 | 0 | 0
7 | Available Resources without Bottling (MW) | 29172.5187 | 29504.4987 | 26587.0082 | 26945.9682 | 25822.9667 | 26238.9267
Back to main menu

## Table 3.1
Back to main menu
Table 3.1 Firm: Summary of Zonal Energy for Firm Scenario, Expected Weather
| 18-Month Energy Demand |  | 18-Month Energy Production |  | Net Inter-Zonal Energy Transfer | Zonal Energy Demand on Peak Day of 18-Month Period | Available Energy on Peak Day of 18 Month Period
| TWh | Average MW | TWh | Average MW | TWh | GWh | GWh
Ontario | 219 | 16654 | 219.4 | 16685 | 0.4 | 489.4 | 7.6
Bruce | 1.1 | 82 | 65.4 | 4974 | 64.3 | 1.8 | 0.1
East | 13.2 | 1005 | 26.1 | 1986 | 12.9 | 28.7 | 0.6
Essa | 15.6 | 1183 | 5.9 | 447 | -9.7 | 35.5 | 0.1
Niagara | 8.6 | 653 | 21.8 | 1657 | 13.2 | 18.3 | 0.7
Northeast | 16.6 | 1265 | 14.8 | 1124 | -1.8 | 29.9 | 0.2
Northwest | 5 | 378 | 6.9 | 526 | 1.9 | 9.5 | 0.1
Ottawa | 13.4 | 1016 | 0.9 | 65 | -12.5 | 31.7 | 0.4
Southwest | 44.7 | 3399 | 11.3 | 858 | -33.4 | 97.9 | 2.6
Toronto | 77.1 | 5863 | 43.9 | 3335 | -33.2 | 184.6 | 2.4
West | 23.8 | 1809 | 22.5 | 1713 | -1.3 | 51.5 | 0.4
Back to main menu

## Table 3.2
Back to main menu
Table 3.2 Planned: Summary of Zonal Energy for Planned Scenario, Expected Weather
| 18-Month Energy Demand |  | 18-Month Energy Production |  | Net Inter-Zonal Energy Transfer | Zonal Energy Demand on Peak Day of 18-Month Period | Available Energy on Peak Day of 18 Month Period
| TWh | Average MW | TWh | Average MW | TWh | GWh | GWh
Ontario | 219 | 16653 | 219.4 | 16685 | 0.4 | 489.4 | 604.2
Bruce | 1.1 | 82 | 65.4 | 4974 | 64.3 | 1.8 | 138.2
East | 13.2 | 1006 | 25.8 | 1958 | 12.6 | 28.7 | 93.7
Essa | 15.6 | 1183 | 5.8 | 441 | -9.8 | 35.5 | 18.4
Niagara | 8.6 | 653 | 21.8 | 1656 | 13.2 | 18.3 | 49.1
Northeast | 16.6 | 1265 | 14.8 | 1123 | -1.8 | 29.9 | 35.9
Northwest | 5 | 378 | 6.9 | 526 | 1.9 | 9.5 | 19.6
Ottawa | 13.4 | 1016 | 0.9 | 65 | -12.5 | 31.7 | 1.4
Southwest | 44.7 | 3397 | 11.2 | 855 | -33.5 | 97.9 | 22.3
Toronto | 77.1 | 5863 | 43.9 | 3339 | -33.2 | 184.6 | 140.7
West | 23.8 | 1808 | 23 | 1748 | -0.8 | 51.5 | 84.8
Back to main menu

## Table 3.3
Back to main menu
Table 3.3 Firm: Ontario Energy Production by Fuel Type for the Firm Scenario, Expected Weather
Fuel Type (Grid Connected) | 2026 | 2027 (January 1 - September 30) | Total
Nuclear (GWh) | 57228.83 | 43165.18 | 100394.01
Hydro (GWh) | 26947.98 | 27453.95 | 54401.93
Gas & Oil (GWh) | 15356.87 | 30434.79 | 45791.66
Wind (GWh) | 8205.78 | 9004.2 | 17209.98
Bio Fuel (GWh) | 293.18 | 324.32 | 617.5
Other (GWh) | 423.6 | 600.48 | 1024.08
Total (GWh) | 108456.24 | 110982.92 | 219439.16
Back to main menu

## Table 3.4
Back to main menu
Table 3.4 Planned: Ontario Energy Production by Fuel Type for the Planned Scenario, Expected Weather
Fuel Type (Grid Connected) | 2026 | 2027 (January 1 - September 30) | Total
Nuclear (GWh) | 57229.39 | 43165.18 | 100394.57
Hydro (GWh) | 26948.27 | 27453.89 | 54402.16
Gas & Oil (GWh) | 15356.3 | 30457.46 | 45813.76
Wind (GWh) | 8206.29 | 9003.51 | 17209.8
Bio Fuel (GWh) | 292.04 | 321.14 | 613.18
Other (GWh) | 420.7 | 584.71 | 1005.41
Total (GWh) | 108452.99 | 110985.89 | 219438.88
Back to main menu

## Table 3.5
Back to main menu
Table 3.5: Assessment of Resource Adequacy: Expected Weather, Firm Scenario
Week | Ontario | Total Installed | Total Reductions | Demand | Firm Imports (+) | Total Available | Required | Available | Available | Required | Required | Reserve Above
Ending | Demand | Capacity | in Resources | Measures | Exports (-) | Resources | Resources | Reserve | Reserve | Reserve | Reserve | Requirement
Day | MW | MW | MW | MW | MW | MW | MW | % | MW | % | MW | MW
2026-04-05 | 18385 | 38418.5 | 12690 | 817.8227 | -612.9 | 25933.4227 | 22359 | 41.06 | 7548 | 21.62 | 3974 | 3574
2026-04-12 | 17954 | 38418.5 | 13616 | 817.8227 | -612.9 | 25007.4227 | 21704 | 39.28 | 7053 | 20.89 | 3750 | 3303
2026-04-19 | 17704 | 38418.5 | 14134 | 817.8227 | -612.9 | 24489.4227 | 21308 | 38.32 | 6785 | 20.36 | 3604 | 3181
2026-04-26 | 17441 | 38418.5 | 14538 | 817.8227 | -612.9 | 24085.4227 | 21083 | 38.09 | 6644 | 20.88 | 3642 | 3002
2026-05-03 | 17226 | 38418.5 | 14625 | 817.8227 | -612.9 | 23998.4227 | 20888 | 39.31 | 6772 | 21.26 | 3662 | 3110
2026-05-10 | 17258 | 38418.5 | 13653 | 897.3554 | 600 | 25662.8554 | 21476 | 48.7 | 8405 | 24.44 | 4218 | 4187
2026-05-17 | 17349 | 38418.5 | 15282 | 897.3554 | 600 | 24033.8554 | 21625 | 38.53 | 6685 | 24.65 | 4276 | 2409
2026-05-24 | 17954 | 38418.5 | 13724 | 897.3554 | 600 | 25591.8554 | 22993 | 42.54 | 7638 | 28.07 | 5039 | 2599
2026-05-31 | 18428 | 38418.5 | 13201 | 897.3554 | 600 | 26114.8554 | 25830 | 41.71 | 7687 | 40.17 | 7402 | 285
2026-06-07 | 19256 | 38418.5 | 14344 | 1088.4245 | 900 | 25162.9245 | 26522 | 30.68 | 5907 | 37.73 | 7266 | -1359
2026-06-14 | 19718 | 38418.5 | 12564 | 1088.4245 | 900 | 26942.9245 | 26808 | 36.64 | 7225 | 35.96 | 7090 | 135
2026-06-21 | 20835 | 38418.5 | 12700 | 1088.4245 | 900 | 26806.9245 | 27202 | 28.66 | 5972 | 30.56 | 6367 | -395
2026-06-28 | 21712 | 38418.5 | 12166 | 1138.4245 | 900 | 27390.9245 | 27278 | 26.16 | 5679 | 25.64 | 5566 | 113
2026-07-05 | 21685 | 38418.5 | 12123 | 1088.4245 | 900 | 27383.9245 | 27740 | 26.28 | 5699 | 27.92 | 6055 | -356
2026-07-12 | 22386 | 38418.5 | 11121 | 1088.4245 | 900 | 28385.9245 | 28450 | 26.8 | 6000 | 27.09 | 6064 | -64
2026-07-19 | 22526 | 38418.5 | 11222 | 1088.4245 | 900 | 28284.9245 | 28484 | 25.57 | 5759 | 26.45 | 5958 | -199
2026-07-26 | 22545 | 38418.5 | 11243 | 1088.4245 | 900 | 28263.9245 | 28483 | 25.37 | 5719 | 26.34 | 5938 | -219
2026-08-02 | 22294 | 38418.5 | 11222 | 1088.4245 | 900 | 28284.9245 | 28242 | 26.87 | 5991 | 26.68 | 5948 | 43
2026-08-09 | 21765 | 38418.5 | 11522 | 1088.4245 | 900 | 27984.9245 | 27957 | 28.58 | 6220 | 28.45 | 6192 | 28
2026-08-16 | 21817 | 38418.5 | 11723 | 1088.4245 | 900 | 27783.9245 | 27403 | 27.35 | 5967 | 25.6 | 5586 | 381
2026-08-23 | 21657 | 38418.5 | 12023 | 1088.4245 | 900 | 27483.9245 | 26599 | 26.91 | 5827 | 22.82 | 4942 | 885
2026-08-30 | 21528 | 38418.5 | 12177 | 1088.4245 | 900 | 27329.9245 | 26264 | 26.95 | 5802 | 22 | 4736 | 1066
2026-09-06 | 21099 | 38418.5 | 11770 | 1088.4245 | 900 | 27736.9245 | 27017 | 31.46 | 6638 | 28.05 | 5918 | 720
2026-09-13 | 19902 | 38418.5 | 11715 | 1088.4245 | 900 | 27791.9245 | 26698 | 39.64 | 7890 | 34.15 | 6796 | 1094
2026-09-20 | 19409 | 38418.5 | 12381 | 1088.4245 | 900 | 27125.9245 | 25679 | 39.76 | 7717 | 32.3 | 6270 | 1447
2026-09-27 | 18840 | 38418.5 | 14333 | 1088.4245 | 900 | 25173.9245 | 24856 | 33.62 | 6334 | 31.93 | 6016 | 318
2026-10-04 | 18735 | 36354.5 | 14054 | 1088.4245 | 900 | 23388.9245 | 23481 | 24.84 | 4654 | 25.33 | 4746 | -92
2026-10-11 | 18023 | 36354.5 | 16374 | 897.3554 | 600 | 20877.8554 | 22202 | 15.84 | 2855 | 23.19 | 4179 | -1324
2026-10-18 | 17959 | 36354.5 | 15252 | 897.3554 | 600 | 21999.8554 | 21757 | 22.5 | 4041 | 21.15 | 3798 | 243
2026-10-25 | 18280 | 36354.5 | 15330 | 897.3554 | 600 | 21921.8554 | 21698 | 19.92 | 3642 | 18.7 | 3418 | 224
2026-11-01 | 18587 | 36354.5 | 14389 | 897.3554 | 600 | 22862.8554 | 22206 | 23.01 | 4276 | 19.47 | 3619 | 657
2026-11-08 | 19120 | 36354.5 | 13773 | 828.4437 | 0 | 23409.9437 | 22621 | 22.44 | 4290 | 18.31 | 3501 | 789
2026-11-15 | 19620 | 36354.5 | 12433 | 828.4437 | 0 | 24749.9437 | 23721 | 26.15 | 5130 | 20.9 | 4101 | 1029
2026-11-22 | 20177 | 36354.5 | 11637 | 828.4437 | 0 | 25545.9437 | 24278 | 26.61 | 5369 | 20.33 | 4101 | 1268
2026-11-29 | 20753 | 36354.5 | 11337 | 828.4437 | 0 | 25845.9437 | 24757 | 24.54 | 5093 | 19.29 | 4004 | 1089
2026-12-06 | 21047 | 36354.5 | 11419 | 828.4437 | 0 | 25763.9437 | 24987 | 22.41 | 4717 | 18.72 | 3940 | 777
2026-12-13 | 21392 | 36354.5 | 10886 | 828.4437 | 0 | 26296.9437 | 25415 | 22.93 | 4905 | 18.81 | 4023 | 882
2026-12-20 | 21607 | 36354.5 | 10947 | 828.4437 | 0 | 26235.9437 | 25611 | 21.42 | 4629 | 18.53 | 4004 | 625
2026-12-27 | 21046 | 36354.5 | 10640 | 828.4437 | 0 | 26542.9437 | 25377 | 26.12 | 5497 | 20.58 | 4331 | 1166
2027-01-03 | 21262 | 36354.5 | 9971 | 828.4437 | 0 | 27211.9437 | 25887 | 27.98 | 5950 | 21.75 | 4625 | 1325
2027-01-10 | 22006 | 36354.5 | 10985 | 715.7142 | 0 | 26085.2143 | 26400 | 18.54 | 4079 | 19.97 | 4394 | -315
2027-01-17 | 21899 | 36354.5 | 11660 | 737.9142 | 0 | 25432.4143 | 25931 | 16.13 | 3533 | 18.41 | 4032 | -499
2027-01-24 | 21975 | 36354.5 | 11540 | 715.7142 | 0 | 25530.2143 | 26168 | 16.18 | 3555 | 19.08 | 4193 | -638
2027-01-31 | 21958 | 36354.5 | 11631 | 715.7142 | 0 | 25439.2143 | 26050 | 15.85 | 3481 | 18.64 | 4092 | -611
2027-02-07 | 21395 | 36354.5 | 12035 | 828.4437 | 0 | 25147.9437 | 25374 | 17.54 | 3753 | 18.6 | 3979 | -226
2027-02-14 | 21351 | 36354.5 | 11873 | 828.4437 | 0 | 25309.9437 | 25345 | 18.54 | 3959 | 18.71 | 3994 | -35
2027-02-21 | 21027 | 36354.5 | 11686 | 828.4437 | 0 | 25496.9437 | 25192 | 21.26 | 4470 | 19.81 | 4165 | 305
2027-02-28 | 20973 | 36354.5 | 11851 | 828.4437 | 0 | 25331.9437 | 24972 | 20.78 | 4359 | 19.07 | 3999 | 360
2027-03-07 | 20446 | 36354.5 | 11570 | 828.4437 | 0 | 25612.9437 | 24634 | 25.27 | 5167 | 20.48 | 4188 | 979
2027-03-14 | 19989 | 36354.5 | 11570 | 828.4437 | 0 | 25612.9437 | 24177 | 28.14 | 5624 | 20.95 | 4188 | 1436
2027-03-21 | 19492 | 36354.5 | 11860 | 828.4437 | 0 | 25322.9437 | 23554 | 29.91 | 5831 | 20.84 | 4062 | 1769
2027-03-28 | 19050 | 36354.5 | 11753 | 828.4437 | 0 | 25429.9437 | 23210 | 33.49 | 6380 | 21.84 | 4160 | 2220
2027-04-04 | 18553 | 36354.5 | 12720 | 828.4437 | 0 | 24462.9437 | 22064 | 31.85 | 5910 | 18.92 | 3511 | 2399
2027-04-11 | 18274 | 36354.5 | 13033 | 828.4437 | 0 | 24149.9437 | 21737 | 32.15 | 5876 | 18.95 | 3463 | 2413
2027-04-18 | 17958 | 36354.5 | 16665 | 828.4437 | 0 | 20517.9437 | 20946 | 14.26 | 2560 | 16.64 | 2988 | -428
2027-04-25 | 17667 | 36354.5 | 16598 | 828.4437 | 0 | 20584.9437 | 20688 | 16.52 | 2918 | 17.1 | 3021 | -103
2027-05-02 | 17449 | 36354.5 | 14329 | 828.4437 | 0 | 22853.9437 | 20731 | 30.98 | 5405 | 18.81 | 3282 | 2123
2027-05-09 | 17474 | 36354.5 | 15623 | 1934.9294 | 0 | 22666.4294 | 20688 | 29.71 | 5192 | 18.39 | 3214 | 1978
2027-05-16 | 17513 | 36354.5 | 14637 | 1934.9294 | 0 | 23652.4294 | 21399 | 35.05 | 6139 | 22.19 | 3886 | 2253
2027-05-23 | 18191 | 36354.5 | 14638 | 1934.9294 | 0 | 23651.4294 | 22457 | 30.01 | 5460 | 23.45 | 4266 | 1194
2027-05-30 | 18359 | 36354.5 | 14184 | 1934.9294 | 0 | 24105.4294 | 24921 | 31.3 | 5746 | 35.74 | 6562 | -816
2027-06-06 | 19286 | 36354.5 | 12362 | 2131.9961 | 0 | 26124.4961 | 26122 | 35.46 | 6838 | 35.45 | 6836 | 2
2027-06-13 | 19819 | 36354.5 | 11938 | 2131.9961 | 0 | 26548.4961 | 26361 | 33.95 | 6729 | 33.01 | 6542 | 187
2027-06-20 | 20870 | 36354.5 | 12060 | 2131.9961 | 0 | 26426.4961 | 26866 | 26.62 | 5556 | 28.73 | 5996 | -440
2027-06-27 | 21846 | 36354.5 | 12108 | 2131.9961 | 0 | 26378.4961 | 26690 | 20.75 | 4532 | 22.17 | 4844 | -312
2027-07-04 | 21771 | 36354.5 | 11895 | 2131.9961 | 0 | 26591.4961 | 27083 | 22.14 | 4820 | 24.4 | 5312 | -492
2027-07-11 | 22577 | 36354.5 | 12290 | 2131.9961 | 0 | 26196.4961 | 27841 | 16.03 | 3619 | 23.32 | 5264 | -1645
2027-07-18 | 22726 | 36354.5 | 12436 | 2131.9961 | 0 | 26050.4961 | 27804 | 14.63 | 3324 | 22.34 | 5078 | -1754
2027-07-25 | 22786 | 36354.5 | 12573 | 2041.4667 | 0 | 25822.9667 | 27728 | 13.33 | 3037 | 21.69 | 4942 | -1905
2027-08-01 | 22530 | 36354.5 | 12360 | 2131.9961 | 0 | 26126.4961 | 27764 | 15.96 | 3596 | 23.23 | 5234 | -1638
2027-08-08 | 22037 | 36354.5 | 12624 | 2131.9961 | 0 | 25862.4961 | 27466 | 17.36 | 3825 | 24.64 | 5429 | -1604
2027-08-15 | 22078 | 36354.5 | 13069 | 2131.9961 | 0 | 25417.4961 | 26756 | 15.12 | 3339 | 21.19 | 4678 | -1339
2027-08-22 | 21893 | 36354.5 | 12924 | 2131.9961 | 0 | 25562.4961 | 26287 | 16.76 | 3669 | 20.07 | 4394 | -725
2027-08-29 | 21770 | 36354.5 | 12871 | 2131.9961 | 0 | 25615.4961 | 26027 | 17.66 | 3845 | 19.55 | 4257 | -412
2027-09-05 | 21440 | 36354.5 | 12501 | 2131.9961 | 0 | 25985.4961 | 26840 | 21.2 | 4545 | 25.19 | 5400 | -855
2027-09-12 | 20266 | 36354.5 | 12483 | 2131.9961 | 0 | 26003.4961 | 26614 | 28.31 | 5737 | 31.32 | 6348 | -611
2027-09-19 | 19739 | 36354.5 | 12372 | 2131.9961 | 0 | 26114.4961 | 25853 | 32.3 | 6375 | 30.97 | 6114 | 261
2027-09-26 | 19140 | 36354.5 | 13805 | 2131.9961 | 0 | 24681.4961 | 25078 | 28.95 | 5541 | 31.02 | 5938 | -397
2027-10-03 | 18821 | 36354.5 | 14267 | 2131.9961 | 0 | 24219.4961 | 24269 | 28.68 | 5398 | 28.95 | 5448 | -50
Note: The reader should be aware that security and adequacy assessments are published on the IESO web site on a daily basis that progressively supersedes information presented
in this report.
Back to main menu

## Table 3.6
Back to main menu
Table 3.6: Assessment of Resource Adequacy: Expected Weather, Planned Scenario
Week | Ontario | Total Installed | Total Reductions | Demand | Firm Imports (+) | Total Available | Required | Available | Available | Required | Required | Reserve Above
Ending | Demand | Capacity | in Resources | Measures | Exports (-) | Resources | Resources | Reserve | Reserve | Reserve | Reserve | Requirement
Day | MW | MW | MW | MW | MW | MW | MW | % | MW | % | MW | MW
2026-04-05 | 18385 | 38468 | 12738 | 817.8227 | -612.9 | 25934.9227 | 22359 | 41.07 | 7550 | 21.62 | 3974 | 3576
2026-04-12 | 17954 | 38468 | 13664 | 817.8227 | -612.9 | 25008.9227 | 21704 | 39.29 | 7055 | 20.89 | 3750 | 3305
2026-04-19 | 17704 | 38468 | 14182 | 817.8227 | -612.9 | 24490.9227 | 21308 | 38.34 | 6787 | 20.36 | 3604 | 3183
2026-04-26 | 17441 | 38468 | 14586 | 817.8227 | -612.9 | 24086.9227 | 21083 | 38.11 | 6646 | 20.88 | 3642 | 3004
2026-05-03 | 17226 | 38536.5 | 14742 | 817.8227 | -612.9 | 23999.4227 | 20888 | 39.32 | 6773 | 21.26 | 3662 | 3111
2026-05-10 | 17257 | 38536.5 | 13752 | 897.3554 | 600 | 25681.8554 | 21495 | 48.82 | 8425 | 24.56 | 4238 | 4187
2026-05-17 | 17349 | 38536.5 | 15381 | 897.3554 | 600 | 24052.8554 | 21606 | 38.64 | 6704 | 24.54 | 4257 | 2447
2026-05-24 | 17955 | 38536.5 | 13823 | 897.3554 | 600 | 25610.8554 | 22994 | 42.64 | 7656 | 28.06 | 5039 | 2617
2026-05-31 | 18428 | 38536.5 | 13300 | 897.3554 | 600 | 26133.8554 | 25850 | 41.82 | 7706 | 40.28 | 7422 | 284
2026-06-07 | 19256 | 38891.49 | 14492 | 1088.4245 | 900 | 25487.9145 | 26522 | 32.36 | 6232 | 37.73 | 7266 | -1034
2026-06-14 | 19720 | 38891.49 | 12685 | 1088.4245 | 900 | 27294.9145 | 26810 | 38.41 | 7575 | 35.95 | 7090 | 485
2026-06-21 | 20836 | 38891.49 | 12822 | 1088.4245 | 900 | 27157.9145 | 27203 | 30.34 | 6322 | 30.56 | 6367 | -45
2026-06-28 | 21711 | 38891.49 | 12287 | 1138.4245 | 900 | 27742.9145 | 27297 | 27.78 | 6032 | 25.73 | 5586 | 446
2026-07-05 | 21684 | 38923.77 | 12248 | 1088.4245 | 900 | 27741.9045 | 27739 | 27.94 | 6058 | 27.92 | 6055 | 3
2026-07-12 | 22386 | 38923.77 | 11272 | 1088.4245 | 900 | 28717.9045 | 28460 | 28.29 | 6332 | 27.13 | 6074 | 258
2026-07-19 | 22526 | 38923.77 | 11372 | 1088.4245 | 900 | 28617.9045 | 28484 | 27.04 | 6092 | 26.45 | 5958 | 134
2026-07-26 | 22545 | 38923.77 | 11394 | 1088.4245 | 900 | 28595.9045 | 28493 | 26.84 | 6051 | 26.38 | 5948 | 103
2026-08-02 | 22295 | 38923.77 | 11373 | 1088.4245 | 900 | 28616.9045 | 28253 | 28.36 | 6322 | 26.72 | 5958 | 364
2026-08-09 | 21765 | 38923.77 | 11673 | 1088.4245 | 900 | 28316.9045 | 27957 | 30.1 | 6552 | 28.45 | 6192 | 360
2026-08-16 | 21818 | 38923.77 | 11873 | 1088.4245 | 900 | 28116.9045 | 27424 | 28.87 | 6299 | 25.69 | 5606 | 693
2026-08-23 | 21658 | 38923.77 | 12174 | 1088.4245 | 900 | 27815.9045 | 26600 | 28.43 | 6158 | 22.82 | 4942 | 1216
2026-08-30 | 21528 | 38923.77 | 12386 | 1088.4245 | 900 | 27603.9045 | 26274 | 28.22 | 6076 | 22.05 | 4746 | 1330
2026-09-06 | 21099 | 38923.77 | 11979 | 1088.4245 | 900 | 28010.9045 | 27017 | 32.76 | 6912 | 28.05 | 5918 | 994
2026-09-13 | 19902 | 38923.77 | 11879 | 1088.4245 | 900 | 28110.9045 | 26698 | 41.25 | 8209 | 34.15 | 6796 | 1413
2026-09-20 | 19409 | 38923.77 | 12590 | 1088.4245 | 900 | 27399.9045 | 25679 | 41.17 | 7991 | 32.3 | 6270 | 1721
2026-09-27 | 18840 | 38923.77 | 14542 | 1088.4245 | 900 | 25447.9045 | 24876 | 35.07 | 6608 | 32.04 | 6036 | 572
2026-10-04 | 18735 | 36965.77 | 14369 | 1088.4245 | 900 | 23662.9045 | 23491 | 26.3 | 4928 | 25.39 | 4756 | 172
2026-10-11 | 18023 | 36965.77 | 16554 | 897.3554 | 600 | 21286.8354 | 22221 | 18.11 | 3264 | 23.29 | 4198 | -934
2026-10-18 | 17959 | 36965.77 | 15489 | 897.3554 | 600 | 22351.8354 | 21767 | 24.46 | 4393 | 21.2 | 3808 | 585
2026-10-25 | 18280 | 36965.77 | 15568 | 897.3554 | 600 | 22272.8354 | 21708 | 21.84 | 3993 | 18.75 | 3428 | 565
2026-11-01 | 18587 | 36965.77 | 14700 | 897.3554 | 600 | 23140.8354 | 22220 | 24.5 | 4554 | 19.55 | 3633 | 921
2026-11-08 | 19120 | 36965.77 | 14068 | 828.4437 | 0 | 23703.9237 | 22636 | 23.97 | 4584 | 18.39 | 3516 | 1068
2026-11-15 | 19620 | 36965.77 | 12772 | 828.4437 | 0 | 24999.9237 | 23726 | 27.42 | 5380 | 20.93 | 4106 | 1274
2026-11-22 | 20177 | 36965.77 | 11932 | 828.4437 | 0 | 25839.9237 | 24292 | 28.07 | 5663 | 20.39 | 4115 | 1548
2026-11-29 | 20753 | 36965.77 | 11631 | 828.4437 | 0 | 26140.9237 | 24767 | 25.96 | 5388 | 19.34 | 4014 | 1374
2026-12-06 | 21047 | 36975.75 | 11719 | 828.4437 | 0 | 26062.9037 | 25001 | 23.83 | 5016 | 18.79 | 3954 | 1062
2026-12-13 | 21392 | 36975.75 | 11185 | 828.4437 | 0 | 26596.9037 | 25429 | 24.33 | 5205 | 18.87 | 4037 | 1168
2026-12-20 | 21607 | 36975.75 | 11247 | 828.4437 | 0 | 26534.9037 | 25621 | 22.81 | 4928 | 18.58 | 4014 | 914
2026-12-27 | 21046 | 36975.75 | 10940 | 828.4437 | 0 | 26841.9037 | 25387 | 27.54 | 5796 | 20.63 | 4341 | 1455
2027-01-03 | 21272 | 36975.75 | 10270 | 828.4437 | 0 | 27511.9037 | 25907 | 29.33 | 6240 | 21.79 | 4635 | 1605
2027-01-10 | 22032 | 36975.75 | 11283 | 715.7142 | 0 | 26386.1743 | 26441 | 19.76 | 4354 | 20.01 | 4409 | -55
2027-01-17 | 21925 | 36975.75 | 11899 | 737.9142 | 0 | 25792.3743 | 25972 | 17.64 | 3867 | 18.46 | 4047 | -180
2027-01-24 | 22002 | 36975.75 | 11780 | 715.7142 | 0 | 25889.1743 | 26205 | 17.67 | 3887 | 19.1 | 4203 | -316
2027-01-31 | 21984 | 36975.75 | 11923 | 715.7142 | 0 | 25746.1743 | 26090 | 17.11 | 3762 | 18.68 | 4106 | -344
2027-02-07 | 21430 | 36975.75 | 12333 | 828.4437 | 0 | 25448.9037 | 25419 | 18.75 | 4019 | 18.61 | 3989 | 30
2027-02-14 | 21386 | 36975.75 | 12171 | 828.4437 | 0 | 25610.9037 | 25390 | 19.76 | 4225 | 18.72 | 4004 | 221
2027-02-21 | 21063 | 36975.75 | 11983 | 828.4437 | 0 | 25798.9037 | 25242 | 22.48 | 4736 | 19.84 | 4179 | 557
2027-02-28 | 21008 | 36975.75 | 12148 | 828.4437 | 0 | 25633.9037 | 25017 | 22.02 | 4626 | 19.08 | 4009 | 617
2027-03-07 | 20485 | 36975.75 | 11868 | 828.4437 | 0 | 25913.9037 | 24688 | 26.5 | 5429 | 20.52 | 4203 | 1226
2027-03-14 | 20027 | 36975.75 | 11868 | 828.4437 | 0 | 25913.9037 | 24225 | 29.4 | 5887 | 20.96 | 4198 | 1689
2027-03-21 | 19530 | 36975.75 | 12158 | 828.4437 | 0 | 25623.9037 | 23607 | 31.2 | 6094 | 20.88 | 4077 | 2017
2027-03-28 | 19089 | 36975.75 | 12050 | 828.4437 | 0 | 25731.9037 | 23259 | 34.8 | 6643 | 21.85 | 4170 | 2473
2027-04-04 | 18593 | 36975.75 | 12960 | 828.4437 | 0 | 24821.9037 | 22114 | 33.5 | 6229 | 18.94 | 3521 | 2708
2027-04-11 | 18322 | 36975.75 | 13272 | 828.4437 | 0 | 24509.9037 | 21799 | 33.77 | 6188 | 18.98 | 3477 | 2711
2027-04-18 | 18006 | 36975.75 | 16905 | 828.4437 | 0 | 20876.9037 | 20999 | 15.94 | 2871 | 16.62 | 2993 | -122
2027-04-25 | 17715 | 36975.75 | 16895 | 828.4437 | 0 | 20886.9037 | 20746 | 17.91 | 3172 | 17.11 | 3031 | 141
2027-05-02 | 17496 | 36975.75 | 14552 | 828.4437 | 0 | 23229.9037 | 20798 | 32.77 | 5734 | 18.87 | 3302 | 2432
2027-05-09 | 17529 | 36975.75 | 15909 | 1934.9294 | 0 | 22979.3894 | 20753 | 31.09 | 5450 | 18.39 | 3224 | 2226
2027-05-16 | 17568 | 36975.75 | 14923 | 1934.9294 | 0 | 23965.3894 | 21464 | 36.41 | 6397 | 22.18 | 3896 | 2501
2027-05-23 | 18246 | 36975.75 | 14878 | 1934.9294 | 0 | 24010.3894 | 22522 | 31.59 | 5764 | 23.44 | 4276 | 1488
2027-05-30 | 18414 | 36975.75 | 14425 | 1934.9294 | 0 | 24463.3894 | 24996 | 32.85 | 6049 | 35.74 | 6582 | -533
2027-06-06 | 19349 | 36975.75 | 12603 | 2131.9961 | 0 | 26482.4561 | 26224 | 36.86 | 7133 | 35.53 | 6875 | 258
2027-06-13 | 19885 | 36975.75 | 12121 | 2131.9961 | 0 | 26964.4561 | 26447 | 35.6 | 7079 | 33 | 6562 | 517
2027-06-20 | 20939 | 36975.75 | 12243 | 2131.9961 | 0 | 26842.4561 | 26955 | 28.19 | 5903 | 28.73 | 6016 | -113
2027-06-27 | 21912 | 36975.75 | 12291 | 2131.9961 | 0 | 26794.4561 | 26776 | 22.28 | 4882 | 22.2 | 4864 | 18
2027-07-04 | 21842 | 36975.75 | 12078 | 2131.9961 | 0 | 27007.4561 | 27154 | 23.65 | 5165 | 24.32 | 5312 | -147
2027-07-11 | 22655 | 36975.75 | 12473 | 2131.9961 | 0 | 26612.4561 | 27928 | 17.47 | 3957 | 23.28 | 5273 | -1316
2027-07-18 | 22804 | 36975.75 | 12619 | 2131.9961 | 0 | 26466.4561 | 27882 | 16.06 | 3662 | 22.27 | 5078 | -1416
2027-07-25 | 22864 | 36975.75 | 12756 | 2041.4667 | 0 | 26238.9267 | 27825 | 14.76 | 3375 | 21.7 | 4961 | -1586
2027-08-01 | 22608 | 36975.75 | 12543 | 2131.9961 | 0 | 26542.4561 | 27862 | 17.4 | 3934 | 23.24 | 5254 | -1320
2027-08-08 | 22126 | 36975.75 | 12807 | 2131.9961 | 0 | 26278.4561 | 27555 | 18.77 | 4152 | 24.54 | 5429 | -1277
2027-08-15 | 22167 | 36975.75 | 13252 | 2131.9961 | 0 | 25833.4561 | 26855 | 16.54 | 3666 | 21.15 | 4688 | -1022
2027-08-22 | 21980 | 36975.75 | 13107 | 2131.9961 | 0 | 25978.4561 | 26374 | 18.19 | 3998 | 19.99 | 4394 | -396
2027-08-29 | 21858 | 36975.75 | 13054 | 2131.9961 | 0 | 26031.4561 | 26134 | 19.09 | 4173 | 19.56 | 4276 | -103
2027-09-05 | 21536 | 36975.75 | 12684 | 2131.9961 | 0 | 26401.4561 | 26946 | 22.59 | 4865 | 25.12 | 5410 | -545
2027-09-12 | 20369 | 36975.75 | 12666 | 2131.9961 | 0 | 26419.4561 | 26717 | 29.7 | 6050 | 31.17 | 6348 | -298
2027-09-19 | 19842 | 36975.75 | 12555 | 2131.9961 | 0 | 26530.4561 | 25956 | 33.71 | 6688 | 30.81 | 6114 | 574
2027-09-26 | 19242 | 36975.75 | 13988 | 2131.9961 | 0 | 25097.4561 | 25180 | 30.43 | 5855 | 30.86 | 5938 | -83
2027-10-03 | 18926 | 36975.75 | 14450 | 2131.9961 | 0 | 24635.4561 | 24374 | 30.16 | 5709 | 28.79 | 5448 | 261
Note: The reader should be aware that security and adequacy assessments are published on the IESO web site on a daily basis that progressively supersedes
information presented in this report.
Back to main menu

## Table 3.7
Back to main menu
Table 3.7: Zonal Bottled Generation: Expected Weather, Both Scenarios
Week | Firm Scenario | Firm Scenario | Firm Scenario | Planned Scenario | Planned Scenario | Planned Scenario
Ending | Bruce & West | Northeast | Northwest | Bruce & West | Northeast | Northwest
Day | MW | MW | MW | MW | MW | MW
2026-04-05 | 590.7372 | 0 | 0 | 590.7372 | 0 | 0
2026-04-12 | 0 | 0 | 0 | 0 | 0 | 0
2026-04-19 | 419.3919 | 0 | 0 | 419.3919 | 0 | 0
2026-04-26 | 1262.1629 | 0 | 0 | 1262.1629 | 0 | 0
2026-05-03 | 15.4853 | 0 | 0 | 15.4853 | 0 | 0
2026-05-10 | 574.2267 | 0 | 0 | 632.2267 | 0 | 0
2026-05-17 | 1102.3856 | 0 | 0 | 1160.3856 | 0 | 0
2026-05-24 | 760.6705 | 0 | 0 | 818.6705 | 0 | 0
2026-05-31 | 288.3561 | 0 | 0 | 346.3561 | 0 | 0
2026-06-07 | 0 | 0 | 0 | 0 | 0 | 0
2026-06-14 | 0 | 329.4262 | 18.7885 | 0 | 303.0262 | 18.7607
2026-06-21 | 0 | 475.0241 | 0 | 0 | 448.6118 | 0
2026-06-28 | 0 | 382.9649 | 0 | 0 | 356.5812 | 0
2026-07-05 | 0 | 506.3955 | 0 | 0 | 480.009 | 0
2026-07-12 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-19 | 0 | 0 | 0 | 0 | 0 | 0
2026-07-26 | 8.5942 | 0 | 0 | 8.5942 | 0 | 0
2026-08-02 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-09 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-16 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-23 | 0 | 0 | 6.6393 | 0 | 0 | 6.63
2026-08-30 | 1.9527 | 0 | 57.7203 | 59.9527 | 0 | 57.7177
2026-09-06 | 0.45159 | 0 | 16.5532 | 58.4516 | 0 | 16.5615
2026-09-13 | 0 | 0 | 55.8923 | 12.8152 | 0 | 55.8991
2026-09-20 | 660.9072 | 0 | 0 | 718.9072 | 0 | 0
2026-09-27 | 188.1624 | 0 | 0 | 246.1624 | 0 | 0
2026-10-04 | 39.86 | 0 | 0 | 97.86 | 0 | 0
2026-10-11 | 0 | 0 | 0 | 0 | 0 | 0
2026-10-18 | 951.3541 | 0 | 0 | 1009.3541 | 0 | 0
2026-10-25 | 897.3139 | 0 | 0 | 955.3139 | 0 | 0
2026-11-01 | 446.5047 | 0 | 89.1685 | 504.5047 | 0 | 89.1733
2026-11-08 | 73.9275 | 0 | 60.7199 | 131.9275 | 0 | 60.7139
2026-11-15 | 126.8946 | 0 | 79.9436 | 184.8946 | 0 | 79.9403
2026-11-22 | 696.6287 | 0 | 93.7971 | 754.6287 | 0 | 93.7913
2026-11-29 | 490.0584 | 0 | 0 | 548.0584 | 0 | 0
2026-12-06 | 687.1138 | 0 | 0 | 745.1138 | 0 | 0
2026-12-13 | 513.5693 | 0 | 0 | 571.5693 | 0 | 0
2026-12-20 | 535.3721 | 0 | 0 | 593.3721 | 0 | 0
2026-12-27 | 522.5288 | 0 | 0 | 580.5288 | 0 | 0
2027-01-03 | 783.5184 | 0 | 0 | 841.5184 | 0 | 0
2027-01-10 | 501.794 | 0 | 0 | 559.794 | 0 | 0
2027-01-17 | 0 | 0 | 0 | 0 | 0 | 0
2027-01-24 | 0 | 0 | 0 | 0 | 0 | 0
2027-01-31 | 0 | 0 | 0 | 52.6504 | 0 | 0
2027-02-07 | 140.7042 | 0 | 0 | 198.7042 | 0 | 0
2027-02-14 | 156.9067 | 0 | 0 | 214.9067 | 0 | 0
2027-02-21 | 127.0755 | 0 | 0 | 185.0755 | 0 | 0
2027-02-28 | 224.8308 | 0 | 0 | 282.8308 | 0 | 0
2027-03-07 | 280.6324 | 0 | 0 | 338.6324 | 0 | 0
2027-03-14 | 240.4098 | 0 | 0 | 298.4098 | 0 | 0
2027-03-21 | 1257.8085 | 0 | 0 | 1315.8085 | 0 | 0
2027-03-28 | 1342.1361 | 0 | 0 | 1400.1361 | 0 | 0
2027-04-04 | 0 | 0 | 0 | 0 | 0 | 0
2027-04-11 | 0 | 0 | 0 | 0 | 0 | 0
2027-04-18 | 0 | 0 | 0 | 0 | 0 | 0
2027-04-25 | 35.1567 | 0 | 0 | 93.1567 | 0 | 0
2027-05-02 | 357.8953 | 0 | 0 | 415.8953 | 0 | 0
2027-05-09 | 900.6363 | 0 | 0 | 958.6363 | 0 | 0
2027-05-16 | 248.984 | 0 | 0 | 306.984 | 0 | 0
2027-05-23 | 711.4624 | 0 | 0 | 769.4624 | 0 | 0
2027-05-30 | 305.4551 | 0 | 0 | 363.4551 | 0 | 0
2027-06-06 | 438.2976 | 0 | 0 | 496.2976 | 0 | 0
2027-06-13 | 0 | 0 | 0 | 0 | 0 | 0
2027-06-20 | 0 | 0 | 0 | 0 | 0 | 0
2027-06-27 | 0 | 0 | 0 | 0 | 0 | 0
2027-07-04 | 0 | 0 | 0 | 0 | 0 | 0
2027-07-11 | 0 | 0 | 0 | 0 | 0 | 0
2027-07-18 | 0 | 0 | 0 | 0 | 0 | 0
2027-07-25 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-01 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-08 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-15 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-22 | 0 | 0 | 0 | 0 | 0 | 0
2027-08-29 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-05 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-12 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-19 | 0 | 0 | 0 | 0 | 0 | 0
2027-09-26 | 0 | 0 | 0 | 0 | 0 | 0
2027-10-03 | 0 | 0 | 0 | 0 | 0 | 0
Back to main menu

## Table 3.8
Back to main menu
Table 3.8: Energy Production Capability Forecast
Month | Firm Scenario Forecast Energy Production Capability (GWh) | Planned Scenario Forecast Energy Production Capability (GWh)
2026-04-01 | 16687.1764 | 16734.7263
2026-05-01 | 17232.5963 | 17306.4563
2026-06-01 | 17376.1064 | 17493.395
2026-07-01 | 18386.6063 | 18505.8638
2026-08-01 | 18103.0663 | 18219.3338
2026-09-01 | 17016.9964 | 17123.3138
2026-10-01 | 14545.1163 | 14712.4438
2026-11-01 | 15655.6464 | 15828.9438
2026-12-01 | 16914.3563 | 17083.8313
2027-01-01 | 16219.5563 | 16407.1913
2027-02-01 | 14579.5566 | 14738.0913
2027-03-01 | 16335.6863 | 16538.7713
2027-04-01 | 14169.8964 | 14359.6913
2027-05-01 | 15434.6363 | 15595.1913
2027-06-01 | 16006.0064 | 16181.1613
2027-07-01 | 16072.5363 | 16242.9413
2027-08-01 | 15895.9063 | 16069.5813
2027-09-01 | 14904.8064 | 15078.0213
Back to main menu

## Table 3.9
Back to main menu
Table 3.9: Reductions by Fuel Type: Expected Weather, Firm Scenario
Week | Ontario | Total Internal | Total Reductions | Nuclear | Biomass, Oil & Gas | Hydro, Wind, Solar & Storage | Total Bottled
Ending | Demand | Resources | in Resources | Reductions | Reductions | Capacity Unavailable | Generation
Day | MW | MW | MW | MW | MW | MW | MW
2026-04-05 | 18385 | 38418.5 | 12690 | 3127.2 | 1485.9967 | 7485.495 | 590.7372
2026-04-12 | 17954 | 38418.5 | 13616 | 3116.2 | 2904.4733 | 7594.6129 | 0
2026-04-19 | 17704 | 38418.5 | 14134 | 3937.2 | 1861.9333 | 7914.8208 | 419.3919
2026-04-26 | 17441 | 38418.5 | 14538 | 3116.2 | 2418.8633 | 7740.2467 | 1262.1629
2026-05-03 | 17226 | 38418.5 | 14625 | 3116.2 | 3526.4933 | 7966.4483 | 15.4853
2026-05-10 | 17258 | 38418.5 | 13653 | 3112.2 | 2269.0967 | 7696.3519 | 574.2267
2026-05-17 | 17349 | 38418.5 | 15282 | 3112.2 | 2914.7567 | 8151.849 | 1102.3856
2026-05-24 | 17954 | 38418.5 | 13724 | 3112.2 | 1995.7067 | 7854.5556 | 760.6705
2026-05-31 | 18428 | 38418.5 | 13201 | 3112.2 | 2064.0967 | 7735.2249 | 288.3561
2026-06-07 | 19256 | 38418.5 | 14344 | 3946.2 | 2179.1167 | 8218.3664 | 0
2026-06-14 | 19718 | 38418.5 | 12564 | 2603.2 | 1462.2267 | 8149.1347 | 348.2147
2026-06-21 | 20835 | 38418.5 | 12700 | 2603.2 | 1462.2267 | 8158.9689 | 475.0241
2026-06-28 | 21712 | 38418.5 | 12166 | 2603.2 | 937.2267 | 8241.6066 | 382.9649
2026-07-05 | 21685 | 38418.5 | 12123 | 2603.2 | 937.2267 | 8075.4251 | 506.3955
2026-07-12 | 22386 | 38418.5 | 11121 | 1821.2 | 1034.1067 | 8264.9919 | 0
2026-07-19 | 22526 | 38418.5 | 11222 | 1821.2 | 1034.1067 | 8365.4428 | 0
2026-07-26 | 22545 | 38418.5 | 11243 | 1821.2 | 1071.9467 | 8340.1376 | 8.5942
2026-08-02 | 22294 | 38418.5 | 11222 | 1821.2 | 1034.1067 | 8365.6252 | 0
2026-08-09 | 21765 | 38418.5 | 11522 | 1868.2 | 988.2867 | 8664.8387 | 0
2026-08-16 | 21817 | 38418.5 | 11723 | 1868.2 | 988.2867 | 8865.3238 | 0
2026-08-23 | 21657 | 38418.5 | 12023 | 1868.2 | 988.2867 | 9159.3814 | 6.6393
2026-08-30 | 21528 | 38418.5 | 12177 | 1868.2 | 988.2867 | 9260.4931 | 59.673
2026-09-06 | 21099 | 38418.5 | 11770 | 1831.2 | 861.7367 | 9059.5334 | 17.0048
2026-09-13 | 19902 | 38418.5 | 11715 | 1831.2 | 965.0167 | 8862.1391 | 55.8923
2026-09-20 | 19409 | 38418.5 | 12381 | 1831.2 | 996.7367 | 8891.8378 | 660.9072
2026-09-27 | 18840 | 38418.5 | 14333 | 3676.2 | 1521.7367 | 8946.0481 | 188.1624
2026-10-04 | 18735 | 36354.5 | 14054 | 2638.2 | 2559.7367 | 8815.4998 | 39.86
2026-10-11 | 18023 | 36354.5 | 16374 | 2614.2 | 5897.5067 | 7861.8379 | 0
2026-10-18 | 17959 | 36354.5 | 15252 | 2614.2 | 3745.9867 | 7939.2166 | 951.3541
2026-10-25 | 18280 | 36354.5 | 15330 | 2614.2 | 3663.4867 | 8154.5207 | 897.3139
2026-11-01 | 18587 | 36354.5 | 14389 | 2614.2 | 3242.8967 | 7995.54 | 535.6732
2026-11-08 | 19120 | 36354.5 | 13773 | 3410.2 | 2578.2067 | 7649.5367 | 134.6474
2026-11-15 | 19620 | 36354.5 | 12433 | 3410.2 | 1534.4233 | 7280.3822 | 206.8382
2026-11-22 | 20177 | 36354.5 | 11637 | 2596.2 | 907.8367 | 7342.173 | 790.4258
2026-11-29 | 20753 | 36354.5 | 11337 | 2596.2 | 907.8367 | 7342.173 | 490.0584
2026-12-06 | 21047 | 36354.5 | 11419 | 2595.2 | 982.6567 | 7153.691 | 687.1138
2026-12-13 | 21392 | 36354.5 | 10886 | 2595.2 | 789.6567 | 6986.6509 | 513.5693
2026-12-20 | 21607 | 36354.5 | 10947 | 2595.2 | 789.6567 | 7026.3903 | 535.3721
2026-12-27 | 21046 | 36354.5 | 10640 | 2595.2 | 789.6567 | 6732.2971 | 522.5288
2027-01-03 | 21262 | 36354.5 | 9971 | 1725.2 | 789.6567 | 6671.811 | 783.5184
2027-01-10 | 22006 | 36354.5 | 10985 | 2566.2 | 1232.0667 | 6684.4662 | 501.794
2027-01-17 | 21899 | 36354.5 | 11660 | 3391.2 | 1232.0667 | 7035.4761 | 0
2027-01-24 | 21975 | 36354.5 | 11540 | 3391.2 | 1232.0667 | 6916.2045 | 0
2027-01-31 | 21958 | 36354.5 | 11631 | 3391.2 | 1276.0667 | 6963.0786 | 0
2027-02-07 | 21395 | 36354.5 | 12035 | 3391.2 | 1434.5267 | 7068.2872 | 140.7042
2027-02-14 | 21351 | 36354.5 | 11873 | 3391.2 | 1254.5267 | 7069.5158 | 156.9067
2027-02-21 | 21027 | 36354.5 | 11686 | 3391.2 | 1254.5267 | 6912.1106 | 127.0755
2027-02-28 | 20973 | 36354.5 | 11851 | 3391.2 | 1254.5267 | 6979.4641 | 224.8308
2027-03-07 | 20446 | 36354.5 | 11570 | 3392.2 | 839.6367 | 7057.0825 | 280.6324
2027-03-14 | 19989 | 36354.5 | 11570 | 3392.2 | 839.6367 | 7097.2189 | 240.4098
2027-03-21 | 19492 | 36354.5 | 11860 | 2566.2 | 839.6367 | 7195.7996 | 1257.8085
2027-03-28 | 19050 | 36354.5 | 11753 | 2566.2 | 839.6367 | 7004.114 | 1342.1361
2027-04-04 | 18553 | 36354.5 | 12720 | 2566.2 | 2585.7867 | 7567.2982 | 0
2027-04-11 | 18274 | 36354.5 | 13033 | 2565.2 | 2886.3867 | 7580.4119 | 0
2027-04-18 | 17958 | 36354.5 | 16665 | 5199.2 | 3636.7267 | 7828.4009 | 0
2027-04-25 | 17667 | 36354.5 | 16598 | 5199.2 | 3636.7267 | 7726.0314 | 35.1567
2027-05-02 | 17449 | 36354.5 | 14329 | 5199.2 | 1342.4867 | 7428.5913 | 357.8953
2027-05-09 | 17474 | 36354.5 | 15623 | 5199.2 | 1427.1533 | 8095.2992 | 900.6363
2027-05-16 | 17513 | 36354.5 | 14637 | 5199.2 | 1247.1533 | 7941.3701 | 248.984
2027-05-23 | 18191 | 36354.5 | 14638 | 5199.2 | 715.9067 | 8010.2115 | 711.4624
2027-05-30 | 18359 | 36354.5 | 14184 | 5199.2 | 715.9067 | 7962.4379 | 305.4551
2027-06-06 | 19286 | 36354.5 | 12362 | 2565.2 | 715.9067 | 8641.7198 | 438.2976
2027-06-13 | 19819 | 36354.5 | 11938 | 2570.2 | 885.8267 | 8481.5091 | 0
2027-06-20 | 20870 | 36354.5 | 12060 | 2570.2 | 885.8267 | 8603.531 | 0
2027-06-27 | 21846 | 36354.5 | 12108 | 2570.2 | 885.8267 | 8651.1069 | 0
2027-07-04 | 21771 | 36354.5 | 11895 | 2570.2 | 885.8267 | 8437.8283 | 0
2027-07-11 | 22577 | 36354.5 | 12290 | 2589.2 | 982.7067 | 8716.9424 | 0
2027-07-18 | 22726 | 36354.5 | 12436 | 2589.2 | 982.7067 | 8863.2004 | 0
2027-07-25 | 22786 | 36354.5 | 12573 | 2589.2 | 982.7067 | 9000.4861 | 0
2027-08-01 | 22530 | 36354.5 | 12360 | 2589.2 | 982.7067 | 8787.3838 | 0
2027-08-08 | 22037 | 36354.5 | 12624 | 2628.2 | 936.8867 | 9058.5971 | 0
2027-08-15 | 22078 | 36354.5 | 13069 | 2628.2 | 936.8867 | 9503.4191 | 0
2027-08-22 | 21893 | 36354.5 | 12924 | 2628.2 | 936.8867 | 9358.3153 | 0
2027-08-29 | 21770 | 36354.5 | 12871 | 2628.2 | 936.8867 | 9305.6352 | 0
2027-09-05 | 21440 | 36354.5 | 12501 | 2596.2 | 810.3367 | 9094.1722 | 0
2027-09-12 | 20266 | 36354.5 | 12483 | 2596.2 | 990.3367 | 8895.297 | 0
2027-09-19 | 19739 | 36354.5 | 12372 | 2596.2 | 990.3367 | 8784.6019 | 0
2027-09-26 | 19140 | 36354.5 | 13805 | 3413.2 | 1515.3367 | 8875.3107 | 0
2027-10-03 | 18821 | 36354.5 | 14267 | 3395.2 | 1861.6767 | 9009.253 | 0
Back to main menu

## Table 3.10
Back to main menu
Table 3.10: Firm Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Month | Year | Nuclear (GWh) | Hydro (GWh) | Gas & Oil (GWh) | Wind (GWh) | Biofuel (GWh) | Other (GWh) | Total (GWh)
Apr | 2026 | 6331.07 | 3120.86 | 765.03 | 1100.44 | 31.48 | 69.52 | 11418.4
May | 2026 | 6531.31 | 3424.8 | 453.16 | 630.58 | 18.08 | 44.72 | 11102.65
Jun | 2026 | 6560.06 | 3183.45 | 1323.52 | 666.86 | 23.49 | 75.26 | 11832.64
Jul | 2026 | 6985.52 | 2993.63 | 2429.18 | 582.4 | 37.45 | 108.76 | 13136.94
Aug | 2026 | 6920.45 | 2735.52 | 2377.71 | 621.22 | 36.15 | 107.55 | 12798.6
Sep | 2026 | 6196.66 | 2587.85 | 1819.84 | 745.4 | 29.77 | 86.6 | 11466.12
Oct | 2026 | 4904.25 | 2745.05 | 2410.75 | 1280.69 | 33.79 | 112.92 | 11487.45
Nov | 2026 | 4479.99 | 2980.76 | 3019.86 | 1396.7 | 48.16 | 83.16 | 12008.63
Dec | 2026 | 5257.58 | 3176.35 | 3340.78 | 1368.85 | 48.3 | 76.45 | 13268.31
Jan | 2027 | 4885.69 | 3211.08 | 4095.13 | 1464.1 | 80.01 | 108.72 | 13844.73
Feb | 2027 | 4328.33 | 2993.55 | 3509.68 | 1255.39 | 41.39 | 82.16 | 12210.5
Mar | 2027 | 5094.08 | 3174.19 | 2977.32 | 1232.17 | 25.75 | 97.42 | 12600.93
Apr | 2027 | 4115.25 | 3127.56 | 2542.38 | 1288.4 | 23.65 | 107.27 | 11204.51
May | 2027 | 3913.66 | 3448.93 | 2745.85 | 988.37 | 23.45 | 101.21 | 11221.47
Jun | 2027 | 5132.83 | 3180.36 | 2779.87 | 762.89 | 24.04 | 106.53 | 11986.52
Jul | 2027 | 5471.71 | 2990.48 | 4037.71 | 596.05 | 36.92 | 112.79 | 13245.66
Aug | 2027 | 5446.72 | 2740.31 | 4030.28 | 628.4 | 31.92 | 105.3 | 12982.93
Sep | 2027 | 4894.47 | 2587.43 | 3238.64 | 788.53 | 29.26 | 92.11 | 11630.44
Back to main menu

## Table 3.11
Back to main menu
Table 3.11: Planned Scenario - Expected Weather: Ontario Monthly Energy Production by Fuel Type
Month | Year | Nuclear (GWh) | Hydro (GWh) | Gas & Oil (GWh) | Wind (GWh) | Biofuel (GWh) | Other (GWh) | Total (GWh)
2026-04-01 | 2026 | 6329.59 | 3120.67 | 766.06 | 1101.22 | 31.48 | 65.09 | 11414.11
2026-05-01 | 2026 | 6531.3 | 3424.82 | 453.38 | 630.58 | 18.08 | 42.73 | 11100.89
2026-06-01 | 2026 | 6560.06 | 3183.41 | 1323.6 | 666.9 | 23.51 | 71.48 | 11828.96
2026-07-01 | 2026 | 6985.52 | 2993.63 | 2428.97 | 582.36 | 37.77 | 97.96 | 13126.21
2026-08-01 | 2026 | 6920.47 | 2735.52 | 2377.65 | 621.2 | 36.26 | 94.55 | 12785.65
2026-09-01 | 2026 | 6197.93 | 2587.85 | 1819.07 | 745.11 | 29.75 | 83.27 | 11462.98
2026-10-01 | 2026 | 4904.25 | 2745.05 | 2410.23 | 1280.58 | 35.31 | 98.19 | 11473.61
2026-11-01 | 2026 | 4479.99 | 2980.76 | 3023.34 | 1396.69 | 44.9 | 81.63 | 12007.31
2026-12-01 | 2026 | 5257.58 | 3176.35 | 3339.4 | 1368.99 | 49.64 | 70.21 | 13262.17
2027-01-01 | 2027 | 4885.69 | 3211.08 | 4123.21 | 1464.43 | 78.74 | 124.71 | 13887.86
2027-02-01 | 2027 | 4328.33 | 2993.55 | 3537.68 | 1255.39 | 37.77 | 88.22 | 12240.94
2027-03-01 | 2027 | 5094.08 | 3174.2 | 3005.91 | 1232.75 | 24.46 | 100.64 | 12632.04
2027-04-01 | 2027 | 4115.25 | 3127.56 | 2575.08 | 1289.1 | 23.65 | 94.35 | 11224.99
2027-05-01 | 2027 | 3913.66 | 3448.9 | 2785.27 | 989.06 | 23.49 | 90.87 | 11251.25
2027-06-01 | 2027 | 5132.83 | 3180.36 | 2827.55 | 763.48 | 24.04 | 95.66 | 12023.92
Jul | 2027 | 5471.71 | 2990.48 | 4099.54 | 596.14 | 37.13 | 131.74 | 13326.74
Aug | 2027 | 5446.72 | 2740.31 | 4096.3 | 628.5 | 32.47 | 120.56 | 13064.86
Sep | 2027 | 4894.47 | 2587.43 | 3311.9 | 788.93 | 29.53 | 109.73 | 11721.99
Back to main menu

## Table 4.1
Back to main menu
Table 4.1: Transmission Projects
Zone | ID | Transmitter | Description | Proposed I/S Date
Bruce | N/A | Hydro-One | Tara Battery Storage 230kV LT1 Connection | 2027 Q2
East | 2023-746 | Hydro-One | Connect Napanee BESS _ ELT1 | 2026 Q1
East | N/A | Hydro-One | Connect Marmora Pumping Station TX | 2026 Q2
East | 2020-EX1089 | Hydro-One | Lennox TS BULK: ABCB component replacement | 2026 Q2
East | N/A | Hydro-One | Picton TS - T1/T2 Transformer Replacement | 2026 Q3
East | 2024-800 | Hydro-One | Connect Skyview BESS | 2026 Q4
East | N/A | Hydro-One | Lennox TS - Replace 500kV Breaker KL526 | 2026 Q4
East | 2023-758 | Hydro-One | Belleville TS: Build 75/125 MVA, 230/44 kV DESN | 2026 Q4
East | N/A | Hydro-One | Gardiner TS: T1/T2 PCT Component Replacement | 2026 Q4
East | 2024-793 | Hydro-One | Connect Trailroad BESS | 2027 Q1
Essa | 2022-EX1208 | Hydro-One | Essa TS -T3 and Component Replacement | 2026 Q2
Essa | N/A | Hydro-One | Orillia TS: T2 Transformer Replacement | 2026 Q4
Essa | 2016-575 | Hydro-One | MetroLinx Burlington Traction Substation Connectio | 2026 Q4
Niagara | N/A | Hydro-One | Temporary A6C 115kV Line Tap | 2026 Q2
Niagara | 2016-EX862 | Hydro-One | Beck 1 SS 115kV ABCB Replacement | 2026 Q3
Niagara | N/A | Hydro-One | Q28A (Beck2 X Abitibi Jct): 230kV Line Section Upr | 2026 Q4
Northeast | 2023-749 | Hydro-One | HOSSM Hollingsworth Circuit - Connection of Hollin | 2026 Q1
Northeast | 2020-EX115 | Hydro-One | HOSSM Tx Lines Sault #3 Line Refurbishment | 2026 Q3
Northeast | N/A | Hydro-One | HOSSM Third Line TS PUC 230kV Connections | 2026 Q3
Northeast | 2020-EX1106 | Hydro-One | Porcupine TS: Component Replacement | 2026 Q4
Northeast | 2022-EX1196 | Hydro-One | Elliot Lake TS: Component Replacement | 2026 Q4
Northeast | 2020-676 | Hydro-One | Wikwemikong Pellet Plant Connection | 2026 Q4
Northeast | N/A | Hydro-One | A4H/A5H, Tunis JCT-Fournier JCT, Tx Line Refurb. | 2027 Q1
Northwest | N/A | Hydro-One | Mackenzie TS: 230kV Brownfield Refurb | 2026 Q4
Northwest | N/A | Hydro-One | 115kV E2R GBR CTS Connection | 2027 Q1
Ottawa | N/A | Hydro-One | Lisgar TS: T1 and Component Replacement | 2026 Q2
Ottawa | N/A | Hydro-One | South East Ottawa Build New 230kV line Tap | 2026 Q2
Ottawa | N/A | Hydro-One | Longueuil TS: T3/T4 Replacement | 2026 Q4
Ottawa | 2023-EX1243 | Hydro-One | Merivale TS Add 230/115kV Autotransformers | 2026 Q4
Ottawa | 2024-EX1280 | Hydro-One | Russell TS - T1/T2 & Comp Replacement | 2027 Q2
Southwest | 2019-EX1021 | Hydro-One | Tx Line Refurb. B7/B8 ¦ Burlington TS-Bronte TS | 2026 Q1
Southwest | N/A | Hydro-One | B5/6C, BurlingtonTS X WestoverCTS, Tx Line Refurb. | 2026 Q2
Southwest | 2024-780 | Hydro-One | Oxford Battery Energy Storage Project | 2026 Q4
Southwest | 2024-EX1285 | Hydro-One | M31W: Reinforce Buchanan x St Thomas Line Tap Point | 2027 Q1
Southwest | 2022-EX1217 | Hydro-One | Nanticoke TS; ABCB Project | 2027 Q1
Southwest | 2024-776 | Hydro-One | Elora BESS LP1 Connection | 2027 Q1
Southwest | 2024-777 | Hydro-One | Hedley BESS LP1 Connection | 2027 Q1
Southwest | N/A | Hydro-One | Preston TS: T3, T4 & Component Replacement | 2027 Q2
Toronto | 2019-EX1041 | Hydro-One | Bridgman TS: T11,T12,T13,T14 & Component Replacem | 2026 Q2
Toronto | 2020-EX1104 | Hydro-One | HV UG Cable - Replace C5E/C7E | 2026 Q2
Toronto | 2020-679 | Hydro-One | Richview x Trafalgar 230kV Conductor Upgrade | 2026 Q2
Toronto | 2019-EX1034 | Hydro-One | Claireville TS: Component Replacements | 2026 Q3
Toronto | N/A | Hydro-One | Scarboro TS:T23 & Component Replacements | 2026 Q4
Toronto | N/A | Hydro-One | Clarington TS: Install Surge Capacitors | 2026 Q4
Toronto | 2016-EX869 | Hydro-One | Main TS: T3, T4 & Component Replacement | 2026 Q4
Toronto | N/A | Hydro-One | Malvern T3 EOL Replacement | 2027 Q1
Toronto | 2019-EX1083 | Hydro-One | Strachan TS: T14 & Component Replacement | 2027 Q1
Toronto | 2016-561 | Hydro-One | MetroLinx Mimico Traction Substation Connection | 2027 Q1
Toronto | 2016-576 | Hydro-One | MetroLinx ERMF Traction Substation Connection | 2027 Q1
Toronto | 2018-637 | Hydro-One | Richview Manby Transmission Reinforcement - Line | 2027 Q2
West | N/A | Hydro-One | Wallaceburg TS: Conversion from 115 kV to 230 kV | 2026 Q3
West | 2022-718 | Hydro-One | Connect East Windsor (Expansion) L.P. ELT1 | 2026 Q4
West | N/A | Hydro-One | St. Andrews TS: T3, T4 & Switchyard Refurbishment | 2026 Q4
West | 2021-EX1166 | Hydro-One | Lauzon TS: T6, T5 & Component Replacement | 2026 Q4
Back to main menu
Back to main menu

## Table 4.2
Back to main menu
Table 4.2: Interface Limits with All Elements in Service
Interface | Limit (MW) | Notes
BLIP | 3000
NBLIP | 1800
QFW | 2000 | ****
FABCW | 7500 | *
FETT | 5000 | **
CLAN | 2000
FIO | 2900
SLW | 1350
FN | 1500 | ***
FS | 1750
P502X South | 1000
EWTE | 500
EWTW | 500
(*) FABCW limit varies according to BLIP flow and QFWN (QFW plus Nanticoke) flow.
For each recognized contingency, separate voltage and stability limit ranges are defined.
Published limit range based on the most restrictive contigency under optimal
Bruce System Conditions in SCO-South Tab1.
Lower limit based on NBLIP @ 1500MW and QFWN @ 4000MW.
Upper limit based on BLIP @ 3000MW and QFWN @ 4000MW.
(**) FETT is a fixed boundary condition limit.
(***) FN is a fixed boundary condition limit.
(****) With Q26M and Q35M being 3-ended circuits (connected to Middleport TS), the
QFW limit is improved to the boundary limit of 2000 MW.
Back to main menu

## Table 4.3
Back to main menu
Table 4.3: Interconnection Flow Limits
Interconnection | Limit - Flows Out of Ontario (MW) |  | Limit - Flows Into Ontario (MW)
Manitoba – Summer* | 246 |  | 260 | (3,6)
Manitoba – Winter* | 300 | (3) | 368 | (3,6)
Minnesota | 150 |  | 100 | (3)
Quebec North (Northeast) – Summer* | 105 |  | 85
D4Z | 0 | (5) | 85
H4Z | 105 | (5) | 0
Quebec North (Northeast)– Winter* | 105 |  | 85
D4Z | 0 |  | 85
H4Z | 105 |  | 0
Quebec South (Ottawa) – Summer* | 1570 |  | 1865
X2Y | 0 |  | 65
Q4C | 120 |  | not of concern
P33C | 0 |  | 300
D5A | 200 |  | 250
H9A | 0 |  | 0
HVDC | 1250 |  | 1250
Quebec South (Ottawa) – Winter* | 1590 |  | 1865
X2Y | 0 |  | 65
Q4C | 140 |  | not of concern
P33C | 0 |  | 300
D5A | 200 |  | 250
H9A | 0 |  | 0
HVDC | 1250 |  | 1250
Quebec South (East) – Summer* | 470 |  | 400
B31L + B5D | 470 |  | 400
Quebec South (East) – Winter* | 470 |  | 400
B31L + B5D | 470 |  | 400
New York St. Lawrence – Summer* | 300 |  | 300
New York St. Lawrence – Winter* | 300 |  | 300
New York Niagara – Summer* | 1900 | (1) | 1500 | (1,7)
Emergency Transfer Limit - Summer* | N/A | (1) | N/A | (1,7)
New York Niagara – Winter* | 2100 | (1) | 1750 | (1,7)
Emergency Transfer Limit - Winter* | N/A | (1) | N/A | (1,7)
Michigan – Summer* | 1650 | (2,3) | 1550 | (2,3)
Emergency Transfer Limit - Summer* | N/A | (2,3) | N/A | (2,3)
Michigan – Winter* | 1650 | (2,3) | 1700 | (2,3)
Emergency Transfer Limit - Winter* | N/A | (2,3) | N/A | (2,3)
* Summer Limits apply from May 1 to October 31. Winter Limits apply from November 1 to April 30.
(1) Flow limits depend on generation dispatch outside Ontario.
(2) Normal limits are based on LT ratings and phase shifters bypassed and Emergency limits are based on
ST ratings and phase shifters regulating. Flow limits vary depending on the generation dispatch
within Ontario.
(3) For real time operation of the interconnection, limits are based on ambient conditions.
(5) Limit based on 0 to 4 km/h wind speed and 30˚C ambient temperature.
(6) Flows into Ontario include flows on circuit SK1.
(7) Flow limits into Ontario are shown without considering QFW transmission constraints within Ontario.
Back to main menu

## Table 4.4
Back to main menu
Table 4.4: Bruce Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-03-12 09:00 | 2026-06-05 09:00 | 85 | BRUCE A TS | L560L569, OLD21-B560V, OLD21-B569B, OLDAL560, OLDEL569, OLDL560_BUS, OLDL569_BUS | 1-00306356 Rev. #2 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2026-05-12 05:00 | 2026-06-05 09:00 | 24.1667 | MILTON SS, BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, OLD21-B502M, 40-B502M | 1-00293588 Rev. #6 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-05-12 05:00 | 2026-06-05 09:00 | 24.1667 | BRUCE A TS, MILTON SS | EL502, OLDHT4L502, KL502, L502L573, OLD21-B502M, 40-B502M, L502_BUS, HT4L502, L502WT27, 21-B502M, OLDL502_BUS | 1-00252396 Rev. #9 | 4 Day(s) | FABCW NBLIP BLIP | 1900 300 300
2026-05-12 05:00 | 2026-07-27 05:00 | 76 | BRUCE A TS | OLDAL562, EL502, HT28L562, OLDHT4L502, L560L569, OLDT3E, OLDT3T28, OLDT4A, OLD21-B560V, OLD21-B502M, OLD21-B562E, OLDE_BUS, T25-A, T27-E, OLDAL560, OLDEL569, OLDA_BUS | 1-00252395 Rev. #10 | Non-recallable | FABCW NBLIP BLIP | 150 0 0
2026-07-20 06:15 | 2026-08-28 16:00 | 39.4062 | BRUCE B SS, MILTON SS, BRUCE JCT, WILLOW CREEK JCT | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, L501L563, 29-B561M | 1-00293589 Rev. #6 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-08-30 08:00 | 2026-09-04 16:00 | 5.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #3 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-08-30 08:00 | 2026-09-11 16:00 | 12.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #5 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-11-05 09:00 | 2026-11-23 06:00 | 17.875 | BRUCE A TS | T27-E | 1-00301193 Rev. #1 | Non-recallable | FABCW NBLIP BLIP | 150 0 0
2026-03-12 09:00 | 2026-06-05 09:00 | 85 | BRUCE A TS | L560L569, OLD21-B560V, OLD21-B569B, OLDAL560, OLDEL569, OLDL560_BUS, OLDL569_BUS | 1-00306356 Rev. #2 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2026-05-12 05:00 | 2026-06-05 09:00 | 24.1667 | MILTON SS, BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, OLD21-B502M, 40-B502M | 1-00293588 Rev. #6 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-05-12 05:00 | 2026-06-05 09:00 | 24.1667 | BRUCE A TS, MILTON SS | EL502, OLDHT4L502, KL502, L502L573, OLD21-B502M, 40-B502M, L502_BUS, HT4L502, L502WT27, 21-B502M, OLDL502_BUS | 1-00252396 Rev. #9 | 4 Day(s) | FABCW NBLIP BLIP | 1750 300 300
2026-05-12 05:00 | 2026-07-27 05:00 | 76 | BRUCE A TS | OLDAL562, EL502, HT28L562, OLDHT4L502, L560L569, OLDT3E, OLDT3T28, OLDT4A, OLD21-B560V, OLD21-B502M, OLD21-B562E, OLDE_BUS, T25-A, T27-E, OLDAL560, OLDEL569, OLDA_BUS | 1-00252395 Rev. #10 | Non-recallable | FABCW NBLIP BLIP | 150 0 0
2026-08-30 08:00 | 2026-09-04 16:00 | 5.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #3 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-08-30 08:00 | 2026-09-11 16:00 | 12.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #5 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2026-03-12 09:00 | 2026-06-05 09:00 | 85 | BRUCE A TS | L560L569, OLD21-B560V, OLD21-B569B, OLDAL560, OLDEL569, OLDL560_BUS, OLDL569_BUS | 1-00306356 Rev. #2 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2026-05-12 05:00 | 2026-07-27 05:00 | 76 | BRUCE A TS | OLDAL562, EL502, HT28L562, OLDHT4L502, L560L569, OLDT3E, OLDT3T28, OLDT4A, OLD21-B560V, OLD21-B502M, OLD21-B562E, OLDE_BUS, T25-A, T27-E, OLDAL560, OLDEL569, OLDA_BUS | 1-00252395 Rev. #10 | Non-recallable | FABCW NBLIP BLIP | 150 0 0
2026-07-20 06:15 | 2026-08-28 16:00 | 39.4062 | BRUCE B SS, MILTON SS, BRUCE JCT, WILLOW CREEK JCT | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, L501L563, 29-B561M | 1-00293589 Rev. #6 | 4 Hour(s) | FABCW NBLIP BLIP | 1750 300 300
2025-11-11 12:00 | 2026-03-30 05:00 | 138.7083 | BRUCE A TS | T25-WT25 | 1-00283773 Rev. #21 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2025-11-12 10:00 | 2026-06-02 05:00 | 201.7917 | BRUCE A TS | 21-B502M | 1-00283776 Rev. #13 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2025-11-12 11:00 | 2026-11-23 07:00 | 375.8333 | BRUCE A TS | T27-WT27 | 1-00283777 Rev. #14 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2026-01-27 09:00 | 2026-11-23 07:00 | 299.9167 | BRUCE A TS | T27-WT27 | 1-00301875 Rev. #7 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2026-02-03 07:15 | 2026-05-12 05:00 | 97.9062 | BRUCE A TS | 21-B502M | 1-00301106 Rev. #27 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2026-02-03 13:15 | 2026-03-30 05:00 | 54.6562 | BRUCE A TS | T25-WT25 | 1-00301105 Rev. #17 | Non-recallable | FABCW NBLIP BLIP | 0 0 0
2026-07-19 12:15 | 2026-10-02 13:00 | 75.0312 | BRUCE B SS | P-P5 | 1-00295508 Rev. #7 | Non-recallable | No Impact | #N/A
2027-09-20 07:00 | 2027-09-30 19:00 | 10.5 | BRUCE B SS | P-P7 | 1-00252425 Rev. #3 | 6 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.5
Back to main menu
Table 4.5: East Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-28 08:00 | 2026-10-09 16:00 | 11.3333 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P | 1-00275118 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-11-13 16:00 | 15.3333 | ST. LAWRENCE TS, MASSENA JCT | L34P.ROXLA, 49-L34P | 1-00275119 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-11-30 07:30 | 2026-12-11 17:30 | 11.4167 | MASSON GS, IPB MASSON JCT, ORLEANS JCT 2, HAWTHORNE TS, ORLEANS TS, CUMBERLAND JCT, ST. ISIDORE TS, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00299005 Rev. #1 | 6 Hour(s) | D5A BEAU FIO | 250 690 250
2026-03-31 08:00 | 2026-11-15 16:00 | 229.3333 | BOWMANVILLE SS | H3E, H3L521, H3_BUS | 1-00285558 Rev. #6 | 8 Hour(s) | No Impact | #N/A
2026-07-19 07:00 | 2026-08-28 09:00 | 40.0833 | LENNOX TS, BOWMANVILLE SS | X521B.BOXLE, H3L521, L21L41, PL521, X4L521 | 1-00285555 Rev. #8 | 8 Hour(s) | No Impact | #N/A
2027-05-30 07:00 | 2027-07-09 09:00 | 40.0833 | LENNOX TS, BOWMANVILLE SS | X520B.BOXLE, H2L520, KL520, L20L42, X3L520 | 1-00276876 Rev. #12 | 8 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-04 16:00 | 22.3333 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS, DUFFIN JCT, OSHAWA WILSON TS, CHERRYWOOD TS, WHITBY TS, WILSON JCT, WHITBY JCT, B23C H26C TIE JCT | 81-T23C, 81-T28C, 128T1-T31H, 54T2-T23C, 40T3-T23C, 54T4-T23C, K2L28, L23L28, L23L31, P2L31, 296-T23C, 296-T28C, 296-T31H, L28_BUS, L31_BUS, T28C.CLXDJ, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, T23C.BJXCH, T23C.CLXWJ, T23C.WJXBJ, T23C.WJXWH, T23C.WJXWI, T23C.WJXWY, 57-T31H, 54T7-T23C, L23_BUS | 1-00295709 Rev. #1 | 12 Hour(s) | P33C | 100
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #1 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #48 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-04-02 08:00 | 2026-06-04 16:00 | 63.3333 | ODESSA JCT, MILLTOWN JCT | 59Q6S-78, 78Q6S-59 | 1-00290611 Rev. #9 | 12 Hour(s) | No Impact | #N/A
2026-05-18 08:00 | 2026-06-04 16:00 | 17.3333 | ODESSA JCT, MILLTOWN JCT | 59Q6S-78, 78Q6S-59 | 1-00292195 Rev. #11 | 4 Hour(s) | No Impact | #N/A
2026-09-14 06:30 | 2026-09-29 16:00 | 15.3958 | DOBBIN TS | DL3, DL4, KL4, 20-P4S, D_BUS, T5-D | 1-00290612 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-09-30 06:30 | 2026-10-14 16:00 | 14.3958 | DOBBIN TS, DALE JCT, DOBBIN JCT | P4S.DOXDA, DL4, KL3, KL4, 20-P4S, 65P4S-52, K_BUS, T1-K, T2-K, P4S-2001 | 1-00290615 Rev. #3 | 8 Hour(s) | No Impact | #N/A
2026-10-18 06:30 | 2026-11-02 16:00 | 15.3958 | DOBBIN TS | DL3, DL4, KL3, 20-P3S, D_BUS, P3-P, T5-D | 1-00290621 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-11-04 06:30 | 2026-11-17 16:00 | 13.3958 | DOBBIN TS, DALE JCT | P3S.DOXPO, DL3, KL3, KL4, 20-P3S, 65P3S-2, K_BUS, P3-P, T1-K, T2-K | 1-00290627 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-11-28 08:00 | 2026-12-23 16:00 | 25.3333 | NORTHBROOKE DS, LODGEROOM DS | B1S.LOXNO, 74B1S-12, Q38B1S-14 | 1-00297913 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-04-19 08:00 | 2026-04-24 16:00 | 5.3333 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS | 128T1-T31H, L23L31, P2L31, 296-T31H, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H | 1-00289102 Rev. #10 | 34 Hour(s) | No Impact | #N/A
2026-09-14 06:30 | 2026-09-25 16:00 | 11.3958 | MERIVALE TS, TERRY FOX JCT | 319E34M-6, 6-E34M | 1-00295134 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-04 16:00 | 22.3333 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS, DUFFIN JCT, OSHAWA WILSON TS, CHERRYWOOD TS, WHITBY TS, WILSON JCT, WHITBY JCT, B23C H26C TIE JCT | 81-T23C, 81-T28C, 128T1-T31H, 54T2-T23C, 40T3-T23C, 54T4-T23C, K2L28, L23L28, L23L31, P2L31, 296-T23C, 296-T28C, 296-T31H, L28_BUS, L31_BUS, T28C.CLXDJ, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, T23C.BJXCH, T23C.CLXWJ, T23C.WJXBJ, T23C.WJXWH, T23C.WJXWI, T23C.WJXWY, 57-T31H, 54T7-T23C, L23_BUS | 1-00295709 Rev. #1 | 12 Hour(s) | No Impact | #N/A
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #1 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #48 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-30 07:30 | 2026-12-11 17:30 | 11.4167 | MASSON GS, IPB MASSON JCT, ORLEANS JCT 2, HAWTHORNE TS, ORLEANS TS, CUMBERLAND JCT, ST. ISIDORE TS, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00299005 Rev. #1 | 6 Hour(s) | D5A BEAU FIO | 250 690 250
2026-03-30 07:00 | 2026-04-17 17:00 | 18.4167 | CROSBY TS, ST. LAWRENCE TS, HINCHINBROOKE SS, SMITHS FALLS TS, CROSBY JCT, EASTON YULE JCT | L21H.CRXCR, L21H.CRXEA, L21H.CRXHI, L21H.EAXLA, L21H.EAXSM, 10-L21H, 23T1-L21H, 49-L21H, T3-L21H, T4-L21H | 1-00295831 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-04-20 08:00 | 2026-05-01 16:00 | 11.3333 | ST. LAWRENCE TS, CROSBY TS, BROCKVILLE TS, HINCHINBROOKE SS, CROSBY JCT, EASTON JCT | L20H.CRXCR, L20H.CRXEA, L20H.CRXHI, L20H.EAXBR, L20H.EAXLA, 10-L20H, 23T2-L20H, 24T2-L20H, 49-L20H, T2-L20H, T3-L20H | 1-00303502 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-05-09 08:00 | 2026-05-29 16:00 | 20.3333 | SMITHS FALLS TS, BROCKVILLE TS, ST. LAWRENCE TS, HINCHINBROOKE SS, EASTON YULE JCT, EASTON JCT | L22H.EAXBR, L22H.EAXEA, L22H.EAXHI, L22H.EAXLA, L22H.EAXSM, 10-L22H, 24T1-L22H, 49-L22H, T3-L22H | 1-00295760 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-06-14 12:00 | 2026-07-24 12:00 | 40 | CATARAQUI TS, HINCHINBROOKE SS, KINGSTON SOLAR JCT | X3H.CAXHI, HL3, L3L23, 10-X3H, T2-X3H, 371X3H-BO2 | 1-00302305 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-09-01 08:00 | 2026-12-13 23:00 | 103.625 | HINCHINBROOKE SS, CATARAQUI TS, LENNOX TS, LAFARGE JCT, GARDINER TS, GARDINER STR 44 JCT, WESTBROOK JCT, NPIF KINGSTON JCT | X2H.DEXWE, X2H.HIXCA, X2H.LAXDE, X2H.LAXLE, X2H.WEXGA, 10-X2H, 12-X2H, 1A-X2H, 1T3-X2H, H1T2-X2H | 1-00292309 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-04-02 08:00 | 2026-06-04 16:00 | 63.3333 | ODESSA JCT, MILLTOWN JCT | 59Q6S-78, 78Q6S-59 | 1-00290611 Rev. #9 | 12 Hour(s) | No Impact | #N/A
2026-05-18 08:00 | 2026-06-04 16:00 | 17.3333 | ODESSA JCT, MILLTOWN JCT | 59Q6S-78, 78Q6S-59 | 1-00292195 Rev. #11 | 4 Hour(s) | No Impact | #N/A
2026-11-28 08:00 | 2026-12-23 16:00 | 25.3333 | NORTHBROOKE DS, LODGEROOM DS | B1S.LOXNO, 74B1S-12, Q38B1S-14 | 1-00297913 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-09-28 08:00 | 2026-10-09 16:00 | 11.3333 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P | 1-00275118 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-11-13 16:00 | 15.3333 | ST. LAWRENCE TS, MASSENA JCT | L34P.ROXLA, 49-L34P | 1-00275119 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2025-11-25 08:00 | 2031-12-31 16:00 | 2227.3333 | ST. LAWRENCE TS | 49-L5C | 1-00301379 Rev. #1 | 2 Hour(s) | No Impact | #N/A
2025-12-12 13:31 | 2026-05-08 16:00 | 147.1035 | PIPERVILLE JCT | 644L24A-MSO3 | 1-00303243 Rev. #7 | 2 Hour(s) | FIO BEAU P33C | 0 0 0
2025-12-12 20:00 | 2026-05-08 08:00 | 146.5 | PIPERVILLE JCT | 644L24A-MSO1, 644L24A-MSO2, 644L24A-MSO4, 644L24A-MSO5, 644L24A-MSO6, 644L24A-MSO7 | 1-00299488 Rev. #10 | Non-recallable | FIO BEAU P33C | 0 0 0
2026-01-08 08:00 | 2026-05-29 09:30 | 141.0625 | GARDINER TS | 33T1B, T4J, 1A-X2H, 1A-X4H, 1T4-X4H, H1T1-X4H, T1, T4 | 1-00268235 Rev. #21 | 8 Hour(s) | No Impact | #N/A
2026-03-06 15:00 | 2026-11-11 16:00 | 250.0417 | PICTON TS | OLDT1, OLD28T1-X21 | 1-00304973 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-03-29 06:00 | 2026-04-03 16:00 | 5.4167 | MARINE JCT, OTONABEE TS, CHATS FALLS TS, CLARINGTON TS | 128T2-T22C, HT2L22, P1L22, 296-T22C, L22_BUS, T22C.CHXMJ, T22C.MJXCL, T22C.MJXOT, 2-T22C | 1-00289071 Rev. #8 | 34 Hour(s) | FIO BEAU P33C | 0 0 100
2026-04-07 07:00 | 2026-04-22 17:00 | 15.4167 | LENNOX TS, BOWMANVILLE SS | X520B.BOXLE, 12-X520B, R56-X520B | 1-00276875 Rev. #7 | 6 Hour(s) | No Impact | #N/A
2026-04-20 08:00 | 2026-05-01 16:00 | 11.3333 | HINCHINBROOKE SS | HL20, L1L20, 10-L20H | 1-00303504 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-04-26 07:00 | 2026-05-04 17:00 | 8.4167 | R. H. SAUNDERS GS, ST. LAWRENCE TS | S26L.SAXLA, 49-S26L | 1-00267874 Rev. #11 | 4 Hour(s) | No Impact | #N/A
2026-05-03 08:00 | 2026-05-29 16:00 | 26.3333 | MARINE JCT, OTONABEE TS, CHATS FALLS TS, CLARINGTON TS | 128T2-T22C, HT2L22, P1L22, 296-T22C, L22_BUS, T22C.CHXMJ, T22C.MJXCL, T22C.MJXOT, 2-T22C | 1-00295799 Rev. #3 | 8 Hour(s) | FIO BEAU P33C | 0 0 100
2026-05-12 07:30 | 2026-06-03 10:30 | 22.125 | DES JOACHIMS TS, PEMBROKE TS | 5D6, 6X6-D6, T7, T7-5D6, T7-W1 | 1-00283246 Rev. #13 | 6 Hour(s) | No Impact | #N/A
2026-05-17 08:00 | 2026-06-05 16:00 | 19.3333 | DOBBIN TS | T2, T2-A, T2-K | 1-00290609 Rev. #8 | 6 Hour(s) | No Impact | #N/A
2026-06-08 08:00 | 2026-09-02 16:00 | 86.3333 | DOBBIN TS | T2-K, T7-K | 1-00307293 Rev. #2 | 135 Min(s) | No Impact | #N/A
2026-08-24 08:00 | 2027-03-23 17:01 | 211.3757 | LENNOX TS | KL526 | 1-00285554 Rev. #4 | Non-recallable | No Impact | #N/A
2026-08-31 11:30 | 2026-09-10 17:00 | 10.2292 | LENNOX TS, GRETNA JCT, NAPANEE TS, PICTON TS | X22.GRXLE, X22.GRXNA, X22.GRXPI, 12-X22, T2-X22 | 1-00297891 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-08 08:00 | 2026-09-14 16:00 | 6.3333 | BOWMANVILLE SS | EL527, EL542, H1E, H3E, E1_BUS, E2_BUS, E1-E2 | 1-00295505 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-29 05:30 | 2026-11-11 11:30 | 43.25 | LENNOX TS, GRETNA JCT, NAPANEE TS, PICTON TS | X22.GRXLE, X22.GRXNA, X22.GRXPI, 12-X22, T2-X22 | 1-00292505 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-09-30 08:00 | 2026-11-30 16:00 | 61.3333 | DOBBIN TS | T2, T2-A, T2-K | 1-00290614 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-08 07:30 | 2026-10-23 16:30 | 15.375 | CARLING TS, OTTAWA JCT, MERIVALE TS, NEPEAN EPWORTH JCT, LISGAR TS | M5G.CAXLI, M5G.CAXOT, M5G.EPXME, M5G.EPXOT, A1A2, AL12, AL5, L1L5, 47-M5G, 6-A8M, 6-M5G, A2_BUS, L5_BUS, M5G-47, M5G-6 | 1-00287618 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-18 02:00 | 2026-10-23 17:00 | 5.625 | ST. LAWRENCE TS, R. H. SAUNDERS GS | S30L.SAXLA, 49-S30L, S30L-D | 1-00298374 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-28 08:00 | 2026-10-09 16:00 | 11.3333 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P | 1-00275118 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-10-29 08:00 | 2026-11-13 16:00 | 15.3333 | ST. LAWRENCE TS, MASSENA JCT | L34P.ROXLA, 49-L34P | 1-00275119 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-11-30 07:30 | 2026-12-11 17:30 | 11.4167 | MASSON GS, IPB MASSON JCT, ORLEANS JCT 2, HAWTHORNE TS, ORLEANS TS, CUMBERLAND JCT, ST. ISIDORE TS, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00299005 Rev. #1 | 6 Hour(s) | D5A BEAU FIO | 250 690 250
Back to main menu

## Table 4.6
Back to main menu
Table 4.6: Essa Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-03-01 08:00 | 2026-04-26 16:00 | 56.3333 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | T2Y, T2-L82, 51-H82V, T2, L82L88, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00305725 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2026-04-20 07:00 | 2026-04-26 16:01 | 6.3757 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | H1L82, L76L82, 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00276918 Rev. #44 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-10-03 16:01 | 18.334 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-07 08:00 | 2026-10-14 16:00 | 7.3333 | VAUGHAN 4 JCT, WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN MTS 4, HOLLAND TS, HOLLAND JCT | 51-H83V, 153-H83V, H83V.WJXCL, H83V.HJX4J, H83V.4JXWJ, H83V.4JXV4, H83V.HOXHJ | 1-00296676 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-03-01 08:00 | 2026-04-26 16:00 | 56.3333 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | T2Y, T2-L82, 51-H82V, T2, L82L88, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00305725 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2026-04-20 07:00 | 2026-04-26 16:01 | 6.3757 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | H1L82, L76L82, 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00276918 Rev. #44 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-10-03 16:01 | 18.334 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-07 08:00 | 2026-10-14 16:00 | 7.3333 | VAUGHAN 4 JCT, WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN MTS 4, HOLLAND TS, HOLLAND JCT | 51-H83V, 153-H83V, H83V.WJXCL, H83V.HJX4J, H83V.4JXWJ, H83V.4JXV4, H83V.HOXHJ | 1-00296676 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-06-01 06:15 | 2026-06-12 16:00 | 11.4062 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B | 1-00298740 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-06-01 06:15 | 2026-06-12 16:00 | 11.4062 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B | 1-00298740 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-03-01 08:00 | 2026-04-26 16:00 | 56.3333 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | T2Y, T2-L82, 51-H82V, T2, L82L88, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00305725 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2026-04-21 07:00 | 2026-05-29 16:00 | 38.375 | ORILLIA TS, MUSKOKA TS, BRACEBRIDGE JCT, ESSA TS, MIDHURST TS, COOPERS FALLS JCT, MINDEN TS | M7E.BRXMU, M7E.COXBR, M7E.COXMI, M7E.MIXES, M7E.MIXOR, M7E.ORXCO, 18-M7E, 87-M7E, T1-M7E, T2-M7E, T4-M7E | 1-00295032 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-05-21 04:00 | 2026-05-29 09:30 | 8.2292 | MUSKOKA TS, ESSA TS, MIDHURST TS, BRACEBRIDGE JCT, COOPERS FALLS JCT, MINDEN TS, ORILLIA TS | M7E.BRXMU, M7E.COXBR, M7E.COXMI, M7E.MIXES, M7E.MIXOR, M7E.ORXCO, SC2Y, 18-M7E, 87-M7E, T1-M7E, T2-M7E, T4-M7E, SC2Y-Y, 92M6E-MTU05, 92M7E-MTU05 | 1-00304050 Rev. #2 | Non-recallable | No Impact | #N/A
2026-04-27 08:00 | 2026-05-28 08:01 | 31.0007 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #17 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #7 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #2 | Non-recallable | FS FN P502X CLAN | -100 0 -100 700
2026-06-01 06:15 | 2026-06-12 16:00 | 11.4062 | BEAVER JCT, BROWN HILL TS, BEAVERTON JCT, LINDSAY TS, MINDEN TS, BEAVERTON TS | M81B.BEXBE, M81B.BEXBV, M81B.BSXBE, M81B.BVXLI, M81B.BVXMI, L81L89, 4T1-M81B, 87-M81B, T4-M81B | 1-00298740 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-04-27 08:00 | 2026-05-28 08:01 | 31.0007 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #17 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #7 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #2 | Non-recallable | FS FN P502X CLAN | -100 0 -100 700
2026-04-27 08:00 | 2026-05-28 08:01 | 31.0007 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #17 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-06-14 08:00 | 2026-07-05 16:00 | 21.3333 | HANMER TS, ESSA TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00295049 Rev. #4 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #7 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #2 | Non-recallable | FS FN P502X CLAN | -100 0 -100 700
2026-04-27 08:00 | 2026-05-28 08:01 | 31.0007 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #17 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-06-14 08:00 | 2026-07-05 16:00 | 21.3333 | HANMER TS, ESSA TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00295049 Rev. #4 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #7 | 48 Hour(s) | FS FN P502X CLAN | -100 0 -100 700
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #2 | Non-recallable | FS FN P502X CLAN | -100 0 -100 700
2026-03-17 07:30 | 2026-06-03 10:30 | 78.125 | DES JOACHIMS TS | T6, R6-L, R6-T, R6-S, TR6, T6-W1 | 1-00288699 Rev. #9 | 55 Day(s) | No Impact | #N/A
2026-05-12 07:30 | 2026-06-03 10:30 | 22.125 | DES JOACHIMS TS, PEMBROKE TS | 5D6, 6X6-D6, T7, T7-5D6, T7-W1 | 1-00283246 Rev. #13 | 6 Hour(s) | No Impact | #N/A
2026-06-04 14:01 | 2026-06-30 14:01 | 26 | DES JOACHIMS TS | T7-5D6, T6-P, T7-P | 1-00288711 Rev. #6 | 3 Hour(s) | No Impact | #N/A
2026-08-03 06:15 | 2026-10-01 16:00 | 59.4062 | OTTER CREEK JCT, DES JOACHIMS TS, MINDEN TS | D4M.OTXDE, D4M.OTXMI, 5-D4M, 87-D4M, B9D4M-B8 | 1-00295116 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-13 06:15 | 2026-11-06 16:00 | 24.4062 | DES JOACHIMS TS, MINDEN TS | D1M.MIXDE, 5-D1M, 87-D1M | 1-00295094 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-11-09 06:15 | 2026-11-27 16:00 | 18.4062 | OTTER CREEK JCT, DES JOACHIMS TS, MINDEN TS | D2M.OTXDE, D2M.OTXMI, 5-D2M, 87-D2M, B9D2M-B8, B9D4M-B8 | 1-00299045 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-30 07:15 | 2026-12-15 16:00 | 15.3646 | DES JOACHIMS TS, MINDEN TS | D3M.MIXDE, 5-D3M, 87-D3M | 1-00295024 Rev. #4 | 4 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.7
Back to main menu
Table 4.7: Niagara Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-03-22 06:15 | 2026-05-15 16:00 | 54.4062 | HAMILTON NEBO TS, NEBO JCT, BECK 2 TS, HANNON JCT, BEACH TS, MIDDLEPORT TS, DOFASCO KENILWORTH CTS | Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 25-Q24HM, 28-Q24HM, T3-Q24HM | 1-00287140 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-05-19 06:15 | 2026-06-26 16:00 | 38.4062 | BURLINGTON TS, BURLINGTON JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q23BM.BEXNI, Q23BM.BUXBD, Q23BM.BUXBU, Q23BM.MIXCA, Q23BM.NEXBU, 25-Q23BM, 28-Q23BM, 39-Q23BM, T16-Q23BM | 1-00287150 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-07-20 06:15 | 2026-07-31 16:00 | 11.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00289213 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-03-22 06:15 | 2026-05-15 16:00 | 54.4062 | HAMILTON NEBO TS, NEBO JCT, BECK 2 TS, HANNON JCT, BEACH TS, MIDDLEPORT TS, DOFASCO KENILWORTH CTS | Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 25-Q24HM, 28-Q24HM, T3-Q24HM | 1-00287140 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-05-19 06:15 | 2026-06-26 16:00 | 38.4062 | BURLINGTON TS, BURLINGTON JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q23BM.BEXNI, Q23BM.BUXBD, Q23BM.BUXBU, Q23BM.MIXCA, Q23BM.NEXBU, 25-Q23BM, 28-Q23BM, 39-Q23BM, T16-Q23BM | 1-00287150 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-07-20 06:15 | 2026-07-31 16:00 | 11.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00289213 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-05-03 05:30 | 2026-05-15 15:00 | 12.3958 | BECK 2 TS | L76TL35 | 1-00259337 Rev. #8 | 3 Day(s) | No Impact | #N/A
2026-05-10 05:30 | 2026-05-22 16:00 | 12.4375 | BECK 2 TS | K2L76 | 1-00259349 Rev. #29 | 3 Day(s) | No Impact | #N/A
2026-01-23 08:00 | 2026-09-03 17:00 | 223.375 | BECK 1 SS | 6E-7, E3_BUS, E4_BUS, E5_BUS, E6_BUS, E7_BUS, E5-E15, E6-E16, E8-E18, E9-E19, E8_BUS, E5-E6, E4-E5, E3-E4, E8-E9, AQ11S-A11, E9_BUS, A1-A11, E7-E8, A11_BUSNORTH, A11_BUSSOUTH, E3-E13, E4-E14 | 1-00305350 Rev. #27 | Non-recallable | No Impact | #N/A
2026-03-02 05:00 | 2026-04-24 18:00 | 53.5417 | NY NIAGARA 230 KV | 2322, 2402, 2602, 2802, 2502 | 1-00286533 Rev. #4 | Non-recallable | No Impact | #N/A
2026-03-03 03:00 | 2026-06-13 02:00 | 101.9583 | ALLANBURG WEST JCT, ABITIBI CONSOLIDATED NAN91 JCT, MIDDLEPORT TS | 25-Q26M, 64Q26M-25, Q26M-Q10P, Q28A-Q10P | 1-00301036 Rev. #13 | 2 Hour(s) | No Impact | #N/A
2026-03-03 07:00 | 2026-09-25 17:00 | 206.4167 | BECK 1 SS | E8-E9, AQ11S-A11, A1-A11, A11_BUSSOUTH | 1-00285434 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2026-03-03 08:00 | 2026-06-12 16:00 | 101.3333 | ALLANBURG TS, ALLANBURG WEST JCT, MIDDLEPORT TS, ABITIBI CONSOLIDATED NAN91 JCT, BECK 2 TS | Q26M.MIXAW, Q28A.ALXAB, 25-Q26M, 28-Q28A, 45-Q28A, 64Q26M-25, Q26M-Q10P, Q28A-Q10P | 1-00287129 Rev. #23 | 60 Hour(s) | No Impact | #N/A
2026-03-22 04:00 | 2026-04-10 16:00 | 19.5 | BECK 1 SS | AQ11S-A11, A1-A11, A11_BUSNORTH, A11_BUSSOUTH | 1-00285435 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-04-12 15:00 | 2026-05-08 16:00 | 26.0417 | BECK 1 SS | AQ11S-A11, A1-A11, A8Q12S, 20-Q12S, A11_BUSNORTH, A11_BUSSOUTH | 1-00285436 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-04-19 05:30 | 2026-05-01 15:00 | 12.3958 | BECK 2 TS | D2L301 | 1-00259313 Rev. #9 | 3 Day(s) | No Impact | #N/A
2026-04-27 06:15 | 2026-05-29 16:00 | 32.4062 | ALLANBURG TS, ABITIBI CONSOLIDATED NAN91 JCT, BECK 2 TS | Q28A.ALXAB, 28-Q28A, 45-Q28A, Q26M-Q10P | 1-00287146 Rev. #9 | 4 Hour(s) | No Impact | #N/A
2026-05-10 15:00 | 2026-06-05 16:00 | 26.0417 | BECK 1 SS | AQ11S-A11, A1-A11, A11_BUSNORTH, A11_BUSSOUTH | 1-00285437 Rev. #6 | 4 Hour(s) | No Impact | #N/A
2026-05-24 05:30 | 2026-06-05 16:00 | 12.4375 | BECK 2 TS | K1L23 | 1-00259342 Rev. #10 | 3 Day(s) | No Impact | #N/A
2026-05-31 05:30 | 2026-06-12 15:00 | 12.3958 | BECK 2 TS | TL21L23 | 1-00259318 Rev. #12 | 3 Day(s) | No Impact | #N/A
2026-06-07 15:00 | 2026-06-26 16:00 | 19.0417 | BECK 1 SS | 20-Q4N, AQ11S-A11, A3Q4N, A1-A11, A11_BUSNORTH, A11_BUSSOUTH, A3Q4N-A3 | 1-00285438 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-06-14 05:30 | 2026-06-26 15:00 | 12.3958 | BECK 2 TS | L25L302 | 1-00259315 Rev. #10 | 3 Day(s) | No Impact | #N/A
2026-06-21 05:30 | 2026-07-03 16:00 | 12.4375 | BECK 2 TS | K1L25 | 1-00259343 Rev. #6 | 3 Day(s) | No Impact | #N/A
2026-06-21 06:15 | 2026-07-06 16:00 | 15.4062 | BEAMSVILLE TS, WINONA TS, WINONA JCT | Q2AH.WIXBE, 115Q2AH-18, 18Q2AH-17 | 1-00298777 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-07-05 05:30 | 2026-07-17 15:00 | 12.3958 | BECK 2 TS | K1TL26 | 1-00259344 Rev. #6 | 2 Day(s) | No Impact | #N/A
2026-07-19 05:30 | 2026-07-31 15:00 | 12.3958 | BECK 2 TS | D1L302 | 1-00259309 Rev. #6 | 2 Day(s) | No Impact | #N/A
2026-08-09 05:30 | 2026-08-21 15:00 | 12.3958 | BECK 2 TS | TL21L24 | 1-00259321 Rev. #9 | 2 Day(s) | No Impact | #N/A
2026-08-23 05:30 | 2026-09-04 15:00 | 12.3958 | BECK 2 TS | K1K2 | 1-00259341 Rev. #9 | 2 Day(s) | No Impact | #N/A
2026-09-13 05:30 | 2026-09-25 15:00 | 12.3958 | BECK 2 TS | D1D2 | 1-00259300 Rev. #9 | 2 Day(s) | No Impact | #N/A
2026-09-16 04:00 | 2026-11-06 19:00 | 51.625 | NY NIAGARA 230 KV | 2102, 2002, 2202, 2322, 2302 | 1-00286541 Rev. #2 | Non-recallable | No Impact | #N/A
2026-10-01 08:15 | 2026-10-30 16:00 | 29.3229 | ALLANBURG TS, ALLANBURG WEST JCT, MIDDLEPORT TS, ABITIBI CONSOLIDATED NAN91 JCT, BECK 2 TS | Q26M.MIXAW, Q28A.ALXAB, 25-Q26M, 28-Q28A, 45-Q28A, 64Q26M-25, Q26M-Q10P, Q28A-Q10P | 1-00289214 Rev. #2 | 60 Hour(s) | No Impact | #N/A
2026-10-02 15:00 | 2026-10-18 05:30 | 15.6042 | BECK 2 TS | K2L29, K2-BO4, K1K2 | 1-00268449 Rev. #4 | Non-recallable | NY-W-EXP NY-W-IMP NY-S-EXP NY-S-IMP | 500 650 600 500
2026-11-15 06:30 | 2026-11-27 16:00 | 12.3958 | BECK 2 TS | D1L27 | 1-00259303 Rev. #8 | 3 Day(s) | No Impact | #N/A
Back to main menu

## Table 4.8
Back to main menu
Table 4.8: Northeast Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-10-13 07:00 | 2026-11-06 16:00 | 24.375 | HUNTA SS | L2L9 | 1-00287779 Rev. #3 | 8 Hour(s) | No Impact | #N/A
2026-05-31 14:00 | 2026-06-22 08:00 | 21.75 | OTTO HOLDEN TS, MATTAWA JCT | DT3L5, H4Z-L5H, 583L5A-TEMP2 | 1-00295073 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-07-13 08:00 | 2026-07-30 16:00 | 17.3333 | LOWER NOTCH JCT, WIDDIFIELD TS | W71D.WIXLO, 38-W71D, W71D-38 | 1-00298159 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-08 07:00 | 20.9583 | RAMORE TS | 120A9K-16 | 1-00302108 Rev. #1 | 2 Hour(s) | No Impact | #N/A
2026-10-19 06:00 | 2026-11-08 07:00 | 20.0417 | KIRKLAND LAKE TS | D4D9, D8D9, SC11D9, SC11SC, 16-A9K, D9_BUS, SC11, SC11D9-D9 | 1-00299098 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-11-16 08:00 | 2026-12-03 16:00 | 17.3333 | KIRKLAND LAKE TS, DYMOND TS, DANE JCT, GULL LAKE SOUTH JCT, NINE MILE JCT, NORTHLAND KIRKLAND LAKE CGS | D3K.DAXGU, D3K.DYXNI, D3K.GUXKI, D3K.GUXNP, D3K.NIXDA, 16-D3K, 32-D3K, 59D3K-16, 59D3K-68, 68D3K-32, 68D3K-16 | 1-00299028 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-11-15 07:00 | 2026-11-20 16:30 | 5.3958 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00296683 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-06-14 08:00 | 2026-07-05 16:00 | 21.3333 | HANMER TS, ESSA TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00295049 Rev. #4 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2026-06-14 08:00 | 2026-07-05 16:00 | 21.3333 | HANMER TS, ESSA TS | X504E.ESXHA, 18-X504E, 33-X504E | 1-00295049 Rev. #4 | 5 Hour(s) | FS FN P502X CLAN | 990 900 250 0
2026-08-09 08:00 | 2026-08-27 16:00 | 18.3333 | HANMER TS, MARTINDALE TS | X26S.MAXHA, 33-X26S, 9-X26S | 1-00295122 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-11-08 09:00 | 2026-11-13 17:00 | 5.3333 | HANMER TS, MARTINDALE TS, HANMER PARALLEL B JCT, MARTINDALE PARALLEL B JCT | X25S.MAXHA, 33-X25S, 9-X25S, X29S.HAXHB, X29S.HBXMB, X29S.MBXMA | 1-00299046 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-03-02 08:00 | 2026-04-02 16:00 | 31.3333 | CRYSTAL FALLS TS, WIDDIFIELD TS, MARTINDALE TS, GRANT JCT, A.P. NORTH BAY JCT | H24S.GRXCR, H24S.GRXMA, H24S.GRXTC, 7T6-H24S, 9-H24S, H24S-9 | 1-00294391 Rev. #22 | 5 Hour(s) | No Impact | #N/A
2026-05-05 08:00 | 2026-05-14 16:00 | 9.3333 | VERNER JCT, WARREN DS | L1S.VEXWA, 79L1S-39, 939L1S-79 | 1-00295042 Rev. #3 | 5 Hour(s) | No Impact | #N/A
2026-05-31 14:00 | 2026-06-22 08:00 | 21.75 | OTTO HOLDEN TS, MATTAWA JCT | DT3L5, H4Z-L5H, 583L5A-TEMP2 | 1-00295073 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-07-13 08:00 | 2026-07-30 16:00 | 17.3333 | LOWER NOTCH JCT, WIDDIFIELD TS | W71D.WIXLO, 38-W71D, W71D-38 | 1-00298159 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-09-02 08:00 | 2026-10-03 16:00 | 31.3333 | OTTO HOLDEN TS, WIDDIFIELD TS | H24S.WIXHO, 6-H24S, H24S-6 | 1-00294340 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-10-06 08:00 | 2026-10-29 16:00 | 23.3333 | CRYSTAL FALLS TS, MARTINDALE TS, PEDLEY JCT, WIDDIFIELD TS | H23S.PEXCR, H23S.PEXMA, H23S.PEXWI, 7T5-H23S, 9-H23S, H23S-9 | 1-00299061 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-08 07:00 | 20.9583 | RAMORE TS | 120A9K-16 | 1-00302108 Rev. #1 | 2 Hour(s) | No Impact | #N/A
2026-10-19 06:00 | 2026-11-08 07:00 | 20.0417 | KIRKLAND LAKE TS | D4D9, D8D9, SC11D9, SC11SC, 16-A9K, D9_BUS, SC11, SC11D9-D9 | 1-00299098 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-11-16 08:00 | 2026-12-03 16:00 | 17.3333 | KIRKLAND LAKE TS, DYMOND TS, DANE JCT, GULL LAKE SOUTH JCT, NINE MILE JCT, NORTHLAND KIRKLAND LAKE CGS | D3K.DAXGU, D3K.DYXNI, D3K.GUXKI, D3K.GUXNP, D3K.NIXDA, 16-D3K, 32-D3K, 59D3K-16, 59D3K-68, 68D3K-32, 68D3K-16 | 1-00299028 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-07-13 08:00 | 2026-07-30 16:00 | 17.3333 | LOWER NOTCH JCT, WIDDIFIELD TS | W71D.WIXLO, 38-W71D, W71D-38 | 1-00298159 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-09-23 06:00 | 2026-09-29 17:00 | 6.4583 | PINARD TS, PORCUPINE TS | D501P.POXPI, 30-D501P, T1-D501P, T2-D501P | 1-00294189 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-10-05 16:00 | 2026-11-09 07:00 | 34.625 | PINARD TS | L20L21, PL20, 31-L20D | 1-00304043 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-10-05 16:00 | 2026-11-09 07:00 | 34.625 | PINARD TS | 31-L20D | 1-00302163 Rev. #3 | 5 Hour(s) | No Impact | #N/A
2026-10-13 07:00 | 2026-11-06 16:00 | 24.375 | HUNTA SS | L2L9 | 1-00287779 Rev. #3 | 8 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-08 07:00 | 20.9583 | RAMORE TS | 120A9K-16 | 1-00302108 Rev. #1 | 2 Hour(s) | No Impact | #N/A
2026-10-19 06:00 | 2026-11-08 07:00 | 20.0417 | KIRKLAND LAKE TS | D4D9, D8D9, SC11D9, SC11SC, 16-A9K, D9_BUS, SC11, SC11D9-D9 | 1-00299098 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-11-16 08:00 | 2026-12-03 16:00 | 17.3333 | KIRKLAND LAKE TS, DYMOND TS, DANE JCT, GULL LAKE SOUTH JCT, NINE MILE JCT, NORTHLAND KIRKLAND LAKE CGS | D3K.DAXGU, D3K.DYXNI, D3K.GUXKI, D3K.GUXNP, D3K.NIXDA, 16-D3K, 32-D3K, 59D3K-16, 59D3K-68, 68D3K-32, 68D3K-16 | 1-00299028 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-07-13 08:00 | 2026-07-30 16:00 | 17.3333 | LOWER NOTCH JCT, WIDDIFIELD TS | W71D.WIXLO, 38-W71D, W71D-38 | 1-00298159 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-07-13 08:00 | 2026-07-30 16:00 | 17.3333 | LOWER NOTCH JCT, WIDDIFIELD TS | W71D.WIXLO, 38-W71D, W71D-38 | 1-00298159 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-05-07 12:00 | 2026-05-20 16:00 | 13.1667 | HANMER TS, ALGOMA TS | X27A.ALXHA, 26-X27A, 33-X27A | 1-00295045 Rev. #5 | 5 Hour(s) | EWTE | 175
2026-08-23 08:00 | 2026-09-24 16:00 | 32.3333 | AUBREY FALLS JCT, WAWA TS, MISSISSAGI TS | P25W.AUXMI, P25W.AUXWA, 14-P25W, 34-P25W | 1-00294347 Rev. #2 | 5 Hour(s) | EWTE | 280
2026-10-25 08:00 | 2026-11-19 16:00 | 25.3333 | AUBREY FALLS JCT, WAWA TS, MISSISSAGI TS | P26W.AUXMI, P26W.AUXWA, 34-P26W, 14-P26W | 1-00302105 Rev. #1 | 5 Hour(s) | EWTE | 280
2026-12-06 08:00 | 2026-12-17 16:00 | 11.3333 | MISSISSAGI TS, ALGOMA TS | A23P.MIXAL, 26-A23P, 34-A23P | 1-00298969 Rev. #1 | 5 Hour(s) | EWTE | 175
2024-06-20 18:00 | 2027-12-31 16:00 | 1288.9167 | PATRICK ST TS | 1900-07-23 | 1-00257104 Rev. #19 | Non-recallable | No Impact | #N/A
2026-02-22 16:30 | 2026-04-10 17:00 | 47.0208 | MACKAY TS, BATCHAWANA TS | PL3, 668, 9154-K3G, 9153K3G-TL3 | 1-00295004 Rev. #18 | 4 Hour(s) | No Impact | #N/A
2026-04-19 12:00 | 2026-05-09 07:00 | 19.7917 | THIRD LINE TS, ECHO RIVER TS | 548, 9158P22G-1709, P22G.ECXTH | 1-00295035 Rev. #7 | 5 Hour(s) | No Impact | #N/A
2026-04-19 12:00 | 2026-05-09 07:00 | 19.7917 | THIRD LINE TS, ECHO RIVER TS | 408, 415, 548, P22G.ECXTH, L22_BUS, AWT3, DL21, DL22, T3-WT3, 1709-P22G | 1-00291014 Rev. #12 | 10 Hour(s) | No Impact | #N/A
2026-05-10 16:00 | 2026-05-20 09:00 | 9.7083 | MISSISSAGI TS, P21G POLE 6 JCT, THIRD LINE TS | P21G.MIXP8, 34-P21G, 545, P21G.P8XTH | 1-00295048 Rev. #7 | 5 Hour(s) | No Impact | #N/A
2026-05-10 16:00 | 2026-05-20 09:00 | 9.7083 | THIRD LINE TS, MISSISSAGI TS, P21G POLE 6 JCT | P21G.MIXP8, 415, 34-P21G, 545, 548, P21G.P8XTH, DL21 | 1-00290754 Rev. #13 | 8 Hour(s) | No Impact | #N/A
2026-05-12 08:00 | 2026-05-28 17:00 | 16.375 | TIMMINS TS, PORCUPINE TS | P15T.TIXPO, 19-P15T, 30-P15T, K2-P3 | 1-00295083 Rev. #3 | 5 Hour(s) | No Impact | #N/A
2026-05-21 13:00 | 2026-06-09 08:00 | 18.7917 | THIRD LINE TS | 405, 402, 412, 400, K24G-BO, AWT3 | 1-00292522 Rev. #12 | 10 Hour(s) | EWTE | 175
2026-05-26 08:00 | 2026-07-08 16:00 | 43.3333 | MARTINDALE TS, ETHEL LAKE JCT, CREIGHTON JCT, ESPANOLA TS | 52S2B-32, 66S2B-52, 9-S2B, S2B-9 | 1-00295068 Rev. #8 | 6 Hour(s) | No Impact | #N/A
2026-05-26 08:00 | 2026-07-09 16:00 | 44.3333 | CLARABELLE JCT, VALE FROOD STOBIE 2 JCT, HANMER TS, VALE COPPER 4 CTS, CLARABELLE TS | X23N.CLXCL, X23N.CLXFR, X23N.CLXIN, X23N.FRXHA, 33-X23N, 28T1-X23N | 1-00295078 Rev. #3 | 5 Hour(s) | No Impact | #N/A
2026-06-01 17:00 | 2026-09-21 08:00 | 111.625 | PORCUPINE TS | T8, T8-HT8, 30T8-H2, TEMPH2-BO1 | 1-00305822 Rev. #1 | 46 Day(s) | No Impact | #N/A
2026-07-12 12:00 | 2026-07-24 09:00 | 11.875 | THIRD LINE TS | 1610, 1613, 412, 415, 532, 1657, 549, T2, 533, 534, SSB, T2M_BUS, T2H_BUS, T3-WT3, T3 | 1-00290760 Rev. #3 | 8 Hour(s) | No Impact | #N/A
2026-07-24 09:00 | 2026-10-14 07:00 | 81.9167 | THIRD LINE TS | 1657, 549, T2 | 1-00302186 Rev. #2 | Non-recallable | No Impact | #N/A
2026-08-04 08:00 | 2026-08-14 16:00 | 10.3333 | PINARD TS, PINARD JCT, OTTER RAPIDS SS, ABITIBI CANYON SS | R21D.PIXCA, R21D.PIXOT, R21D.PIXPI, 31-R21D | 1-00295120 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-08-10 13:00 | 2026-08-17 12:00 | 6.9583 | MACKAY TS, MILE HILL JCT | 678, 682, 680, L24_BUS, 539K24G-MSO | 1-00290726 Rev. #2 | 8 Hour(s) | EWTE | 175
2026-08-22 08:00 | 2026-09-01 16:00 | 10.3333 | MATTAWA JCT, NORTH BAY TS | 15L5H-A3, 583L5A-387 | 1-00300376 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-09-13 12:00 | 2026-09-25 09:00 | 11.875 | THIRD LINE TS | 408, DL21, DL22, AL25, DL26, L25L26, 1709-G25, 1709-G26 | 1-00291016 Rev. #4 | 8 Hour(s) | No Impact | #N/A
2026-09-28 07:00 | 2026-10-08 09:00 | 10.0833 | THIRD LINE TS | 405, 412, 545, K24G-BO, AWT3, AL25, DL26, L25L26, 1709-G25, 1709-G26 | 1-00292533 Rev. #3 | 8 Hour(s) | EWTE | 175
2026-10-14 07:00 | 2026-10-23 17:00 | 9.4167 | THIRD LINE TS | 412, 415, 1657, 549, T2, T2H_BUS | 1-00289949 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-12-07 08:00 | 2026-12-17 16:00 | 10.3333 | MATTAWA JCT, NORTH BAY TS | 15L5H-A3, 583L5A-387 | 1-00298970 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-05-07 12:00 | 2026-05-20 16:00 | 13.1667 | HANMER TS, ALGOMA TS | X27A.ALXHA, 26-X27A, 33-X27A | 1-00295045 Rev. #5 | 5 Hour(s) | EWTE | 175
2026-12-06 08:00 | 2026-12-17 16:00 | 11.3333 | MISSISSAGI TS, ALGOMA TS | A23P.MIXAL, 26-A23P, 34-A23P | 1-00298969 Rev. #1 | 5 Hour(s) | EWTE | 175
Back to main menu

## Table 4.9
Back to main menu
Table 4.9: Northwest Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-04-28 07:00 | 2026-05-06 16:00 | 8.375 | MOOSE LAKE TS | T2B, T3B, TL2, TL6, AT-MSO, ATPT-AT, T2, T3, TSS2, T2-AT, T3-AT | 1-00295026 Rev. #9 | 8 Hour(s) | No Impact | #N/A
2026-09-11 07:00 | 2026-10-15 16:00 | 34.375 | MOOSE LAKE TS | T2B, T3B, TL2, TL6, AT-MSO, ATPT-AT, T2, T3, TSS2, T2-AT, T3-AT | 1-00295125 Rev. #3 | 8 Hour(s) | No Impact | #N/A
2026-06-05 17:00 | 2026-06-20 17:00 | 15 | MACKENZIE TS, DINORWIC JCT | HL21, HL93, 20-D26A, H_BUS, 519D26A-20 | 1-00285116 Rev. #10 | 1 Day(s) | EWTW | 125
2026-09-18 08:00 | 2026-10-20 16:00 | 32.3333 | MARGACH DS, RABBIT LAKE SS | 15-K6F, 24T2-L, K6FT1-T2 | 1-00304036 Rev. #2 | 5 Hour(s) | EWTW | 125
2026-11-23 08:00 | 2026-12-11 16:00 | 18.3333 | RABBIT LAKE SS | L2L4 | 1-00298951 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2024-05-14 13:00 | 2026-12-31 16:00 | 961.125 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00254393 Rev. #21 | 6 Hour(s) | EWTW | 25
2024-05-14 15:54 | 2026-12-31 23:59 | 961.3368 | WHITESHELL TS | R4, R70, PS7 | 1-00254335 Rev. #14 | Non-recallable | No Impact | #N/A
2025-11-18 08:00 | 2026-12-31 16:00 | 408.3333 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00299527 Rev. #10 | 2 Hour(s) | EWTW | 25
2026-04-01 07:00 | 2026-04-17 16:00 | 16.375 | MARATHON TS, GREENWICH WF CGS JCT | 15-M24L, 253M24L-MSO2 | 1-00295018 Rev. #7 | 4 Hour(s) | EWTW | 125
2026-04-09 07:00 | 2026-04-27 17:00 | 18.4167 | MACKENZIE TS | HL93 | 1-00288959 Rev. #7 | 5 Day(s) | EWTW | 125
2026-04-13 07:00 | 2026-04-27 16:00 | 14.375 | MACKENZIE TS | HL93, L22L93, 20-N93A | 1-00303547 Rev. #2 | 24 Hour(s) | EWTW | 125
2026-04-13 08:00 | 2026-04-27 16:00 | 14.3333 | MARMION LAKE JCT, MACKENZIE TS | N93A.MKXAT, HL93, L22L93, 20-N93A | 1-00304836 Rev. #8 | 24 Hour(s) | EWTW | 125
2026-04-18 08:00 | 2026-05-06 16:00 | 18.3333 | MURILLO JCT, BIRCH TS | B6M.BIXMU, 17-B6M, B6M-8 | 1-00303550 Rev. #2 | 5 Hour(s) | EWTW | 125
2026-04-20 09:00 | 2026-05-08 17:00 | 18.3333 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00302492 Rev. #4 | 6 Hour(s) | EWTW | 25
2026-05-01 07:00 | 2026-05-13 17:00 | 12.4167 | MACKENZIE TS | PL25 | 1-00288960 Rev. #7 | 5 Day(s) | EWTW | 125
2026-05-21 08:00 | 2026-05-28 16:00 | 7.3333 | LAKEHEAD TS, BIRCH TS, PINE PORTAGE SS | R1LB.BIXLA, R1LB.LAXPI, 12-R1LB, 17-R1LB, 26-R1LB | 1-00304037 Rev. #2 | 16 Hour(s) | No Impact | #N/A
2026-06-05 17:00 | 2026-06-20 17:00 | 15 | MACKENZIE TS, DINORWIC JCT | HL21, HL93, 20-D26A, H_BUS, 519D26A-20 | 1-00285116 Rev. #10 | 1 Day(s) | EWTW | 125
2026-06-29 07:00 | 2026-07-10 16:00 | 11.375 | MACKENZIE TS, LAKEHEAD TS | A21L.MKXLA, HL21, L21L25, 12-A21L, 20-A21L | 1-00285118 Rev. #15 | 1 Day(s) | EWTW | 150
2026-06-29 08:00 | 2026-07-05 16:00 | 6.3333 | LAKEHEAD TS, MACKENZIE TS | A21L.MKXLA, 12-A21L, 20-A21L | 1-00295092 Rev. #8 | 6 Min(s) | EWTW | 150
2026-06-29 08:00 | 2026-07-10 16:00 | 11.3333 | MACKENZIE TS, LAKEHEAD TS | A21L: MACKENZIE TS x LAKEHEAD TS, 20-A21L | 1-00304070 Rev. #2 | 24 Hour(s) | EWTW | 150
2026-06-29 09:16 | 2026-07-10 16:00 | 11.2806 | LAKEHEAD TS, MACKENZIE TS | A21L.MKXLA, 12-A21L, 20-A21L | 1-00287610 Rev. #6 | 5 Hour(s) | EWTW | 150
2026-07-12 07:00 | 2026-07-24 16:00 | 12.375 | MACKENZIE TS, FORT FRANCES TS | F25A.FOXMK, L21L25, PL25, 20-F25A, 22-F25A | 1-00288965 Rev. #3 | 2 Day(s) | EWTW | 125
2026-07-12 08:00 | 2026-07-24 16:00 | 12.3333 | FORT FRANCES TS, MACKENZIE TS | F25A.FOXMK, 20-F25A, 22-F25A | 1-00295104 Rev. #2 | 5 Hour(s) | EWTW | 125
2026-07-27 07:00 | 2026-08-04 17:00 | 8.4167 | LAKEHEAD TS, MACKENZIE TS | A22L.MKXLA, L22L93, PL22, 12-A22L, 20-A22L | 1-00285119 Rev. #7 | 1 Day(s) | EWTW | 150
2026-07-27 08:00 | 2026-08-14 16:00 | 18.3333 | LAKEHEAD TS, MACKENZIE TS | A22L.MKXLA, 12-A22L, 20-A22L | 1-00287611 Rev. #2 | 6 Hour(s) | EWTW | 150
2026-07-27 09:16 | 2026-08-14 16:00 | 18.2806 | LAKEHEAD TS, MACKENZIE TS | A22L.MKXLA, 12-A22L, 20-A22L | 1-00295111 Rev. #2 | 5 Hour(s) | EWTW | 150
2026-08-21 08:00 | 2026-09-03 16:00 | 13.3333 | MARATHON DS, MARATHON TS, TERRACE BAY SS, PIC JCT, MARATHON DS JCT | T1M.PIXMA, T1M.PIXMD, 77T1M, 15-T1M, 2735T1-L | 1-00300375 Rev. #2 | 5 Hour(s) | EWTW | 125
2026-09-18 08:00 | 2026-10-20 16:00 | 32.3333 | MARGACH DS, RABBIT LAKE SS | 15-K6F, 24T2-L, K6FT1-T2 | 1-00304036 Rev. #2 | 5 Hour(s) | EWTW | 125
2026-10-06 08:00 | 2026-10-29 16:00 | 23.3333 | LAKEHEAD TS, BIRCH TS, PINE PORTAGE SS | R2LB.BIXLA, R2LB.LAXPI, 12-R2LB, 17-R2LB, 26-R2LB | 1-00295286 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-10-12 08:00 | 2026-10-18 16:00 | 6.3333 | ALEXANDER SS, LAKEHEAD TS, BIRCH TS, PINE PORTAGE SS | A8L.LAXAL, R2LB.BIXLA, R2LB.LAXPI, 12-A8L, 12-R2LB, 17-R2LB, 26-R2LB, 4-A8L | 1-00299074 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2026-10-22 07:00 | 2026-11-05 16:00 | 14.375 | MOOSE LAKE TS | L1L3, L3L6, 3-A3M | 1-00299139 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-22 08:00 | 2026-11-06 16:00 | 15.3333 | MACKENZIE TS, MOOSE LAKE TS | A3M.MAXMO, 20-A3M, 3-A3M | 1-00287613 Rev. #1 | 5 Hour(s) | No Impact | #N/A
2026-11-22 08:00 | 2026-12-06 16:00 | 14.3333 | ALEXANDER SS, MINNOVA JCT | 4-A5A, A5A-5 | 1-00299012 Rev. #1 | 6 Hour(s) | EWTW | 125
2026-11-23 08:00 | 2026-12-05 16:00 | 12.3333 | FORT FRANCES TS, MACKENZIE TS | F25A.FOXMK, 20-F25A, 22-F25A | 1-00287614 Rev. #1 | 2 Day(s) | EWTW | 125
2027-03-30 08:00 | 2027-07-08 16:00 | 100.3333 | LAKEHEAD TS, MACKENZIE TS | A22L.MKXLA, L22L93, L22L23, PL22, L22_BUS | 1-00299000 Rev. #1 | 8 Hour(s) | EWTW | 150
2019-05-29 08:00 | 2026-12-31 16:00 | 2773.3333 | FORT FRANCES TS | SC1.2, SC1, SC1.2-1 | 1-00117652 Rev. #13 | Non-recallable | No Impact | #N/A
2026-02-09 08:00 | 2026-04-12 16:00 | 62.3333 | RABBIT LAKE SS | HL3 | 1-00294996 Rev. #16 | 5 Day(s) | No Impact | #N/A
2026-03-06 15:00 | 2026-04-05 16:00 | 30.0417 | SAPAWE JCT, KASHABOWIE JCT | FR67-3, SPWE-17 | 1-00299815 Rev. #7 | 3 Hour(s) | No Impact | #N/A
2026-03-23 07:00 | 2026-03-30 16:00 | 7.375 | RABBIT LAKE SS, KEEWATIN JCT | 15-SK1, 299SK1-15 | 1-00295013 Rev. #8 | 8 Hour(s) | No Impact | #N/A
2026-03-23 07:00 | 2026-03-30 16:00 | 7.375 | RABBIT LAKE SS, KEEWATIN JCT | 15-SK1, 299SK1-15 | 1-00297691 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2026-03-25 15:00 | 2026-04-04 16:00 | 10.0417 | SAPAWE JCT, KASHABOWIE JCT | FR67-3, SPWE-17 | 1-00303546 Rev. #1 | 3 Hour(s) | No Impact | #N/A
2026-05-14 08:00 | 2026-05-27 16:00 | 13.3333 | RABBIT LAKE SS | L3L4 | 1-00298987 Rev. #3 | 8 Hour(s) | No Impact | #N/A
2026-06-29 08:00 | 2026-07-24 16:00 | 25.3333 | MACKENZIE TS | L21L25 | 1-00287615 Rev. #8 | Non-recallable | No Impact | #N/A
2026-07-06 11:00 | 2026-07-27 16:00 | 21.2083 | FORGIE JCT, KEEWATIN JCT | 299SK1-90, FORGIE-2 | 1-00300324 Rev. #2 | 5 Hour(s) | No Impact | #N/A
2026-07-09 08:00 | 2026-07-23 16:00 | 14.3333 | LAKEHEAD TS | PL37 | 1-00295102 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-07-29 08:00 | 2026-09-13 16:00 | 46.3333 | RABBIT LAKE SS | HL7 | 1-00295115 Rev. #3 | 5 Day(s) | No Impact | #N/A
2026-08-11 17:00 | 2026-08-19 17:00 | 8 | MARATHON TS | T12, SC21T12-T, T12-H, T12-K, T12-SS | 1-00299165 Rev. #3 | 2 Hour(s) | No Impact | #N/A
2026-08-19 07:00 | 2026-09-07 17:00 | 19.4167 | MACKENZIE TS | HL21 | 1-00288970 Rev. #3 | 5 Day(s) | No Impact | #N/A
2026-08-25 08:00 | 2026-09-26 16:00 | 32.3333 | BIRCH TS, PORT ARTHUR TS 1 | P7B.BIXPO, 2P7B, 17-P7B | 1-00295071 Rev. #6 | 5 Hour(s) | No Impact | #N/A
2026-10-09 07:00 | 2026-10-22 19:00 | 13.5 | DRYDEN TS | HL26, HL23, T22R22, H_BUS, T22, R22, T22-H, T22-P, T22-T22R22, TSS22-T | 1-00288972 Rev. #1 | 3 Day(s) | No Impact | #N/A
2026-10-09 08:00 | 2026-10-22 16:00 | 13.3333 | DRYDEN TS | HL23, PL2, PL3, T22R22, 25-D5D, P_BUS, T22, TSS22, R22, T22-H, T22-P, T22-T22R22, TSS22-T | 1-00299072 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-02 08:00 | 2026-11-20 16:00 | 18.3333 | RABBIT LAKE SS | L2L7 | 1-00298950 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2026-11-05 07:00 | 2026-11-15 16:00 | 10.375 | LAKEHEAD TS, MARATHON TS | PL37, W1L37, 12-M37L, L37_BUS, 15-M37L | 1-00288977 Rev. #5 | 8 Hour(s) | EWTW | 125
2026-11-16 08:00 | 2026-11-22 16:00 | 6.3333 | SAPAWE JCT, KASHABOWIE JCT | FR67-3, SPWE-17 | 1-00299031 Rev. #1 | 8 Hour(s) | No Impact | #N/A
2027-06-23 07:00 | 2027-09-04 17:00 | 73.4167 | MARATHON TS | KL1 | 1-00297200 Rev. #4 | Non-recallable | No Impact | #N/A
Back to main menu

## Table 4.10
Back to main menu
Table 4.10: Ottawa Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-17 08:00 | 2026-09-23 16:00 | 6.3333 | HAWTHORNE TS | HT5L31 | 1-00297864 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-11-30 07:30 | 2026-12-11 17:30 | 11.4167 | MASSON GS, IPB MASSON JCT, ORLEANS JCT 2, HAWTHORNE TS, ORLEANS TS, CUMBERLAND JCT, ST. ISIDORE TS, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00299005 Rev. #1 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2026-11-30 08:00 | 2026-12-11 16:00 | 11.3333 | HAWTHORNE TS | HT5L5, KL5 | 1-00297876 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-06-10 13:30 | 2026-07-13 19:30 | 33.25 | MERIVALE TS, NEPEAN TS | M32S.NEXME, 6-M32S, M32S-1, T4-M32S | 1-00295059 Rev. #4 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #1 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #48 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-03-16 13:30 | 2026-04-07 19:30 | 22.25 | MERIVALE TS, ALBION JCT, ELLWOOD MTS JCT, HAWTHORNE TS, ALBION TS | M31A.AJXEJ, M31A.ALXME, M31A.EJXHA, 48-M31A, 6-M31A, 84T1-M31A | 1-00277694 Rev. #27 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-04-13 08:00 | 2026-04-24 15:00 | 11.2917 | HAWTHORNE TS | T2, R2-T2, T2-HT2, T2-LT2 | 1-00297896 Rev. #6 | 10 Hour(s) | FIO BEAU P33C | 150 0 0
2026-04-27 03:30 | 2026-05-06 19:30 | 9.6667 | ALBION TS, ALBION JCT, MERIVALE TS, ELLWOOD MTS JCT, HAWTHORNE TS | M30A.AJXEJ, M30A.ALXME, M30A.EJXHA, 48-M30A, 6-M30A, 84T2-M30A | 1-00285664 Rev. #9 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-05-14 07:00 | 2026-05-24 15:00 | 10.3333 | HAWTHORNE TS | T1, T1-HT1, T1-LT1 | 1-00270247 Rev. #42 | 6 Hour(s) | FIO BEAU P33C | 150 0 0
2026-06-10 13:30 | 2026-07-13 19:30 | 33.25 | MERIVALE TS, NEPEAN TS | M32S.NEXME, 6-M32S, M32S-1, T4-M32S | 1-00295059 Rev. #4 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-09-14 06:30 | 2026-09-25 16:00 | 11.3958 | MERIVALE TS, TERRY FOX JCT | 319E34M-6, 6-E34M | 1-00295134 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-10-26 03:30 | 2026-11-05 19:30 | 10.6667 | ALBION TS, ALBION JCT, MERIVALE TS, ELLWOOD MTS JCT, HAWTHORNE TS | M30A.AJXEJ, M30A.ALXME, M30A.EJXHA, 48-M30A, 6-M30A, 84T2-M30A | 1-00294345 Rev. #5 | 2 Hour(s) | FIO BEAU P33C | 0 0 0
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, DL3, HL3, 2-C3S, A9-C3S | 1-00299036 Rev. #1 | 8 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, A1A2, 2-C3S, A9-C3S, A2_BUS, T2-A | 1-00196163 Rev. #48 | 6 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-16 06:30 | 2026-11-27 16:30 | 11.4167 | CHATS FALLS TS, SOUTH MARCH TS | C3S.CFXSO, 2-C3S, A9-C3S | 1-00299033 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 500 0 150
2026-11-30 07:30 | 2026-12-11 17:30 | 11.4167 | MASSON GS, IPB MASSON JCT, ORLEANS JCT 2, HAWTHORNE TS, ORLEANS TS, CUMBERLAND JCT, ST. ISIDORE TS, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00299005 Rev. #1 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2026-11-30 08:00 | 2026-12-11 16:00 | 11.3333 | HAWTHORNE TS | HT5L5, KL5 | 1-00297876 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2025-11-27 08:00 | 2026-10-14 08:00 | 321 | RUSSELL TS | 36T2-A5RK, A5RK-TEMPNEWT2 | 1-00296803 Rev. #11 | Immediate | No Impact | #N/A
2025-11-27 08:00 | 2027-04-04 07:00 | 492.9583 | RUSSELL TS | 36T1-A6R, A6R-TEMPNEWT1 | 1-00296798 Rev. #9 | Immediate | No Impact | #N/A
2026-04-08 07:00 | 2026-04-13 16:00 | 5.375 | HAWTHORNE TS | SC23SC | 1-00297854 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-05-08 07:00 | 2026-05-13 16:00 | 5.375 | HAWTHORNE TS | SC22SC | 1-00297850 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-05-10 08:00 | 2026-05-29 16:00 | 19.3333 | ORLEANS JCT, CUMBERLAND DS JCT | 42H9A-77, 78H9A-77 | 1-00295047 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2026-05-19 08:00 | 2026-05-29 16:00 | 10.3333 | CITY VIEW JCT, MERIVALE TS, VAL TETREAU JCT, WOODROFFE TS | F10MV.CIXME, F10MV.CIXVA, F10MV.CIXWO, 24-F10MV, 6-F10MV, 97-F10MV | 1-00305875 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-05-27 07:00 | 2026-06-01 16:00 | 5.375 | HAWTHORNE TS | SC23K | 1-00297855 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-06-10 08:00 | 2026-06-16 16:00 | 6.3333 | HAWTHORNE TS | DL42, KL42, 48-A42T | 1-00297857 Rev. #2 | 4 Hour(s) | FIO BEAU P33C | 200 0 0
2026-06-17 08:00 | 2026-06-23 16:00 | 6.3333 | HAWTHORNE TS | DL42 | 1-00297858 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-09 08:00 | 2026-09-15 16:00 | 6.3333 | HAWTHORNE TS | KL41 | 1-00297862 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-24 08:00 | 2026-09-30 16:00 | 6.3333 | HAWTHORNE TS | LT1L41 | 1-00297867 Rev. #2 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-10-08 07:30 | 2026-10-23 16:30 | 15.375 | CARLING TS, OTTAWA JCT, MERIVALE TS, NEPEAN EPWORTH JCT, LISGAR TS | M5G.CAXLI, M5G.CAXOT, M5G.EPXME, M5G.EPXOT, A1A2, AL12, AL5, L1L5, 47-M5G, 6-A8M, 6-M5G, A2_BUS, L5_BUS, M5G-47, M5G-6 | 1-00287618 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-08 07:30 | 2026-11-06 10:30 | 29.125 | VAL TETREAU JCT, MERIVALE TS, HINCHEY TS | V12M.HIXVA, V12M.VAXME, AL12, L3L12, 6-V12M, 7-V12M, 97-V12M, L12_BUS | 1-00299068 Rev. #3 | 8 Hour(s) | No Impact | #N/A
2026-10-08 08:00 | 2026-10-15 16:00 | 7.3333 | HAWTHORNE TS | DLT1 | 1-00297871 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2026-10-25 08:00 | 2026-11-06 16:00 | 12.3333 | HAWTHORNE TS, KING EDWARD TS, OVERBROOK TS, CYRVILLE JCT, BLACKBURN JCT, MOULTON JCT | A4K.BLXCY, A4K.HAXBL, A4K.KIXOV, 48-A4K, 63-A4K, 8A4K-48, A4K-63, A4K-48 | 1-00302104 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2027-03-14 07:00 | 2027-04-09 17:00 | 26.4167 | HAWTHORNE TS, RUSSELL TS, CYRVILLE JCT | 48-A2, 48-A5RK, 66A2-48, A5RK-48 | 1-00298999 Rev. #4 | 4 Hour(s) | No Impact | #N/A
2027-04-13 07:00 | 2027-04-27 17:00 | 14.4167 | HAWTHORNE TS, RUSSELL TS | 48-A6R, 48-A5RK, A5RK-48, 36A6R-25 | 1-00297198 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2027-05-04 08:00 | 2027-05-18 16:00 | 14.3333 | BORROMEE JCT, ORLEANS TS, HAWTHORNE TS | 325T1-H9A, 48-H9A, 64H9A-BO | 1-00295131 Rev. #4 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2027-05-26 07:00 | 2027-06-09 17:00 | 14.4167 | BLACKBURN JCT, CYRVILLE JCT, HAWTHORNE TS, BILBERRY CREEK TS, BILBERRY CREEK JCT, NATIONAL RESEARCH JCT, KING EDWARD TS, OVERBROOK TS, MOULTON JCT | A2.BIXBI, A2.BLXCY, A2.CYXBI, A2.CYXNT, A2.HAXBL, A4K.BLXCY, A4K.HAXBL, A4K.KIXOV, 48-A2, 48-A4K, 63-A4K, 8A4K-48, A1-A2, A4K-63, A4K-48, T1-A | 1-00298967 Rev. #1 | 4 Hour(s) | FIO BEAU P33C | 0 0 0
2027-06-12 07:00 | 2027-06-19 17:00 | 7.4167 | HAWTHORNE TS | KL42 | 1-00298961 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2027-06-19 16:00 | 2027-09-20 07:00 | 92.625 | HAWTHORNE TS | KL42 | 1-00298958 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-09-17 08:00 | 2026-09-23 16:00 | 6.3333 | HAWTHORNE TS | HT5L31 | 1-00297864 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-11-30 07:30 | 2026-12-11 17:30 | 11.4167 | MASSON GS, IPB MASSON JCT, ORLEANS JCT 2, HAWTHORNE TS, ORLEANS TS, CUMBERLAND JCT, ST. ISIDORE TS, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00299005 Rev. #1 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2026-11-30 08:00 | 2026-12-11 16:00 | 11.3333 | HAWTHORNE TS | HT5L5, KL5 | 1-00297876 Rev. #1 | 4 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.11
Back to main menu
Table 4.11: Southwest Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-03-22 06:15 | 2026-05-15 16:00 | 54.4062 | HAMILTON NEBO TS, NEBO JCT, BECK 2 TS, HANNON JCT, BEACH TS, MIDDLEPORT TS, DOFASCO KENILWORTH CTS | Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 25-Q24HM, 28-Q24HM, T3-Q24HM | 1-00287140 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-05-11 07:00 | 2026-07-03 17:00 | 53.4167 | NANTICOKE TS, MIDDLEPORT TS | N580M.MDXNA, DL580, T6L580, L580WT11, 25-N580M, 59-N580M | 1-00287149 Rev. #5 | 7 Day(s) | FABCW NBLIP BLIP | 250 0 0
2026-05-19 06:15 | 2026-06-26 16:00 | 38.4062 | BURLINGTON TS, BURLINGTON JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q23BM.BEXNI, Q23BM.BUXBD, Q23BM.BUXBU, Q23BM.MIXCA, Q23BM.NEXBU, 25-Q23BM, 28-Q23BM, 39-Q23BM, T16-Q23BM | 1-00287150 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-06-15 08:00 | 2026-06-30 16:00 | 15.3333 | MIDDLEPORT TS | T3, T3-L580, T3-HT3 | 1-00296663 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-07-06 06:15 | 2026-08-14 16:00 | 39.4062 | MIDDLEPORT TS, BEACH TS | M34H.MIXHA, 17-M34H, 25-M34H | 1-00287126 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2026-07-06 07:15 | 2026-07-18 16:00 | 12.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00306897 Rev. #1 | 4 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-07-13 06:15 | 2026-07-24 16:00 | 11.4062 | BURLINGTON TS, HORNING JCT, MIDDLEPORT TS, HORNING TS | M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B | 1-00296668 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-07-20 06:15 | 2026-07-31 16:00 | 11.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00289213 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-07-27 06:15 | 2026-08-12 16:00 | 16.4062 | BURLINGTON TS, HORNING TS, HORNING JCT, MIDDLEPORT TS | M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B | 1-00296669 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-08-31 08:00 | 2026-09-18 16:00 | 18.3333 | DETWEILER TS | AL4, AL6, AL7, ASC21, HT1A, 26-M21D, A_BUS | 1-00296349 Rev. #2 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-09-13 08:00 | 2026-09-18 16:00 | 5.3333 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #5 | 4 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-13 08:00 | 2026-10-16 16:00 | 33.3333 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AHT13, DL582, HT8L582, HT8HT13, 59-N582L, HT13_BUS, HT8_BUS, T13-HT13, W52-N582L | 1-00293595 Rev. #4 | 16 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-20 06:15 | 2026-09-27 16:00 | 7.4062 | PRESTON JCT, GALT JCT, GALT TS, GALT SOUTH JCT, DETWEILER TS, TRINITY JCT, DETWEILER JCT, KITCHENER MTS 6, PRESTON TS, MIDDLEPORT TS | M20D.DEXDE, M20D.DEXGA, M20D.DEXWI, M20D.GAXMI, M20D.GAXPR, M20D.PRXGA, M20D.PRXPR, 21-M20D, 25-M20D, 26-M20D, 65-M20D, M20D.GSXGJ, M20D.TRXGS, 429M20D-41 | 1-00295586 Rev. #2 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-09-20 15:15 | 2027-02-12 08:30 | 144.7188 | SALFORD JCT, BUCHANAN TS | 19-M31W, M31W-TEMP1 | 1-00297259 Rev. #4 | 90 Day(s) | No Impact | #N/A
2026-09-29 06:15 | 2026-10-09 15:00 | 10.3646 | SCHEIFELE JCT, GUELPH NORTH JCT, WATERLOO NORTH 3 JCT, WATERLOO MTS 3, DETWEILER TS | D6V.DEXWA, D6V.SCXGU, D6V.WAXSC, D6V.WAXWA, 26-D6V, 2613D6V-2602 | 1-00295582 Rev. #2 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-10-14 06:15 | 2026-10-30 16:00 | 16.4062 | SCHEIFELE JCT, GUELPH NORTH JCT, WATERLOO NORTH 3 JCT, WATERLOO MTS 3, DETWEILER TS | D6V.DEXWA, D6V.SCXGU, D6V.WAXSC, D6V.WAXWA, 26-D6V, 2613D6V-2602 | 1-00295599 Rev. #1 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-10-19 07:30 | 2026-12-11 16:00 | 53.3542 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #3 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-11-03 06:15 | 2026-12-03 16:00 | 30.4062 | CAMPBELL TS, SPEED RIVER JCT, CEDAR TS, WATERLOO NORTH 3 JCT, SCHEIFELE JCT, WATERLOO MTS 3, GUELPH NORTH JCT, DETWEILER TS | D7V.CAXCJ, D7V.DEXWA, D7V.GUXCA, D7V.WAXSC, D7V.WAXWA, 26-D7V, 2613D7V-2608, 5T4-D7V, T2-D7V, T4-D7V | 1-00295584 Rev. #1 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-04-05 05:00 | 2026-04-15 16:00 | 10.4583 | ERINDALE TS, ERINDALE JCT, RICHVIEW TS, TOMKEN JCT, CHURCHILL MEADOWS JCT, TRAFALGAR TS, TOMKEN TS, HURONTARIO SS, HANLAN JCT, CHURCHILL MEADOWS TS | R17T.ERXER, R17T.ERXTO, R17T.ERXTR, R17T.TOXRI, R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R17T, 31-R19TH, 5T6-R19TH, 88-R17T, 88-R19TH, L19L29-L19, T1-R17T, T3-R19TH, T3-R17T | 1-00280349 Rev. #56 | 4 Hour(s) | No Impact | #N/A
2026-03-22 06:15 | 2026-05-15 16:00 | 54.4062 | HAMILTON NEBO TS, NEBO JCT, BECK 2 TS, HANNON JCT, BEACH TS, MIDDLEPORT TS, DOFASCO KENILWORTH CTS | Q24HM.HAXBE, Q24HM.HAXHA, Q24HM.HAXKE, Q24HM.HNXHA, Q24HM.HNXHN, Q24HM.HNXMI, 157T1-Q24HM, 17-Q24HM, 25-Q24HM, 28-Q24HM, T3-Q24HM | 1-00287140 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-05-19 06:15 | 2026-06-26 16:00 | 38.4062 | BURLINGTON TS, BURLINGTON JCT, BURLINGTON DESN TS, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q23BM.BEXNI, Q23BM.BUXBD, Q23BM.BUXBU, Q23BM.MIXCA, Q23BM.NEXBU, 25-Q23BM, 28-Q23BM, 39-Q23BM, T16-Q23BM | 1-00287150 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-07-06 06:15 | 2026-08-14 16:00 | 39.4062 | MIDDLEPORT TS, BEACH TS | M34H.MIXHA, 17-M34H, 25-M34H | 1-00287126 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2026-07-13 06:15 | 2026-07-24 16:00 | 11.4062 | BURLINGTON TS, HORNING JCT, MIDDLEPORT TS, HORNING TS | M27B.HOXBU, M27B.HOXHO, M27B.HOXMI, 25-M27B, 39-M27B, 4T4-M27B | 1-00296668 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-07-20 06:15 | 2026-07-31 16:00 | 11.4062 | BURLINGTON TS, BURLINGTON DESN TS, BURLINGTON JCT, BECK 2 TS, NIAGARA WEST JCT, MIDDLEPORT TS, NEALE JCT, CARLUKE JCT | Q25BM.BEXNI, Q25BM.BUXBD, Q25BM.BUXBU, Q25BM.MIXCA, Q25BM.NEXBU, 25-Q25BM, 28-Q25BM, 39-Q25BM, T15-Q25BM | 1-00289213 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-07-27 06:15 | 2026-08-12 16:00 | 16.4062 | BURLINGTON TS, HORNING TS, HORNING JCT, MIDDLEPORT TS | M28B.HOXBU, M28B.HOXHO, M28B.HOXMI, 25-M28B, 39-M28B, 4T3-M28B | 1-00296669 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-09-20 15:15 | 2027-02-12 08:30 | 144.7188 | SALFORD JCT, BUCHANAN TS | 19-M31W, M31W-TEMP1 | 1-00297259 Rev. #4 | 90 Day(s) | No Impact | #N/A
2026-04-05 05:00 | 2026-04-15 16:00 | 10.4583 | ERINDALE TS, ERINDALE JCT, RICHVIEW TS, TOMKEN JCT, CHURCHILL MEADOWS JCT, TRAFALGAR TS, TOMKEN TS, HURONTARIO SS, HANLAN JCT, CHURCHILL MEADOWS TS | R17T.ERXER, R17T.ERXTO, R17T.ERXTR, R17T.TOXRI, R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R17T, 31-R19TH, 5T6-R19TH, 88-R17T, 88-R19TH, L19L29-L19, T1-R17T, T3-R19TH, T3-R17T | 1-00280349 Rev. #56 | 4 Hour(s) | No Impact | #N/A
2026-04-22 08:00 | 2026-04-28 16:00 | 6.3333 | ERINDALE JCT, TOMKEN JCT, TRAFALGAR TS, RICHVIEW TS, TOMKEN TS, ERINDALE TS | R17T.ERXER, R17T.ERXTO, R17T.ERXTR, R17T.TOXRI, A1L17, L17L79, 31-R17T, 88-R17T, T1-R17T, T3-R17T | 1-00295795 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-05-11 07:00 | 2026-07-03 17:00 | 53.4167 | NANTICOKE TS, MIDDLEPORT TS | N580M.MDXNA, DL580, T6L580, L580WT11, 25-N580M, 59-N580M | 1-00287149 Rev. #5 | 7 Day(s) | FABCW NBLIP BLIP | 250 0 0
2026-07-06 07:15 | 2026-07-18 16:00 | 12.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00306897 Rev. #1 | 4 Hour(s) | FABCW NBLIP BLIP | 300 0 0
2026-09-13 08:00 | 2026-09-18 16:00 | 5.3333 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #5 | 4 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-09-13 08:00 | 2026-10-16 16:00 | 33.3333 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AHT13, DL582, HT8L582, HT8HT13, 59-N582L, HT13_BUS, HT8_BUS, T13-HT13, W52-N582L | 1-00293595 Rev. #4 | 16 Hour(s) | FABCW NBLIP BLIP | 1100 300 800
2026-10-19 07:30 | 2026-12-11 16:00 | 53.3542 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #3 | Non-recallable | FABCW NBLIP BLIP | 300 0 0
2026-11-15 07:00 | 2026-11-20 16:30 | 5.3958 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00296683 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-03-25 11:00 | 2026-04-02 16:00 | 8.2083 | NANTICOKE TS | SC22K1, SC22SC | 1-00296651 Rev. #7 | 6 Hour(s) | No Impact | #N/A
2026-10-22 07:00 | 2026-10-30 16:00 | 8.375 | NANTICOKE TS | SC22K1, SC22SC, SC22 | 1-00298903 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2024-08-22 14:20 | 2026-12-31 16:00 | 861.0694 | NANTICOKE TS | SVC1 | 1-00263077 Rev. #8 | Non-recallable | No Impact | #N/A
2024-10-27 08:00 | 2026-12-31 16:00 | 795.3333 | NANTICOKE TS | T13, SVC1, T13-HT13 | 1-00269611 Rev. #3 | Non-recallable | No Impact | #N/A
2026-03-03 03:00 | 2026-06-13 02:00 | 101.9583 | ALLANBURG WEST JCT, ABITIBI CONSOLIDATED NAN91 JCT, MIDDLEPORT TS | 25-Q26M, 64Q26M-25, Q26M-Q10P, Q28A-Q10P | 1-00301036 Rev. #13 | 2 Hour(s) | No Impact | #N/A
2026-03-03 08:00 | 2026-06-12 16:00 | 101.3333 | ALLANBURG TS, ALLANBURG WEST JCT, MIDDLEPORT TS, ABITIBI CONSOLIDATED NAN91 JCT, BECK 2 TS | Q26M.MIXAW, Q28A.ALXAB, 25-Q26M, 28-Q28A, 45-Q28A, 64Q26M-25, Q26M-Q10P, Q28A-Q10P | 1-00287129 Rev. #23 | 60 Hour(s) | No Impact | #N/A
2026-03-29 08:00 | 2026-05-01 16:00 | 33.3333 | NANTICOKE TS | AHT13, AL581, AWT11, HT8L582, HT8HT13, A_BUS, HT13_BUS, HT8_BUS, T13-HT13 | 1-00298629 Rev. #8 | 2 Day(s) | No Impact | #N/A
2026-04-13 08:00 | 2026-04-24 16:00 | 11.3333 | NANTICOKE TS | AHT13, HT8HT13, T13, SVC1, T13-HT13 | 1-00298662 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-04-13 08:00 | 2026-04-24 16:00 | 11.3333 | DETWEILER TS | T1, T1-HT1, SVC1 | 1-00295860 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-04-26 13:00 | 2026-05-08 16:00 | 12.125 | SEAFORTH LSO JCT | L7S-M18 | 1-00214178 Rev. #10 | 8 Hour(s) | No Impact | #N/A
2026-05-04 08:00 | 2026-05-15 16:00 | 11.3333 | MIDDLEPORT TS | SC21K1, SC21SC | 1-00298688 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-05-05 14:00 | 2026-05-14 16:00 | 9.0833 | NANTICOKE TS | P1F | 1-00298693 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-05-06 08:00 | 2027-10-28 15:00 | 540.2917 | SANDUSK SS | SS3, SS3-L25 | 1-00291644 Rev. #11 | 1 Hour(s) | No Impact | #N/A
2026-06-08 06:15 | 2026-06-18 16:00 | 10.4062 | ONEIDA ENERGY STORAGE, JARVIS TS, NANTICOKE CREEK JCT, U.S. STEEL NANTICOKE JCT, NANTICOKE TS | N21J.NJXST, N21J.STXJA, N21J.STXNA, 59-N21J, T4-N21J, N21J.JJXON, N21J.JJXJA | 1-00298763 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-06-21 06:15 | 2026-07-06 16:00 | 15.4062 | BEAMSVILLE TS, WINONA TS, WINONA JCT | Q2AH.WIXBE, 115Q2AH-18, 18Q2AH-17 | 1-00298777 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-08-24 07:00 | 2026-09-11 16:00 | 18.375 | GLANFORD JCT, HORNING MOUNTAIN JCT, MOHAWK TS | B3.GLXHO, B3.MOXGL, 76B3-1, 20T2-B3 | 1-00298826 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-14 07:00 | 2026-10-02 16:00 | 18.375 | MOHAWK TS, GLANFORD JCT, HORNING MOUNTAIN JCT | 76B4-1, 20T1-B4, B4.GLXHO, B4.MOXGL | 1-00298849 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-09-22 08:00 | 2026-09-30 16:00 | 8.3333 | BURLINGTON TS | L23L37 | 1-00298863 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-10-01 08:15 | 2026-10-30 16:00 | 29.3229 | ALLANBURG TS, ALLANBURG WEST JCT, MIDDLEPORT TS, ABITIBI CONSOLIDATED NAN91 JCT, BECK 2 TS | Q26M.MIXAW, Q28A.ALXAB, 25-Q26M, 28-Q28A, 45-Q28A, 64Q26M-25, Q26M-Q10P, Q28A-Q10P | 1-00289214 Rev. #2 | 60 Hour(s) | No Impact | #N/A
2026-10-05 06:15 | 2026-10-30 17:00 | 25.4479 | BRANT TS, POWERLINE JCT, BURLINGTON TS, DUNDAS 2 JCT, DUNDAS 2 TS, HORNING MOUNTAIN JCT, ALFORD JCT, NEWTON TS | 117T5-B12BL, 12-B12BL, 26-B12BL, 26-B13BL, 39-B12BL, B12BL.BRXPO, B12BL.DUXDU, B12BL.HOXAL, B12BL.HOXDU, B12BL.ALXBR, B12BL.BUXDU, B12BL.NEXHO | 1-00296675 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-10-16 16:00 | 2027-02-22 08:00 | 128.6667 | NANTICOKE TS | AHT13, HT8L582, HT8HT13, HT13_BUS, HT8_BUS, T13-HT13 | 1-00298901 Rev. #1 | Non-recallable | No Impact | #N/A
2026-10-18 08:00 | 2026-10-23 16:00 | 5.3333 | BEACH TS | 17-H36D | 1-00298902 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-10-19 06:15 | 2026-12-15 16:00 | 57.4062 | BRONTE TS, BURLINGTON TS, PALERMO JCT | B8.BRXBR, B8.BRXBU, 39-B8, T2-B8, T2-B7, T4, 13T4-B8 | 1-00298822 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-11-02 06:15 | 2026-11-27 17:00 | 25.4479 | DUNDAS JCT, MCMASTER JCT, BURLINGTON TS, GLANFORD JCT, HORNING MOUNTAIN JCT, MOHAWK TS, NEWTON TS, DUNDAS TS | B3.DUXBU, B3.GLXHO, B3.HOXNE, B3.MCXDU, B3.MOXGL, 26B3-39, 26B4-39, 39-B3, 76B3-1, T2, T2-B3, 20T2-B3, B3.MCXHO | 1-00298907 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-16 07:15 | 2026-12-03 16:00 | 17.3646 | BURLINGTON TS, GAGE TS, GAGE JCT, BIRMINGHAM TS | B10.BIXGA, B10.BUXGA, B10.GAXGA, B11.BIXGA, B11.BUXGA, B11.GAXGA, 24-B11, 24-K2G, 24-B10, 24-K1G, 39-B11, 39-B10, 50-B11, 50-B10 | 1-00298916 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-05-05 07:00 | 2026-05-15 16:00 | 10.375 | BEACH TS | A1TL18, A1L20, A1L36, A1_BUS, T8-A1 | 1-00287148 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-08-30 12:30 | 2026-09-10 16:30 | 11.1667 | SEAFORTH TS, SEAFORTH LSO JCT, ST. MARYS TS | BY, DTL18, KL6, KTL18, KTL7, 61-61M18, K_BUS, TL18_BUS, L7S-M18, T2-TL18, T5-K, DBUS-TEMP1 | 1-00296308 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2026-09-15 07:30 | 2026-09-21 16:30 | 6.375 | SEAFORTH TS, SEAFORTH LSO JCT, ST. MARYS TS | BY, DL6, DTL18, DTL7, KTL7, 61-L7S, D_BUS, L7S-M18, T1-TL7, T6-D | 1-00296312 Rev. #3 | 12 Hour(s) | No Impact | #N/A
2026-09-20 06:15 | 2026-09-27 16:00 | 7.4062 | PRESTON JCT, GALT JCT, GALT TS, GALT SOUTH JCT, DETWEILER TS, TRINITY JCT, DETWEILER JCT, KITCHENER MTS 6, PRESTON TS, MIDDLEPORT TS | M20D.DEXDE, M20D.DEXGA, M20D.DEXWI, M20D.GAXMI, M20D.GAXPR, M20D.PRXGA, M20D.PRXPR, 21-M20D, 25-M20D, 26-M20D, 65-M20D, M20D.GSXGJ, M20D.TRXGS, 429M20D-41 | 1-00295586 Rev. #2 | 4 Hour(s) | FABCW NBLIP BLIP | 100 0 0
2026-09-22 07:30 | 2026-09-29 07:30 | 7 | SEAFORTH TS, SEAFORTH LSO JCT, ST. MARYS TS | BY, DTL7, KL6, KTL18, KTL7, 61-L7S, K_BUS, L7S-M18, T1-TL7, T5-K, DBUS-TEMP2 | 1-00296313 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-09-29 07:30 | 2026-10-13 16:30 | 14.375 | SEAFORTH TS, SEAFORTH LSO JCT | DTL7, KTL7, 61-L7S, L7S-M18, T1-TL7 | 1-00296315 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-10-14 07:30 | 2026-10-22 16:30 | 8.375 | SEAFORTH TS, ST. MARYS TS | BY, DL6, DTL18, DTL7, D_BUS, T6-D | 1-00296316 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-10-15 08:30 | 2026-10-20 16:00 | 5.3125 | BUCHANAN TS, INGERSOLL TS | W12.BUXIN, L12K, L9L12, 19-W12, 38W7-19, 38W12-19 | 1-00295725 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-11-08 07:00 | 2026-11-27 16:00 | 19.375 | BEACH TS | A1TL18, A1L20, A1L36, A1_BUS, T8-A1 | 1-00296682 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-01-19 16:00 | 2026-04-02 16:00 | 73 | BURLINGTON TS, PALERMO JCT, BRONTE TS | B7.BRXBR, B7.BRXBU, 39-B7, T2-B7 | 1-00296643 Rev. #21 | 48 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.12
Back to main menu
Table 4.12: Toronto Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-03-01 08:00 | 2026-04-26 16:00 | 56.3333 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | T2Y, T2-L82, 51-H82V, T2, L82L88, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00305725 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2026-04-03 08:00 | 2026-04-17 16:00 | 14.3333 | HEARN SS | L6L13, L9L13, 22-H13P-L13-G, L13_BUS | 1-00284522 Rev. #12 | 6 Hour(s) | No Impact | #N/A
2026-04-20 07:00 | 2026-04-26 16:01 | 6.3757 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | H1L82, L76L82, 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00276918 Rev. #44 | 4 Hour(s) | No Impact | #N/A
2026-05-25 07:00 | 2026-06-12 16:00 | 18.375 | CHERRYWOOD TS, CLAIREVILLE TS | C552V.CHXCL, D1L552, L552L586, 51-C552V, 81-C552V | 1-00295570 Rev. #7 | 4 Hour(s) | FABCW | 200
2026-06-15 07:00 | 2026-06-26 16:00 | 11.375 | CLAIREVILLE TS, CHERRYWOOD TS, PARKWAY JCT, PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP | 1-00295576 Rev. #4 | 4 Hour(s) | FABCW | 200
2026-09-15 08:00 | 2026-10-03 16:01 | 18.334 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-23 08:45 | 2026-10-02 16:00 | 9.3021 | HEARN SS, BASIN TS, BASIN JCT, GERRARD TS, CARLAW TS, LEASIDE TS, BLOOR STREET JCT, MILL STREET JCT | H3L.BAXBA, H3L.BAXHE, H3L.BAXMI, H3L.BLXLE, H3L.CAXGE, H3L.GEXBL, H3L.MIXGE, H2L3, LT2L3, LT2L11, 22-H3L-L3-G, 34-H3L, 4-H3L, 87-H3L, H3L-34, H3L-22, H3L-87, 4H3LR1, H3L-CA | 1-00239128 Rev. #32 | 6 Hour(s) | No Impact | #N/A
2026-10-07 08:00 | 2026-10-14 16:00 | 7.3333 | VAUGHAN 4 JCT, WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN MTS 4, HOLLAND TS, HOLLAND JCT | 51-H83V, 153-H83V, H83V.WJXCL, H83V.HJX4J, H83V.4JXWJ, H83V.4JXV4, H83V.HOXHJ | 1-00296676 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-03 08:00 | 2026-11-10 16:00 | 7.3333 | HEARN SS, DON FLEET JCT, ESPLANADE TS, COPELAND SS, LOWER SIMCOE ST JCT | K1L9, L7L9, L9L13, 22-H9DE, T13-D, H9DE.DOXES, H9DE.ESXLS, H9DE.HEXDO, H9DE.LSXCP, K2L9 | 1-00296049 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-04-12 08:00 | 2026-04-17 16:00 | 5.3333 | CHERRYWOOD TS, CLARINGTON TS, DUFFIN JCT | 81-T28C, K2L28, L23L28, 296-T28C, L28_BUS, T28C.CLXDJ | 1-00289074 Rev. #7 | 34 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-04 16:00 | 22.3333 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS, DUFFIN JCT, OSHAWA WILSON TS, CHERRYWOOD TS, WHITBY TS, WILSON JCT, WHITBY JCT, B23C H26C TIE JCT | 81-T23C, 81-T28C, 128T1-T31H, 54T2-T23C, 40T3-T23C, 54T4-T23C, K2L28, L23L28, L23L31, P2L31, 296-T23C, 296-T28C, 296-T31H, L28_BUS, L31_BUS, T28C.CLXDJ, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, T23C.BJXCH, T23C.CLXWJ, T23C.WJXBJ, T23C.WJXWH, T23C.WJXWI, T23C.WJXWY, 57-T31H, 54T7-T23C, L23_BUS | 1-00295709 Rev. #1 | 12 Hour(s) | No Impact | #N/A
2027-05-12 06:00 | 2027-05-19 16:30 | 7.4375 | CHERRYWOOD TS, CLARINGTON TS, DUFFIN JCT | 81-T28C, K2L28, L23L28, 296-T28C, T28C.CLXDJ | 1-00297185 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-03-01 08:00 | 2026-04-26 16:00 | 56.3333 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | T2Y, T2-L82, 51-H82V, T2, L82L88, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00305725 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2026-04-20 07:00 | 2026-04-26 16:01 | 6.3757 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | H1L82, L76L82, 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00276918 Rev. #44 | 4 Hour(s) | No Impact | #N/A
2026-09-15 08:00 | 2026-10-03 16:01 | 18.334 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | 51-H82V, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00296672 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-10-07 08:00 | 2026-10-14 16:00 | 7.3333 | VAUGHAN 4 JCT, WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN MTS 4, HOLLAND TS, HOLLAND JCT | 51-H83V, 153-H83V, H83V.WJXCL, H83V.HJX4J, H83V.4JXWJ, H83V.4JXV4, H83V.HOXHJ | 1-00296676 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-03-01 08:00 | 2026-04-26 16:00 | 56.3333 | WOODBRIDGE JCT, CLAIREVILLE TS, VAUGHAN 4 JCT, VAUGHAN MTS #4, HOLLAND TS, HOLLAND JCT | T2Y, T2-L82, 51-H82V, T2, L82L88, 153-H82V, H82V.WJXCL, H82V.4JXV4, H82V.4JXWJ, H82V.HJX4J, H82V.HOXHJ | 1-00305725 Rev. #10 | 4 Hour(s) | No Impact | #N/A
2026-03-30 07:00 | 2026-04-09 16:00 | 10.375 | MILTON SS | HL501, HL573, HL585, HL571, H_BUS | 1-00306838 Rev. #1 | 4 Hour(s) | FABCW | 250
2026-04-16 08:00 | 2026-04-22 09:00 | 6.0417 | CLAIREVILLE TS | AL550, W2L550, 51-C550VP | 1-00296655 Rev. #2 | 1 Hour(s) | FABCW | 200
2026-04-16 08:00 | 2026-04-22 16:00 | 6.3333 | CHERRYWOOD TS, CLAIREVILLE TS, PARKWAY JCT, PARKWAY TS | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, JL550, W2L550, WT16L550, 51-C550VP, 52-C550VP, 81-C550VP | 1-00295515 Rev. #7 | 4 Hour(s) | FABCW | 200
2026-04-16 15:00 | 2026-04-22 16:00 | 6.0417 | CLAIREVILLE TS | AL550, W2L550, 51-C550VP | 1-00296656 Rev. #2 | 1 Hour(s) | FABCW | 200
2026-04-27 08:00 | 2026-05-28 08:01 | 31.0007 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #17 | 48 Hour(s) | No Impact | #N/A
2026-05-12 05:00 | 2026-06-05 09:00 | 24.1667 | MILTON SS, BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, OLD21-B502M, 40-B502M | 1-00293588 Rev. #6 | 4 Hour(s) | FABCW | 1750
2026-05-12 05:00 | 2026-06-05 09:00 | 24.1667 | BRUCE A TS, MILTON SS | EL502, OLDHT4L502, KL502, L502L573, OLD21-B502M, 40-B502M, L502_BUS, HT4L502, L502WT27, 21-B502M, OLDL502_BUS | 1-00252396 Rev. #9 | 4 Day(s) | FABCW | 1750
2026-06-15 07:00 | 2026-06-26 16:00 | 11.375 | CLAIREVILLE TS, CHERRYWOOD TS, PARKWAY JCT, PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP | 1-00295576 Rev. #4 | 4 Hour(s) | FABCW | 200
2026-06-29 07:00 | 2026-07-10 16:00 | 11.375 | CLAIREVILLE TS | HT16L75, HT16L72, HT16_BUS, T16, T16-W4, T16-HT16 | 1-00295577 Rev. #3 | 4 Hour(s) | FABCW | 250
2026-07-06 07:15 | 2026-07-18 16:00 | 12.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00306897 Rev. #1 | 4 Hour(s) | FABCW | 300
2026-07-20 06:15 | 2026-08-28 16:00 | 39.4062 | BRUCE B SS, MILTON SS, BRUCE JCT, WILLOW CREEK JCT | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, L501L563, 29-B561M | 1-00293589 Rev. #6 | 4 Hour(s) | FABCW | 1750
2026-08-30 08:00 | 2026-09-04 16:00 | 5.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #3 | 4 Hour(s) | FABCW | 1750
2026-08-30 08:00 | 2026-09-11 16:00 | 12.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #5 | 4 Hour(s) | FABCW | 1750
2026-10-19 07:30 | 2026-12-11 16:00 | 53.3542 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #3 | Non-recallable | FABCW | 300
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #7 | 48 Hour(s) | No Impact | #N/A
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #2 | Non-recallable | No Impact | #N/A
2026-04-05 05:00 | 2026-04-15 16:00 | 10.4583 | ERINDALE TS, ERINDALE JCT, RICHVIEW TS, TOMKEN JCT, CHURCHILL MEADOWS JCT, TRAFALGAR TS, TOMKEN TS, HURONTARIO SS, HANLAN JCT, CHURCHILL MEADOWS TS | R17T.ERXER, R17T.ERXTO, R17T.ERXTR, R17T.TOXRI, R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R17T, 31-R19TH, 5T6-R19TH, 88-R17T, 88-R19TH, L19L29-L19, T1-R17T, T3-R19TH, T3-R17T | 1-00280349 Rev. #56 | 4 Hour(s) | No Impact | #N/A
2026-05-20 08:00 | 2026-05-29 16:00 | 9.3333 | CLAIREVILLE TS, RICHVIEW TS | V73R.CLXRI, A2L73, L18L73, 51-V73R, 88-V73R | 1-00295787 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-06-15 07:00 | 2026-06-26 16:00 | 11.375 | CLAIREVILLE TS, CHERRYWOOD TS, PARKWAY JCT, PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP | 1-00295576 Rev. #4 | 4 Hour(s) | FABCW | 200
2026-05-12 05:00 | 2026-06-05 09:00 | 24.1667 | MILTON SS, BRUCE A TS, BRUCE JCT, WILLOW CREEK JCT | B502M.BAXBJ, B502M.BJXMI, B502M.BJXWJ, OLD21-B502M, 40-B502M | 1-00293588 Rev. #6 | 4 Hour(s) | FABCW | 1750
2026-05-12 05:00 | 2026-06-05 09:00 | 24.1667 | BRUCE A TS, MILTON SS | EL502, OLDHT4L502, KL502, L502L573, OLD21-B502M, 40-B502M, L502_BUS, HT4L502, L502WT27, 21-B502M, OLDL502_BUS | 1-00252396 Rev. #9 | 4 Day(s) | FABCW | 1750
2026-08-30 08:00 | 2026-09-04 16:00 | 5.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, 40-B501M, 29-B501M | 1-00293593 Rev. #3 | 4 Hour(s) | FABCW | 1750
2026-08-30 08:00 | 2026-09-11 16:00 | 12.3333 | WILLOW CREEK JCT, MILTON SS, BRUCE B SS, BRUCE JCT | B501M.BBXBJ, B501M.BJXWJ, B501M.WJXMI, HL501, L501L570, 40-B501M, 29-B501M | 1-00295573 Rev. #5 | 4 Hour(s) | FABCW | 1750
2026-04-05 05:00 | 2026-04-15 16:00 | 10.4583 | ERINDALE TS, ERINDALE JCT, RICHVIEW TS, TOMKEN JCT, CHURCHILL MEADOWS JCT, TRAFALGAR TS, TOMKEN TS, HURONTARIO SS, HANLAN JCT, CHURCHILL MEADOWS TS | R17T.ERXER, R17T.ERXTO, R17T.ERXTR, R17T.TOXRI, R19TH.CHXTR, R19TH.ERXCH, R19TH.ERXER, R19TH.ERXHA, R19TH.HAXHU, R19TH.TOXRI, R19TH.TOXTO, L19L29, 240T2-R19TH, 31-R17T, 31-R19TH, 5T6-R19TH, 88-R17T, 88-R19TH, L19L29-L19, T1-R17T, T3-R19TH, T3-R17T | 1-00280349 Rev. #56 | 4 Hour(s) | No Impact | #N/A
2026-04-16 08:00 | 2026-04-22 09:00 | 6.0417 | CLAIREVILLE TS | AL550, W2L550, 51-C550VP | 1-00296655 Rev. #2 | 1 Hour(s) | FABCW | 200
2026-04-16 08:00 | 2026-04-22 16:00 | 6.3333 | CHERRYWOOD TS, CLAIREVILLE TS, PARKWAY JCT, PARKWAY TS | C550VP.CHXPJ, C550VP.CLXPJ, C550VP.PJXPR, AL550, JL550, W2L550, WT16L550, 51-C550VP, 52-C550VP, 81-C550VP | 1-00295515 Rev. #7 | 4 Hour(s) | FABCW | 200
2026-04-16 15:00 | 2026-04-22 16:00 | 6.0417 | CLAIREVILLE TS | AL550, W2L550, 51-C550VP | 1-00296656 Rev. #2 | 1 Hour(s) | FABCW | 200
2026-04-22 08:00 | 2026-04-28 16:00 | 6.3333 | ERINDALE JCT, TOMKEN JCT, TRAFALGAR TS, RICHVIEW TS, TOMKEN TS, ERINDALE TS | R17T.ERXER, R17T.ERXTO, R17T.ERXTR, R17T.TOXRI, A1L17, L17L79, 31-R17T, 88-R17T, T1-R17T, T3-R17T | 1-00295795 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-04-27 08:00 | 2026-05-28 08:01 | 31.0007 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #17 | 48 Hour(s) | No Impact | #N/A
2026-06-15 07:00 | 2026-06-26 16:00 | 11.375 | CLAIREVILLE TS, CHERRYWOOD TS, PARKWAY JCT, PARKWAY TS | C553VP.CHXPJ, C553VP.PJXCL, C553VP.PJXPR, A2L553, L553L560, 51-C553VP, 52-C553VP, 81-C553VP | 1-00295576 Rev. #4 | 4 Hour(s) | FABCW | 200
2026-06-29 07:00 | 2026-07-10 16:00 | 11.375 | CLAIREVILLE TS | HT16L75, HT16L72, HT16_BUS, T16, T16-W4, T16-HT16 | 1-00295577 Rev. #3 | 4 Hour(s) | FABCW | 250
2026-07-06 07:15 | 2026-07-18 16:00 | 12.3646 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, 25-V586M, 51-V586M | 1-00306897 Rev. #1 | 4 Hour(s) | FABCW | 300
2026-07-20 06:15 | 2026-08-28 16:00 | 39.4062 | BRUCE B SS, MILTON SS, BRUCE JCT, WILLOW CREEK JCT | B561M.BBXBR, B561M.BRXWI, B561M.WIXMI, 40-B561M, L501L563, 29-B561M | 1-00293589 Rev. #6 | 4 Hour(s) | FABCW | 1750
2026-07-27 07:00 | 2026-08-07 16:00 | 11.375 | CLAIREVILLE TS, RICHVIEW TS, CLAIREVILLE JCT | V79R.CLXCL, V79R.CLXRI, HT14L79, K2L79, 51-V79R, 88-V79R | 1-00298812 Rev. #2 | 4 Hour(s) | FABCW | 250
2026-10-19 07:30 | 2026-12-11 16:00 | 53.3542 | MIDDLEPORT TS, CLAIREVILLE TS | V586M.MDXCL, L80L86, 25-V586M, 51-V586M | 1-00288368 Rev. #3 | Non-recallable | FABCW | 300
2026-10-26 07:00 | 2026-11-20 16:00 | 25.375 | CLAIREVILLE TS, RICHVIEW TS | V77R.CLXCL, L41L77, L71L77, 51-V77R, 88-V77R | 1-00296680 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #7 | 48 Hour(s) | No Impact | #N/A
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #2 | Non-recallable | No Impact | #N/A
2026-11-04 08:00 | 2026-11-10 16:00 | 6.3333 | RICHVIEW TS, CLAIREVILLE TS | V77R.CLXCL, A1L77, L21L77, 51-V77R, 88-V77R | 1-00295786 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-15 07:00 | 2026-11-20 16:30 | 5.3958 | TRAFALGAR TS, PALERMO TS, BURLINGTON TS, GLENORCHY JCT, PALERMO TXB JCT, LANTZ JCT, GLENORCHY MTS1 | T37B.GJXGL, T37B.GJXLA, T37B.PAXBU, T37B.PAXTR, T37B.PJXGJ, 31-T37B, 31SC21L-T37B, 39-T37B, T4-T37B | 1-00296683 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-04-05 08:00 | 2026-04-10 16:00 | 5.3333 | WILSON JCT, WHITBY JCT, CLARINGTON TS, CHERRYWOOD TS, OSHAWA WILSON TS, WHITBY TS | 40T4-T29C, 54T3-T29C, 81-T29C, HT3L29, P2L29, 296-T29C, L29_BUS, T29C.CLXWJ, T29C.WJXWI, T29C.WJXWY, T29C.WYXCH, T29C.WYXWH | 1-00289073 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-04-12 08:00 | 2026-04-17 16:00 | 5.3333 | CHERRYWOOD TS, CLARINGTON TS, DUFFIN JCT | 81-T28C, K2L28, L23L28, 296-T28C, L28_BUS, T28C.CLXDJ | 1-00289074 Rev. #7 | 34 Hour(s) | No Impact | #N/A
2026-04-19 08:00 | 2026-04-24 16:00 | 5.3333 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS | 128T1-T31H, L23L31, P2L31, 296-T31H, L31_BUS, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, 57-T31H | 1-00289102 Rev. #10 | 34 Hour(s) | No Impact | #N/A
2026-10-13 08:00 | 2026-11-04 16:00 | 22.3333 | CLARINGTON TS, HAVELOCK TS, MARINE JCT, OTONABEE TS, DUFFIN JCT, OSHAWA WILSON TS, CHERRYWOOD TS, WHITBY TS, WILSON JCT, WHITBY JCT, B23C H26C TIE JCT | 81-T23C, 81-T28C, 128T1-T31H, 54T2-T23C, 40T3-T23C, 54T4-T23C, K2L28, L23L28, L23L31, P2L31, 296-T23C, 296-T28C, 296-T31H, L28_BUS, L31_BUS, T28C.CLXDJ, T31H.HAXMJ, T31H.MJXCL, T31H.MJXOT, T23C.BJXCH, T23C.CLXWJ, T23C.WJXBJ, T23C.WJXWH, T23C.WJXWI, T23C.WJXWY, 57-T31H, 54T7-T23C, L23_BUS | 1-00295709 Rev. #1 | 12 Hour(s) | No Impact | #N/A
2027-05-12 06:00 | 2027-05-19 16:30 | 7.4375 | CHERRYWOOD TS, CLARINGTON TS, DUFFIN JCT | 81-T28C, K2L28, L23L28, 296-T28C, T28C.CLXDJ | 1-00297185 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-04-27 08:00 | 2026-05-28 08:01 | 31.0007 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #17 | 48 Hour(s) | No Impact | #N/A
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #7 | 48 Hour(s) | No Impact | #N/A
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #2 | Non-recallable | No Impact | #N/A
2026-04-27 08:00 | 2026-05-28 08:01 | 31.0007 | CLAIREVILLE TS, ESSA TS | E511V.CLXES, DL511, W2L511, 18-E511V, 51-E511V | 1-00238538 Rev. #17 | 48 Hour(s) | No Impact | #N/A
2026-11-01 07:00 | 2026-12-04 17:00 | 33.4167 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, 18-E510V, 51-E510V | 1-00296677 Rev. #7 | 48 Hour(s) | No Impact | #N/A
2026-11-01 08:00 | 2027-03-19 16:00 | 138.3333 | ESSA TS, CLAIREVILLE TS | E510V.CLXES, AL510, W3L510, 18-E510V, 51-E510V | 1-00296678 Rev. #2 | Non-recallable | No Impact | #N/A
2022-06-22 16:50 | 2026-12-31 16:00 | 1652.9653 | CLARINGTON TS | K1K2, P1P2 | 1-00202079 Rev. #19 | Non-recallable | No Impact | #N/A
2025-06-06 09:00 | 2026-05-14 16:00 | 342.2917 | GLENGROVE TS | P3_BUS | 1-00286152 Rev. #7 | Non-recallable | No Impact | #N/A
2025-09-08 04:15 | 2026-04-17 16:00 | 221.4896 | RICHVIEW TS | SC22A, SC22SC | 1-00293207 Rev. #17 | 4 Hour(s) | No Impact | #N/A
2025-12-06 08:52 | 2026-12-31 16:00 | 390.2972 | CLARINGTON TS | HT3L32 | 1-00302902 Rev. #2 | Non-recallable | No Impact | #N/A
2026-01-17 08:00 | 2026-04-26 16:00 | 99.3333 | VAUGHAN MTS #4 | T1A, T1B, TIE AB, TIE BA, 5125T1-H82V, VAUGHAN MTS #4-T1 | 1-00304683 Rev. #4 | 2 Hour(s) | No Impact | #N/A
2026-03-02 08:00 | 2026-04-17 16:00 | 46.3333 | RICHVIEW TS | SC22A, SC22SC, SC22 | 1-00296079 Rev. #5 | 36 Hour(s) | No Impact | #N/A
2026-03-03 08:00 | 2026-12-25 16:00 | 297.3333 | CHERRYWOOD TS | K3K4 | 1-00307345 Rev. #1 | 30 Min(s) | No Impact | #N/A
2026-03-04 08:00 | 2026-05-05 16:00 | 62.3333 | PARKWAY TS | K1L22 | 1-00295650 Rev. #4 | 30 Day(s) | No Impact | #N/A
2026-03-16 07:00 | 2026-03-31 15:00 | 15.3333 | HEARN SS | SC12SC, SC12, SC12SC-SC12CA | 1-00295894 Rev. #6 | 6 Hour(s) | No Impact | #N/A
2026-03-23 07:00 | 2026-04-01 16:00 | 9.375 | CECIL TS, TERAULEY TS | C5E.CEXTE, L5L6, L5L9, 1C5E-49, 49-C5E | 1-00266190 Rev. #28 | 6 Hour(s) | No Impact | #N/A
2026-03-29 06:00 | 2026-04-03 16:00 | 5.4167 | MARINE JCT, OTONABEE TS, CHATS FALLS TS, CLARINGTON TS | 128T2-T22C, HT2L22, P1L22, 296-T22C, L22_BUS, T22C.CHXMJ, T22C.MJXCL, T22C.MJXOT, 2-T22C | 1-00289071 Rev. #8 | 34 Hour(s) | No Impact | #N/A
2026-03-31 07:30 | 2026-04-14 16:00 | 14.3542 | MANBY WEST TS | T2, T2-H1, T2-K3 | 1-00295971 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-04-09 07:00 | 2026-04-17 16:00 | 8.375 | CECIL TS, CHARLES TS | L9C.CEXCH, HL9, L5L9, 49-L9C, L9C-49 | 1-00296288 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-04-09 08:00 | 2026-04-17 16:00 | 8.3333 | BATHURST TS, BATHURST JCT, PARKWAY TS, LEASIDE JCT, IBM MARKHAM CTS, FINCH JCT, IBM MARKHAM JCT, FINCH TS, MARKHAM 1 JCT, RICHVIEW TS | P22R.BAXBA, P22R.BAXLE, P22R.FIXBA, P22R.FIXFI, P22R.IBXIB, P22R.LEXIB, P22R.PKXM1, K1L22, LT3L22, 52-P22R, 55T2-P22R, 85T1-P22R, 85T3-P22R, 88-P22R, T2-P22R | 1-00295648 Rev. #3 | 2 Hour(s) | No Impact | #N/A
2026-04-15 06:15 | 2026-05-02 17:30 | 17.4688 | BRIDGMAN JCT | L14W-TEMP1 | 1-00292331 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-04-20 08:00 | 2026-05-01 20:00 | 11.5 | GLENGROVE TS, LEASIDE TS | L2Y.GLXLE, EL2, L2L5, 34-L2Y, P3_BUS, L2Y-34, P1-P3, P2-P3, T3-P, T4-P | 1-00296245 Rev. #3 | 9 Hour(s) | No Impact | #N/A
2026-04-26 08:00 | 2026-05-01 16:00 | 5.3333 | LASCO JCT, THORNTON JCT, CLARINGTON TS, OSHAWA THORNTON TS, OSHAWA GM JCT, OSHAWA GM TS, ATLANTIC PACKAGING JCT, GERDAU WHITBY CTS, ATLANTIC PACKAGING CTS, OSHAWA AREA JCT, WHITBY JCT, WHITBY TS, CHERRYWOOD TS, COLUMBUS JCT | 142-T24C, L24L25, P1L24, 296-T24C, L24_BUS, T24C.AJXAT, T24C.AJXGW, T24C.CJXLJ, T24C.CJXWJ, T24C.CLXCJ, T24C.LJXAJ, T24C.LJXTJ, T24C.OJXGJ, T24C.OJXOG, T24C.TJXOJ, T24C.TJXTH, T24C.WJXCH, T24C.WJXWH, 81-T24C, 8117T24C-MSO, 40T1-T24C, 52T4-T24C | 1-00289076 Rev. #6 | 34 Hour(s) | No Impact | #N/A
2026-04-27 08:00 | 2026-05-06 16:00 | 9.3333 | PARKWAY TS, CHERRYWOOD TS | 52-C35P, 81-C35P | 1-00306229 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-05-01 08:00 | 2026-05-11 16:00 | 10.3333 | REXDALE TS, WESTMORE JCT, CLAIREVILLE TS, RICHVIEW TS | V76R.WEXCL, V76R.WEXRE, V76R.WEXRI, 51-V76R, 88-V76R, T2-V76R | 1-00306858 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-05-03 08:00 | 2026-05-29 16:00 | 26.3333 | MARINE JCT, OTONABEE TS, CHATS FALLS TS, CLARINGTON TS | 128T2-T22C, HT2L22, P1L22, 296-T22C, L22_BUS, T22C.CHXMJ, T22C.MJXCL, T22C.MJXOT, 2-T22C | 1-00295799 Rev. #3 | 8 Hour(s) | No Impact | #N/A
2026-05-04 05:00 | 2026-05-28 16:00 | 24.4583 | PICKERING A SS | L6K, L8D, T1D, D_BUS, K_BUS, KBUS-TEMP, L8K | 1-00297696 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-05-04 07:00 | 2026-05-15 16:00 | 11.375 | CLAIREVILLE TS, GRAINGER NORTH JCT | H1L75, HT16L75, 51-V75P, 491V75P-8118 | 1-00276144 Rev. #34 | 4 Hour(s) | FABCW | 250
2026-05-05 08:00 | 2026-05-14 20:00 | 9.5 | GLENGROVE TS | T1A3, T1A4, D6Y-44, T1, T2, P1-P3, UFLS1, T1-P, T2-P | 1-00296240 Rev. #3 | 9 Hour(s) | No Impact | #N/A
2026-05-15 16:00 | 2026-05-26 16:00 | 11 | GRAINGER NORTH JCT | 491V75P-8118 | 1-00306221 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-05-19 08:00 | 2026-05-29 16:00 | 10.3333 | CITY VIEW JCT, MERIVALE TS, VAL TETREAU JCT, WOODROFFE TS | F10MV.CIXME, F10MV.CIXVA, F10MV.CIXWO, 24-F10MV, 6-F10MV, 97-F10MV | 1-00305875 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-05-30 08:00 | 2026-06-04 16:00 | 5.3333 | CHERRYWOOD TS, MALVERN TS, AGINCOURT TS, FINCH TS, AGINCOURT JCT, FINCH JCT, RICHVIEW TS | C4R.AGXAG, C4R.AGXMA, C4R.FIXAG, C4R.FIXFI, C4R.FIXRI, C4R.MAXCH, 63T5-C4R, 81-C4R, 88-C4R, T3-C4R, T4-C4R | 1-00292284 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-06-06 08:00 | 2026-06-18 16:00 | 12.3333 | RICHVIEW TS, MALVERN TS, CHERRYWOOD TS, LESLIE TS, AGINCOURT JCT | C5R.AGXMA, C5R.LEXAG, C5R.LEXRI, C5R.MAXCH, 81-C5R, 88-C5R, T2-C5R, T3-C5R, T4-C5R | 1-00292209 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-06-11 08:30 | 2026-06-30 16:00 | 19.3125 | HEARN SS | K1K2, K2L1, K2L11, K2L14, SC12K2, SC12SC, SS2, SC12, SC12CA-SS2, SC12SC-SC12CA, K2_BUS | 1-00266206 Rev. #26 | 6 Hour(s) | No Impact | #N/A
2026-06-15 04:00 | 2026-07-02 16:00 | 17.5 | CLARINGTON TS | SC22P2, SC22SC, SC22 | 1-00298953 Rev. #2 | 8 Hour(s) | No Impact | #N/A
2026-06-15 09:00 | 2026-07-01 16:00 | 16.2917 | CLAIREVILLE TS | A1P, A2L553, AL510, AL550, AL571, A1_BUS, A2_BUS, A1-A2 | 1-00238547 Rev. #38 | 1 Day(s) | No Impact | #N/A
2026-06-18 16:00 | 2026-06-25 16:01 | 7.0007 | CHERRYWOOD TS, MALVERN TS, AGINCOURT TS, FINCH TS, AGINCOURT JCT, FINCH JCT, RICHVIEW TS | C4R.AGXAG, C4R.AGXMA, C4R.FIXAG, C4R.FIXFI, C4R.FIXRI, C4R.MAXCH, 63T5-C4R, 81-C4R, 88-C4R, T3-C4R, T4-C4R | 1-00292210 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-09-06 08:00 | 2026-09-25 08:01 | 19.0007 | CLAIREVILLE TS | D1L552, DL511, DL560, DL551, DL570, D1_BUS, D2_BUS, D1-D2 | 1-00238542 Rev. #16 | 1 Day(s) | No Impact | #N/A
2026-09-08 07:00 | 2026-10-16 17:00 | 38.4167 | GOREWAY PH JCT, GOREWAY TS, CLAIREVILLE TS, GOREWAY JCT, WOODBRIDGE JCT, KLEINBURG TS, VAUGHAN 3 JCT, WOODBRIDGE TS | V43.CLXGJ, V43.CLXWJ, V43.GJXGO, V43.GOXGO, V43.KLXV3, V43.V3XWJ, V43.WJXWO, 136T2-V43, 136T4-V43, 136T6-V43, 45T2-V43, 51-V43, D6T3-V43 | 1-00287122 Rev. #12 | 48 Hour(s) | No Impact | #N/A
2026-09-14 07:00 | 2026-09-25 16:00 | 11.375 | CLAIREVILLE TS | D1L552, DL511, DL560, DL551, DL570, D1_BUS, D2_BUS, D1-D2 | 1-00298848 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-09-15 07:00 | 2026-09-22 16:00 | 7.375 | LEASIDE TS | T17, T17-K, T17-L17 | 1-00295733 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-09-15 07:00 | 2026-09-22 18:00 | 7.4583 | CHERRYWOOD TS | DL17, L17L32, 81-C17L | 1-00294573 Rev. #47 | 4 Hour(s) | No Impact | #N/A
2026-09-26 08:00 | 2026-10-08 16:00 | 12.3333 | FAIRCHILD TS, FINCH JCT, FINCH TS, AGINCOURT JCT, CAVANAGH TS, RICHVIEW TS, CHERRYWOOD TS | C20R.AGXCA, C20R.AGXCH, C20R.FAXAG, C20R.FIXFA, C20R.FIXFI, C20R.FIXRI, 81-C20R, 88-C20R, T1-C20R, T2-C20R, T4-C20R | 1-00292313 Rev. #2 | 12 Hour(s) | No Impact | #N/A
2026-09-29 07:30 | 2026-10-16 16:00 | 17.3542 | MANBY EAST TS | H2H3, H2L23, H2_BUS, SC22H2-H2, T5-H2, T7-H2 | 1-00295671 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-10-09 08:00 | 2026-10-23 16:00 | 14.3333 | PARKWAY TS, CHERRYWOOD TS | 52-C36P, 81-C36P | 1-00292312 Rev. #1 | 12 Hour(s) | No Impact | #N/A
2026-10-19 06:15 | 2026-12-15 16:00 | 57.4062 | BRONTE TS, BURLINGTON TS, PALERMO JCT | B8.BRXBR, B8.BRXBU, 39-B8, T2-B8, T2-B7, T4, 13T4-B8 | 1-00298822 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-10-19 08:00 | 2026-10-30 16:00 | 11.3333 | RICHVIEW TS | H1H2, H2L20, H2L18, H2L22, H2L72, H2L76, 88-R13K, H2_BUS, SC21H-H2, T7-H2 | 1-00295740 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-03 08:00 | 2026-11-12 16:00 | 9.3333 | CHERRYWOOD TS | K1K2, KL18, K1L2, KL35, KL8, K1_BUS, SS1 | 1-00296246 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-15 08:00 | 2026-12-11 16:00 | 26.3333 | BATHURST JCT, FAIRCHILD TS, BATHURST TS, RICHVIEW TS, CHERRYWOOD TS | C18R.BAXBA, C18R.BAXFA, C18R.BAXRI, C18R.FAXCH, 81-C18R, 88-C18R, T1-C18R, T2-C18R, T3-C18R, T4-C18R | 1-00295785 Rev. #2 | 12 Hour(s) | No Impact | #N/A
2026-11-23 08:00 | 2026-12-04 20:00 | 11.5 | DUPLEX TS | T2A1A2, T2A3A4, T3A5A6, 44-L5D, K_BUS, D6Y-K, T2, T3, T2-K, T3-K | 1-00296161 Rev. #1 | 9 Hour(s) | No Impact | #N/A
2026-12-08 08:00 | 2026-12-15 16:00 | 7.3333 | LEASIDE TS, SCARBORO TS, BERMONDSEY TS, SCARBORO JCT, CHERRYWOOD TS, WARDEN TS | C14L.BEXLE, C14L.BEXSC, C14L.SCXCH, C14L.SCXSC, C14L.SCXWA, HL14HL16, 34-C14L, 81-C14L, T14, T14-CA, T14-HL14, T2-C14L, T21-C14L, T3-C14L, T4-C14L, SS14-X, T14R-SS14 | 1-00265999 Rev. #16 | 4 Hour(s) | No Impact | #N/A
2026-01-19 16:00 | 2026-04-02 16:00 | 73 | BURLINGTON TS, PALERMO JCT, BRONTE TS | B7.BRXBR, B7.BRXBU, 39-B7, T2-B7 | 1-00296643 Rev. #21 | 48 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.13
Back to main menu
Table 4.13: West Zone Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-06 08:45 | 2026-09-25 15:00 | 19.2604 | CHATHAM SS | DL28, DL31, DL44, D_BUS, SC22D-D, SC23D-D, DL42, DL64, KL43, KL65, DL88 | 1-00285801 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-11-29 09:00 | 2026-12-18 09:30 | 19.0208 | CHATHAM SS | DL28, DL31, DL44, D_BUS, SC22D-D, SC23D-D, DL42, DL64, DL88 | 1-00295731 Rev. #1 | 6 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-09-18 16:00 | 5.3333 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-10-16 16:00 | 33.3333 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AHT13, DL582, HT8L582, HT8HT13, 59-N582L, HT13_BUS, HT8_BUS, T13-HT13, W52-N582L | 1-00293595 Rev. #4 | 16 Hour(s) | No Impact | #N/A
2026-09-20 15:15 | 2027-02-12 08:30 | 144.7188 | SALFORD JCT, BUCHANAN TS | 19-M31W, M31W-TEMP1 | 1-00297259 Rev. #4 | 90 Day(s) | No Impact | #N/A
2026-09-20 15:15 | 2027-02-12 08:30 | 144.7188 | SALFORD JCT, BUCHANAN TS | 19-M31W, M31W-TEMP1 | 1-00297259 Rev. #4 | 90 Day(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-09-18 16:00 | 5.3333 | LONGWOOD TS, NANTICOKE TS | N582L.LOXNA, HL582, KL582, 59-N582L, W52-N582L | 1-00295560 Rev. #5 | 4 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-10-16 16:00 | 33.3333 | NANTICOKE TS, LONGWOOD TS | N582L.LOXNA, AHT13, DL582, HT8L582, HT8HT13, 59-N582L, HT13_BUS, HT8_BUS, T13-HT13, W52-N582L | 1-00293595 Rev. #4 | 16 Hour(s) | No Impact | #N/A
2026-09-13 08:00 | 2026-09-27 08:00 | 14 | LAMBTON TS, LAMBTON TS 2 | P1P2, PL23, PL24, P1_BUS, JQ, T2-P1, T2 | 1-00293702 Rev. #4 | 6 Hour(s) | MICH-W-EXP MICH-W-IMP MICH-S-EXP MICH-S-IMP | 300 350 300 200
2026-09-27 08:45 | 2026-10-09 15:00 | 12.2604 | LAMBTON TS 2, LAMBTON TS | K1K2, KL25, KL37, K1L51, K1_BUS, T1-K1, T1, JQ | 1-00294547 Rev. #5 | 6 Hour(s) | No Impact | #N/A
2026-10-18 08:00 | 2026-11-01 08:45 | 14.0312 | LAMBTON TS 2 | P1P2, P2L27, PL38, PL4 | 1-00292251 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-11-01 09:00 | 2026-11-13 15:00 | 12.25 | LAMBTON TS 2 | K1K2, KL26, K2L28, KL4, SS5.6-K2 | 1-00293517 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2025-09-29 12:00 | 2026-12-31 16:00 | 458.1667 | LAKESHORE TS | 530-H76 | 1-00295205 Rev. #20 | 4 Hour(s) | No Impact | #N/A
2026-02-27 07:00 | 2027-07-30 17:30 | 518.4375 | BORALEX TILBURY JCT | 647K2Z-54 | 1-00306348 Rev. #1 | Non-recallable | No Impact | #N/A
2026-05-20 07:00 | 2026-05-29 16:00 | 9.375 | SCOTT TS | L5L7 | 1-00307250 Rev. #1 | 2 Hour(s) | No Impact | #N/A
2026-08-16 08:00 | 2026-09-04 15:45 | 19.3229 | CHATHAM SS | KL29, KL47, SC21K, K_BUS, SC21, SC21K-K, SS1-K, KL43, KL65, KL87, KL88 | 1-00295732 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-09-01 08:00 | 2026-09-30 16:00 | 29.3333 | SCOTT TS, LANXESS INC JCT, SARNIA SCOTT JCT | N7S.SAXBA, N7S.SAXSC, 40-N7S | 1-00291878 Rev. #2 | Non-recallable | No Impact | #N/A
2026-11-01 08:00 | 2026-11-06 16:00 | 5.3333 | CLARKE TS, TALBOT TS, BUCHANAN TS, OXFORD STREET JCT | W36.OXXBU, W36.OXXCL, W36.OXXTA, 19-W36, 26-W36, T3-W36 | 1-00295612 Rev. #2 | 4 Hour(s) | No Impact | #N/A
2026-11-01 08:45 | 2026-11-20 09:30 | 19.0312 | CHATHAM SS, LAKESHORE TS | KL29, KL47, SC21K, K_BUS, SC21, SC21K-K, SS1-K, 530-C88H, KL43, KL65, C88H.CHXLA, DL88, KL87, KL88, 86-C88H | 1-00295669 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-11-15 08:00 | 2026-11-20 16:00 | 5.3333 | ESSEX TS, CHRYSLER WINDSOR ASS. PLANT CTS | E8F.ESXCH, 15-E8F | 1-00295751 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-22 08:00 | 2026-11-27 16:00 | 5.3333 | ESSEX TS, CHRYSLER WINDSOR ASS. PLANT CTS | E9F.ESXCH, 15-E9F | 1-00295752 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-11-29 08:00 | 2026-12-04 16:00 | 5.3333 | TALBOT TS, BUCHANAN TS, CLARKE TS, DUNDAS STREET JCT | W37.DUXBU, W37.DUXCL, W37.DUXTA, 19-W37, 26-W37, T4-W37 | 1-00295616 Rev. #1 | 4 Hour(s) | No Impact | #N/A
2026-10-15 08:30 | 2026-10-20 16:00 | 5.3125 | BUCHANAN TS, INGERSOLL TS | W12.BUXIN, L12K, L9L12, 19-W12, 38W7-19, 38W12-19 | 1-00295725 Rev. #3 | 4 Hour(s) | No Impact | #N/A
2026-04-12 07:00 | 2026-05-22 16:00 | 40.375 | ESSEX TS, KEITH TS, CRAWFORD TS, CRAWFORD JCT | J4E.CRXES, J4E.KEXCR, L3L4, L4L8, 15-J4E, 23-J4E, L4_BUS, 25T4-J4E | 1-00302515 Rev. #4 | 6 Hour(s) | No Impact | #N/A
2026-04-20 06:15 | 2026-05-22 16:00 | 32.4062 | ESSEX TS, KEITH TS, CRAWFORD TS, CRAWFORD JCT | J4E.CRXES, J4E.KEXCR, 15-J4E, 23-J4E, 25T4-J4E | 1-00286360 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-05-25 06:15 | 2026-06-26 16:00 | 32.4062 | ESSEX TS, KEITH TS, CRAWFORD TS, CRAWFORD JCT | J3E.CRXES, J3E.CRXKE, 15-J3E, 23-J3E, 25T3-J3E | 1-00286361 Rev. #7 | 4 Hour(s) | No Impact | #N/A
2026-09-17 07:00 | 2026-10-08 17:00 | 21.4167 | WINDSOR LAUZON TS | A_BUS, T1-A, T5-A, T8-A, 56-H54Z | 1-00293516 Rev. #2 | 6 Hour(s) | No Impact | #N/A
2026-09-20 08:00 | 2026-10-02 16:00 | 12.3333 | WINDSOR LAUZON TS | SS1, T1, T1-A, T1-P | 1-00300160 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2026-10-25 12:30 | 2026-12-16 12:30 | 52 | ESSEX TS | L3L4, L4L8, 15-J4E, L4_BUS | 1-00306028 Rev. #1 | 6 Hour(s) | No Impact | #N/A
Back to main menu

## Table 4.14
Back to main menu
Table 4.14: External Interties Transmission Outages
Planned Start | Planned End | Duration (Days) | Station | Equipment Name | Outage ID | Max Recall | Major Transmission Interface Impacted | Reduction in Limit (MW)
2026-09-28 08:00 | 2026-10-09 16:00 | 11.3333 | ST. LAWRENCE TS, MASSENA JCT | L33P.ROXLA, 49-L33P | 1-00275118 Rev. #8 | 4 Hour(s) | No Impact | #N/A
2026-05-31 14:00 | 2026-06-22 08:00 | 21.75 | OTTO HOLDEN TS, MATTAWA JCT | DT3L5, H4Z-L5H, 583L5A-TEMP2 | 1-00295073 Rev. #3 | 6 Hour(s) | No Impact | #N/A
2024-05-14 13:00 | 2026-12-31 16:00 | 961.125 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00254393 Rev. #21 | 6 Hour(s) | EWTW | 25
2026-11-30 07:30 | 2026-12-11 17:30 | 11.4167 | MASSON GS, IPB MASSON JCT, ORLEANS JCT 2, HAWTHORNE TS, ORLEANS TS, CUMBERLAND JCT, ST. ISIDORE TS, LONGUEUIL JCT, LONGUEUIL TS | D5A.CUXGA, D5A.CUXIS, D5A.CUXO2, D5A.HAXO2, D5A.IPXMA, D5A.LOXIS, D5A.LOXLO, D5A.O2XOR, 325T2-D5A, 48-D5A, 62D5A-26, T3-D5A, T1-A1, 62D5A-625 | 1-00299005 Rev. #1 | 6 Hour(s) | FIO BEAU P33C | 250 690 0
2025-11-18 08:00 | 2026-12-31 16:00 | 408.3333 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00299527 Rev. #10 | 2 Hour(s) | EWTW | 25
2026-04-20 09:00 | 2026-05-08 17:00 | 18.3333 | KENORA TS, WHITESHELL TS | K21W.WHXKE, 34-K21W | 1-00302492 Rev. #4 | 6 Hour(s) | EWTW | 25
Back to main menu