## Winter Reference Net Forecast
The IRRP planning forecasts account for the median weather gross forecasts provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. A power factor of 0.9 was assumed for the forecasts. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Transformer Station | WINTER REFERENCE: Net Extreme Weather Station Peak Demand Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Batchawana TS | 2.078 | 2.0649 | 2.1533 | 2.1399 | 2.2227 | 2.2062 | 2.2898 | 2.3736 | 2.3603 | 2.4461 | 2.439 | 2.5307 | 2.6275 | 2.7247 | 2.821 | 2.9166 | 2.9157 | 3.0112 | 3.1072 | 3.2029
DA Watson TS | 9.002 | 8.9402 | 8.9771 | 8.9171 | 8.9418 | 8.9737 | 8.9066 | 8.9428 | 8.8882 | 9.1267 | 9.2906 | 9.555 | 9.8419 | 10.1309 | 10.5122 | 10.7928 | 11.0774 | 11.4534 | 11.7367 | 12.1145
Echo River TS | 16.5554 | 16.6905 | 16.8188 | 17.0555 | 17.1662 | 17.2824 | 17.5011 | 17.6257 | 17.7596 | 18.197 | 18.7603 | 19.2304 | 19.9254 | 20.4231 | 21.0155 | 21.7044 | 22.2971 | 22.8847 | 23.6757 | 24.3658
Goulais Bay TS | 9.8638 | 9.8961 | 10.0249 | 10.0562 | 10.1655 | 10.1836 | 10.301 | 10.3234 | 10.4528 | 10.6798 | 11.0307 | 11.2891 | 11.5755 | 11.9607 | 12.3411 | 12.7164 | 13.0963 | 13.4707 | 13.849 | 14.2252
No. 4 Circuit | 23.8178 | 23.8773 | 24.9714 | 25.0311 | 24.993 | 25.0441 | 25.0978 | 25.1593 | 25.1197 | 25.0797 | 25.0592 | 25.0965 | 25.147 | 25.2491 | 25.2962 | 25.3431 | 25.3407 | 25.3342 | 25.4352 | 25.536
Andrews TS | 0.25197 | 0.2528 | 0.25247 | 0.2533 | 0.25364 | 0.25421 | 0.25476 | 0.25537 | 0.25619 | 0.25599 | 0.25676 | 0.25765 | 0.25943 | 0.26129 | 0.263 | 0.2636 | 0.26438 | 0.26498 | 0.26573 | 0.26642
MacKay TS | 0.039967 | 0.039436 | 0.038901 | 0.038407 | 0.037881 | 0.038359 | 0.037858 | 0.037357 | 0.036894 | 0.036388 | 0.037031 | 0.036783 | 0.036756 | 0.03675 | 0.036706 | 0.038397 | 0.038352 | 0.038255 | 0.038202 | 0.038132
Northern Avenue TS | 2.9237 | 2.9182 | 2.9128 | 2.9078 | 2.904 | 2.8983 | 2.8929 | 2.8883 | 2.8838 | 2.9818 | 2.9793 | 2.9775 | 2.9774 | 2.9774 | 3.0795 | 3.0789 | 3.0785 | 3.0776 | 3.0774 | 3.0772
Chapleau DS | 11.5665 | 11.6554 | 11.7198 | 16.7922 | 16.8357 | 16.9012 | 16.9681 | 17.0438 | 17.1335 | 17.2292 | 17.3589 | 17.4978 | 17.6694 | 17.8439 | 18.0136 | 18.1799 | 18.3506 | 18.5172 | 18.6876 | 18.857
Chapleau MTS | 3.7558 | 3.7805 | 3.7999 | 3.8209 | 3.8368 | 3.8567 | 3.877 | 3.8992 | 3.9242 | 3.9504 | 3.9831 | 4.0178 | 4.0586 | 4.0999 | 4.1404 | 4.1803 | 4.2211 | 4.2611 | 4.3019 | 4.3426
St. Mary's MTS | 68.2302 | 69.6268 | 69.9665 | 0 | 0 | 71.0201 | 71.356 | 71.7311 | 72.1453 | 72.5804 | 73.1484 | 73.7537 | 74.4803 | 75.2229 | 75.953 | 76.6763 | 77.4238 | 78.1586 | 78.9199 | 79.6836
Tarentorus MTS | 77.0777 | 77.8627 | 78.635 | 79.4429 | 80.1658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tagona West TS | 0 | 0 | 142.8182 | 214.4136 | 213.3395 | 372.2946 | 371.497 | 370.99 | 370.5502 | 370.106 | 370.3118 | 370.7565 | 371.6328 | 372.5242 | 373.2876 | 374.0553 | 374.8763 | 375.5637 | 376.4319 | 377.2946
SSM PUC Coincident Total | 145.3079 | 147.4896 | 291.4197 | 293.8565 | 293.5053 | 443.3147 | 442.853 | 442.7211 | 442.6955 | 442.6864 | 443.4602 | 444.5102 | 446.1131 | 447.7471 | 449.2406 | 450.7316 | 452.3001 | 453.7223 | 455.3518 | 456.9782
Total LDC Region | 225.1628 | 227.6049 | 373.0891 | 380.8689 | 380.8625 | 530.9533 | 530.98 | 531.2698 | 531.5107 | 532.6694 | 534.6552 | 536.9994 | 540.232 | 543.4547 | 546.7598 | 549.946 | 552.9802 | 556.0356 | 559.5266 | 563.004
This document and the information contained herein is provided for informational purposes only and is subject to redaction and/or aggregation to protect against identifying specific customer electricity usage. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Summer Reference Net Forecast
The IRRP planning forecasts account for the median weather gross forecasts provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. A power factor of 0.9 was assumed for the forecasts. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Transformer Station | SUMMER REFERENCE: Net Extreme Weather Station Peak Demand Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Batchawana TS | 1.7388 | 1.7208 | 1.8017 | 1.7831 | 1.757 | 1.9279 | 1.9049 | 1.9789 | 1.9617 | 2.0392 | 2.0313 | 2.1166 | 2.2079 | 2.2074 | 2.2985 | 2.3883 | 2.4789 | 2.4767 | 2.567 | 2.6569
DA Watson TS | 6.9789 | 7.2362 | 7.485 | 7.6389 | 7.8986 | 8.0428 | 8.2937 | 8.4521 | 8.7155 | 8.9812 | 9.1663 | 9.454 | 9.7634 | 10.073 | 10.3798 | 10.7909 | 11.0956 | 11.3974 | 11.8057 | 12.109
Echo River TS | 14.0086 | 14.3203 | 14.5189 | 14.8227 | 14.9848 | 15.258 | 15.4338 | 15.7184 | 15.9201 | 16.3214 | 16.8181 | 17.2611 | 17.8331 | 18.3099 | 18.881 | 19.446 | 20.0142 | 20.5768 | 21.2393 | 21.8049
Goulais Bay TS | 6.1222 | 6.1515 | 6.175 | 6.2023 | 6.2033 | 6.2161 | 6.2302 | 6.2505 | 6.2809 | 6.4059 | 6.5589 | 6.722 | 6.9008 | 7.1707 | 7.3489 | 7.6117 | 7.7878 | 8.0497 | 8.2246 | 8.4882
No. 4 Circuit | 22.4939 | 22.5443 | 23.5172 | 23.5677 | 23.5171 | 23.5578 | 23.6019 | 23.5534 | 23.6099 | 23.5653 | 23.5435 | 23.6243 | 23.6235 | 23.6227 | 23.7227 | 23.7201 | 23.8179 | 23.9128 | 24.0109 | 24.2107
Andrews TS | 0.26513 | 0.27241 | 0.28027 | 0.28811 | 0.29375 | 0.30067 | 0.30645 | 0.31321 | 0.32027 | 0.32351 | 0.33316 | 0.33838 | 0.35056 | 0.36099 | 0.37138 | 0.39715 | 0.40999 | 0.41891 | 0.42199 | 0.43898
MacKay TS | 0.030429 | 0.029785 | 0.029153 | 0.028562 | 0.027945 | 0.02739 | 0.026835 | 0.026298 | 0.025802 | 0.025263 | 0.025007 | 0.024756 | 0.024727 | 0.0247 | 0.024673 | 0.024575 | 0.02453 | 0.024438 | 0.024388 | 0.024322
Northern Avenue TS | 2.4768 | 2.5742 | 2.5683 | 2.5629 | 2.5585 | 2.5526 | 2.547 | 2.5422 | 2.5374 | 2.5324 | 2.53 | 2.5276 | 2.5275 | 2.5274 | 2.5273 | 2.5269 | 2.5265 | 2.5257 | 2.5254 | 2.5251
Chapleau DS | 9.6759 | 9.6982 | 9.6796 | 14.671 | 14.61 | 14.5825 | 14.5608 | 14.5561 | 14.5749 | 14.6062 | 14.6871 | 14.7745 | 14.9012 | 15.0291 | 15.1552 | 15.2746 | 15.3987 | 15.5177 | 15.6409 | 15.7628
Chapleau MTS | 1.9697 | 1.9764 | 1.9778 | 1.9804 | 1.9771 | 1.9775 | 1.9787 | 1.9819 | 1.9878 | 1.9952 | 2.0082 | 2.0219 | 2.04 | 2.0582 | 2.0763 | 2.0937 | 2.1115 | 2.1288 | 2.1466 | 2.1643
St. Mary's MTS | 47.478 | 47.6153 | 47.7321 | 0 | 0 | 49.6771 | 49.7793 | 59.0865 | 59.3796 | 59.6513 | 60.0832 | 60.5378 | 61.3185 | 61.9206 | 62.5242 | 63.1085 | 63.7149 | 64.3068 | 64.9229 | 65.5411
Tarentorus MTS | 57.7723 | 58.2347 | 58.6788 | 59.1596 | 59.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tagona West TS | 0 | 0 | 140.3155 | 197.3717 | 195.8913 | 358.3838 | 357.1905 | 356.3519 | 355.6536 | 354.9937 | 355.111 | 355.2954 | 356.1421 | 356.9959 | 357.8407 | 358.6451 | 359.4166 | 360.0974 | 360.8841 | 361.7093
SSM PUC Coincident Total | 105.2503 | 105.8501 | 246.7263 | 247.1069 | 245.9651 | 403.3382 | 406.9171 | 415.3373 | 414.9726 | 414.6129 | 415.1671 | 415.8332 | 417.4606 | 418.9165 | 420.3649 | 421.7536 | 423.1315 | 424.4042 | 425.807 | 427.2504
Total LDC Region | 171.0106 | 172.3742 | 314.7592 | 330.0768 | 329.2175 | 482.5043 | 481.854 | 490.8114 | 490.9675 | 491.4407 | 492.8957 | 494.6984 | 497.6332 | 500.3005 | 503.1507 | 506.0276 | 508.7971 | 511.4332 | 514.4138 | 517.4357
This document and the information contained herein is provided for informational purposes only and is subject to redaction and/or aggregation to protect against identifying specific customer electricity usage. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Winter High Net Forecast
The IRRP planning forecasts account for the median weather gross forecasts provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. A power factor of 0.9 was assumed for the forecasts. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Transformer Station | WINTER HIGH: Net Extreme Weather Station Peak Demand Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Batchawana TS | 2.078 | 2.0649 | 2.1533 | 2.1399 | 2.2227 | 2.2062 | 2.2898 | 2.3736 | 2.3603 | 2.4461 | 2.439 | 2.5307 | 2.6275 | 2.7247 | 2.821 | 2.9166 | 2.9157 | 3.0112 | 3.1072 | 3.2029
DA Watson TS | 9.002 | 8.9402 | 8.9771 | 8.9171 | 8.9418 | 8.9737 | 8.9066 | 8.9428 | 8.8882 | 9.1267 | 9.2906 | 9.555 | 9.8419 | 10.1309 | 10.5122 | 10.7928 | 11.0774 | 11.4534 | 11.7367 | 12.1145
Echo River TS | 16.5554 | 16.6905 | 16.8188 | 17.0555 | 17.1662 | 17.2824 | 17.5011 | 17.6257 | 17.7596 | 18.197 | 18.7603 | 19.2304 | 19.9254 | 20.4231 | 21.0155 | 21.7044 | 22.2971 | 22.8847 | 23.6757 | 24.3658
Goulais Bay TS | 9.8638 | 9.8961 | 10.0249 | 10.0562 | 10.1655 | 10.1836 | 10.301 | 10.3234 | 10.4528 | 10.6798 | 11.0307 | 11.2891 | 11.5755 | 11.9607 | 12.3411 | 12.7164 | 13.0963 | 13.4707 | 13.849 | 14.2252
No. 4 Circuit | 23.8178 | 23.8773 | 24.9714 | 25.0311 | 24.993 | 25.0441 | 25.0978 | 25.1593 | 25.1197 | 25.0797 | 25.0592 | 25.0965 | 25.147 | 25.2491 | 25.2962 | 25.3431 | 25.3407 | 25.3342 | 25.4352 | 25.536
Andrews TS | 0.25197 | 0.2528 | 0.25247 | 0.2533 | 0.25364 | 0.25421 | 0.25476 | 0.25537 | 0.25619 | 0.25599 | 0.25676 | 0.25765 | 0.25943 | 0.26129 | 0.263 | 0.2636 | 0.26438 | 0.26498 | 0.26573 | 0.26642
MacKay TS | 0.039967 | 0.039436 | 0.038901 | 0.038407 | 0.037881 | 0.038359 | 0.037858 | 0.037357 | 0.036894 | 0.036388 | 0.037031 | 0.036783 | 0.036756 | 0.03675 | 0.036706 | 0.038397 | 0.038352 | 0.038255 | 0.038202 | 0.038132
Northern Avenue TS | 2.9237 | 2.9182 | 2.9128 | 2.9078 | 2.904 | 2.8983 | 2.8929 | 2.8883 | 2.8838 | 2.9818 | 2.9793 | 2.9775 | 2.9774 | 2.9774 | 3.0795 | 3.0789 | 3.0785 | 3.0776 | 3.0774 | 3.0772
Chapleau DS | 11.6488 | 11.8224 | 11.9736 | 17.135 | 17.2697 | 17.4289 | 17.5919 | 17.766 | 17.9565 | 18.1554 | 18.3907 | 18.6376 | 18.9197 | 19.2071 | 19.4924 | 19.7767 | 20.068 | 20.3577 | 20.6538 | 20.9516
Chapleau MTS | 3.7745 | 3.8183 | 3.8574 | 3.8986 | 3.9352 | 3.9763 | 4.0185 | 4.0631 | 4.1109 | 4.1607 | 4.2174 | 4.2767 | 4.3427 | 4.4098 | 4.4766 | 4.5435 | 4.6118 | 4.68 | 4.7495 | 4.8196
St. Mary's MTS | 68.2302 | 69.6268 | 69.9665 | 0 | 0 | 71.0201 | 71.356 | 71.7311 | 72.1453 | 72.5804 | 73.1484 | 73.7537 | 74.4803 | 75.2229 | 75.953 | 76.6763 | 77.4238 | 78.1586 | 78.9199 | 79.6836
Tarentorus MTS | 77.0777 | 77.8627 | 78.635 | 79.4429 | 80.1658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tagona West TS | 0 | 0 | 665.8672 | 737.4626 | 736.3885 | 895.3436 | 894.546 | 894.039 | 893.5992 | 893.155 | 893.3608 | 893.8055 | 894.6818 | 895.5732 | 896.3366 | 897.1043 | 897.9253 | 898.6127 | 899.4809 | 900.3436
SSM PUC Coincident Total | 145.3079 | 147.4896 | 814.4687 | 816.9055 | 816.5543 | 966.3637 | 965.902 | 965.7701 | 965.7445 | 965.7354 | 966.5092 | 967.5592 | 969.1621 | 970.7961 | 972.2896 | 973.7806 | 975.3491 | 976.7713 | 978.4008 | 980.0272
Total LDC Region | 225.2637 | 227.8096 | 896.4494 | 904.3383 | 904.4439 | 1054.6497 | 1054.7942 | 1055.2049 | 1055.5694 | 1056.8549 | 1058.9703 | 1061.4471 | 1064.8154 | 1068.1768 | 1071.6238 | 1074.955 | 1078.1373 | 1081.344 | 1084.9895 | 1088.6246
This document and the information contained herein is provided for informational purposes only and is subject to redaction and/or aggregation to protect against identifying specific customer electricity usage. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Summer High Net Forecast
The IRRP planning forecasts account for the median weather gross forecasts provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. A power factor of 0.9 was assumed for the forecasts. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Transformer Station | SUMMER HIGH: Net Extreme Weather Station Peak Demand Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Batchawana TS | 1.7388 | 1.7208 | 1.8017 | 1.7831 | 1.757 | 1.9279 | 1.9049 | 1.9789 | 1.9617 | 2.0392 | 2.0313 | 2.1166 | 2.2079 | 2.2074 | 2.2985 | 2.3883 | 2.4789 | 2.4767 | 2.567 | 2.6569
DA Watson TS | 6.9789 | 7.2362 | 7.485 | 7.6389 | 7.8986 | 8.0428 | 8.2937 | 8.4521 | 8.7155 | 8.9812 | 9.1663 | 9.454 | 9.7634 | 10.073 | 10.3798 | 10.7909 | 11.0956 | 11.3974 | 11.8057 | 12.109
Echo River TS | 14.0086 | 14.3203 | 14.5189 | 14.8227 | 14.9848 | 15.258 | 15.4338 | 15.7184 | 15.9201 | 16.3214 | 16.8181 | 17.2611 | 17.8331 | 18.3099 | 18.881 | 19.446 | 20.0142 | 20.5768 | 21.2393 | 21.8049
Goulais Bay TS | 6.1222 | 6.1515 | 6.175 | 6.2023 | 6.2033 | 6.2161 | 6.2302 | 6.2505 | 6.2809 | 6.4059 | 6.5589 | 6.722 | 6.9008 | 7.1707 | 7.3489 | 7.6117 | 7.7878 | 8.0497 | 8.2246 | 8.4882
No. 4 Circuit | 22.4939 | 22.5443 | 23.5172 | 23.5677 | 23.5171 | 23.5578 | 23.6019 | 23.5534 | 23.6099 | 23.5653 | 23.5435 | 23.6243 | 23.6235 | 23.6227 | 23.7227 | 23.7201 | 23.8179 | 23.9128 | 24.0109 | 24.2107
Andrews TS | 0.26513 | 0.27241 | 0.28027 | 0.28811 | 0.29375 | 0.30067 | 0.30645 | 0.31321 | 0.32027 | 0.32351 | 0.33316 | 0.33838 | 0.35056 | 0.36099 | 0.37138 | 0.39715 | 0.40999 | 0.41891 | 0.42199 | 0.43898
MacKay TS | 0.030429 | 0.029785 | 0.029153 | 0.028562 | 0.027945 | 0.02739 | 0.026835 | 0.026298 | 0.025802 | 0.025263 | 0.025007 | 0.024756 | 0.024727 | 0.0247 | 0.024673 | 0.024575 | 0.02453 | 0.024438 | 0.024388 | 0.024322
Northern Avenue TS | 2.4768 | 2.5742 | 2.5683 | 2.5629 | 2.5585 | 2.5526 | 2.547 | 2.5422 | 2.5374 | 2.5324 | 2.53 | 2.5276 | 2.5275 | 2.5274 | 2.5273 | 2.5269 | 2.5265 | 2.5257 | 2.5254 | 2.5251
Chapleau DS | 9.7492 | 9.8468 | 9.9051 | 14.9753 | 14.9948 | 15.05 | 15.1128 | 15.1944 | 15.3015 | 15.4229 | 15.5959 | 15.7773 | 16.0001 | 16.2259 | 16.452 | 16.6734 | 16.9015 | 17.1264 | 17.3578 | 17.5899
Chapleau MTS | 1.9796 | 1.9964 | 2.0081 | 2.0212 | 2.0287 | 2.0402 | 2.0527 | 2.0676 | 2.0853 | 2.1049 | 2.1303 | 2.1567 | 2.1877 | 2.2192 | 2.2507 | 2.2819 | 2.3138 | 2.3455 | 2.3779 | 2.4105
St. Mary's MTS | 47.478 | 47.6153 | 47.7321 | 0 | 0 | 49.6771 | 49.7793 | 59.0865 | 59.3796 | 59.6513 | 60.0832 | 60.5378 | 61.3185 | 61.9206 | 62.5242 | 63.1085 | 63.7149 | 64.3068 | 64.9229 | 65.5411
Tarentorus MTS | 57.7723 | 58.2347 | 58.6788 | 59.1596 | 59.4981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tagona West TS | 0 | 0 | 657.4821 | 614.0477 | 612.5673 | 775.0598 | 773.8665 | 773.0279 | 772.3296 | 771.6697 | 771.787 | 771.9714 | 772.8181 | 773.6719 | 774.5168 | 775.3211 | 776.0926 | 776.7734 | 777.5601 | 778.3853
SSM PUC Coincident Total | 105.2503 | 105.8501 | 763.893 | 764.2736 | 763.1318 | 920.5048 | 924.0838 | 932.504 | 932.1393 | 931.7796 | 932.3338 | 932.9999 | 934.6272 | 936.0831 | 937.5316 | 938.9203 | 940.2982 | 941.5709 | 942.9737 | 944.4171
Total LDC Region | 171.0937 | 172.5426 | 832.1817 | 747.0979 | 746.33 | 899.7105 | 899.156 | 908.2114 | 908.4676 | 909.0431 | 910.6026 | 912.512 | 915.5558 | 918.3342 | 921.2979 | 924.2906 | 927.1781 | 929.9346 | 933.0379 | 936.1849
This document and the information contained herein is provided for informational purposes only and is subject to redaction and/or aggregation to protect against identifying specific customer electricity usage. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## CTS Forecast
The IRRP planning forecasts account for the median weather gross forecasts provided by the local distributors, savings from distributed generation and conservation and demand management, as well as extreme weather adjustments. A power factor of 0.9 was assumed for the forecasts. Full details on the overall IRRP forecast methodology will be provided in the IRRP report, once finalized.
Customer Transformer Station | Winter Demand Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
CTS1 | 15.8 | 15.8 | 15.7 | 15.6 | 15.6 | 15.5 | 15.5 | 15.4 | 15.4 | 15.3139 | 15.2562 | 15.2133 | 15.1662 | 15.1081 | 15.0603 | 15.0018 | 14.9538 | 14.8956 | 14.8486 | 14.7964
CTS2 | 16.4 | 16.4 | 16.3 | 16.2 | 16.2 | 16.1 | 16.1 | 16 | 16 | 15.9139 | 15.8562 | 15.8133 | 15.7662 | 15.7081 | 15.6603 | 15.6018 | 15.5538 | 15.4956 | 15.4486 | 15.3964
CTS3 | 11.9 | 11.9 | 12.5 | 12.5 | 12.4 | 12.4 | 12.4 | 12.3 | 12.3 | 12.4972 | 12.471 | 12.3833 | 12.3925 | 12.4154 | 12.4269 | 12.4422 | 12.4621 | 12.4567 | 12.4355 | 12.4521
CTS5 | 0 | 24 | 31.7 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8
CTS6 | 0.7 | 0.7 | 11.5 | 11.5 | 11.4 | 11.4 | 11.4 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3
Total | 44.8 | 68.8 | 87.7 | 98.6 | 98.4 | 98.2 | 98.2 | 97.8 | 97.8 | 97.825 | 97.6833 | 97.51 | 97.4248 | 97.3315 | 97.2475 | 97.1457 | 97.0697 | 96.9479 | 96.8327 | 96.7449
Summer Demand Forecast (MW)
CTS1 | 15.4 | 15.4 | 15.3 | 15.2 | 15.1 | 15.1 | 15 | 15 | 15 | 14.875 | 14.8167 | 14.7762 | 14.7357 | 14.6904 | 14.633 | 14.5843 | 14.5223 | 14.4674 | 14.4279 | 14.377
CTS2 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
CTS3 | 13.1 | 13.1 | 15.8 | 15.8 | 15.8 | 15.7 | 15.6 | 15.6 | 15.6 | 16.5389 | 16.5506 | 16.281 | 16.429 | 16.6026 | 16.8011 | 16.9903 | 17.1412 | 17.2434 | 17.2626 | 17.4402
CTS5 | 0 | 24 | 31.7 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8 | 42.8
CTS6 | 0.4 | 0.4 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7 | 11.7
Total | 45.4 | 69.4 | 91 | 102 | 101.9 | 101.8 | 101.6 | 101.6 | 101.6 | 102.4139 | 102.3673 | 102.0571 | 102.1647 | 102.293 | 102.4341 | 102.5745 | 102.6635 | 102.7108 | 102.6905 | 102.8172
This document and the information contained herein is provided for informational purposes only and is subject to redaction and/or aggregation to protect against identifying specific customer electricity usage. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained herein are subject to risks, uncertainties and other factors, and actual results or circumstances may differ materially. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Winter DG
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | WINTER: Total Contracted Distributed Generation (DG) Contribution to Peak (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Batchawana TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DA Watson TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Echo River TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Goulais Bay TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No. 4 Circuit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Andrews TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MacKay TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Northern Avenue TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapleau DS | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapleau MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St. Mary's MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tarentorus MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tagona West TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SSM PUC Coincident Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Region | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRAFT

## Summer DG
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | SUMMER: Total Contracted Distributed Generation (DG) Contribution to Peak (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Batchawana TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DA Watson TS | 0.010973 | 0.010973 | 0.010973 | 0.010973 | 0.010973 | 0.010973 | 0.010973 | 0.010973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Echo River TS | 0.05715 | 0.05715 | 0.05715 | 0.05715 | 0.05715 | 0.05715 | 0.05715 | 0.05715 | 0.05715 | 0.05715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Goulais Bay TS | 0.0082298 | 0.0082298 | 0.0082298 | 0.0082298 | 0.0082298 | 0.0082298 | 0.0082298 | 0.0082298 | 0.0082298 | 0.0082298 | 0.0082298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
No. 4 Circuit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Andrews TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MacKay TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Northern Avenue TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapleau DS | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chapleau MTS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
St. Mary's MTS | 9.4243 | 9.4243 | 9.4243 | 9.4243 | 9.4243 | 9.4243 | 9.4243 | 0.27462 | 0.20738 | 0.19178 | 0.18961 | 0.18732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tarentorus MTS | 4.7228 | 4.7228 | 4.7228 | 4.7228 | 4.7228 | 4.7228 | 0.052671 | 0.1011 | 0.060601 | 0.032096 | 0.027021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tagona West TS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SSM PUC Coincident Total | 14.1471 | 14.1471 | 14.1471 | 14.1471 | 14.1471 | 14.1471 | 9.477 | 0.37572 | 0.26798 | 0.22387 | 0.21663 | 0.18732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Region | 19.2234 | 19.2234 | 19.2234 | 14.2234 | 14.2234 | 14.2234 | 9.5533 | 0.45208 | 0.33336 | 0.28925 | 0.22486 | 0.18732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DRAFT

## Winter CDM
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | WINTER: Total Conservation and Demand Management (CDM) Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Batchawana TS | 0.014173 | 0.027311 | 0.043497 | 0.056907 | 0.078747 | 0.095233 | 0.11623 | 0.13702 | 0.1503 | 0.16919 | 0.17625 | 0.18915 | 0.19697 | 0.20437 | 0.21264 | 0.22167 | 0.22258 | 0.23173 | 0.24031 | 0.24921
DA Watson TS | 0.064161 | 0.12595 | 0.19325 | 0.25321 | 0.33275 | 0.40507 | 0.47212 | 0.54019 | 0.59473 | 0.66888 | 0.71335 | 0.76166 | 0.7873 | 0.81098 | 0.84647 | 0.87855 | 0.90659 | 0.94737 | 0.97665 | 1.0157
Echo River TS | 0.077599 | 0.15168 | 0.23258 | 0.30976 | 0.40823 | 0.50126 | 0.59636 | 0.68101 | 0.75631 | 0.84194 | 0.90631 | 0.95933 | 0.99657 | 1.022 | 1.0572 | 1.1006 | 1.1355 | 1.1755 | 1.2214 | 1.2636
Goulais Bay TS | 0.07414 | 0.14644 | 0.22682 | 0.30014 | 0.40005 | 0.48663 | 0.5784 | 0.66065 | 0.7405 | 0.82728 | 0.8948 | 0.95024 | 0.97771 | 1.0109 | 1.049 | 1.0921 | 1.1306 | 1.1747 | 1.2148 | 1.257
No. 4 Circuit | 0.045838 | 0.090581 | 0.14276 | 0.18731 | 0.22536 | 0.2785 | 0.32896 | 0.37175 | 0.41127 | 0.45134 | 0.47183 | 0.48662 | 0.48825 | 0.49036 | 0.49533 | 0.50052 | 0.50292 | 0.5094 | 0.51259 | 0.51608
Andrews TS | 0.0022462 | 0.0045365 | 0.006941 | 0.0092175 | 0.011995 | 0.014533 | 0.017101 | 0.019607 | 0.021898 | 0.02417 | 0.025479 | 0.026661 | 0.026958 | 0.027175 | 0.027537 | 0.027974 | 0.028235 | 0.028667 | 0.028957 | 0.029304
MacKay TS | 0.00050034 | 0.0010314 | 0.0015664 | 0.0020611 | 0.0025862 | 0.0031464 | 0.0036476 | 0.004148 | 0.004611 | 0.0051172 | 0.0055114 | 0.0057599 | 0.0057873 | 0.0057933 | 0.0058364 | 0.0062212 | 0.0062665 | 0.0063632 | 0.0064158 | 0.0064861
Northern Avenue TS | 0.0054056 | 0.010834 | 0.01629 | 0.021315 | 0.025101 | 0.030785 | 0.036176 | 0.040768 | 0.045298 | 0.05192 | 0.054417 | 0.056186 | 0.056282 | 0.056303 | 0.058776 | 0.059412 | 0.05975 | 0.060672 | 0.060856 | 0.061101
Chapleau DS | 0.10324 | 0.20085 | 0.30765 | 0.40645 | 0.54188 | 0.66312 | 0.78268 | 0.89329 | 0.9898 | 1.0802 | 1.1365 | 1.184 | 1.1989 | 1.2114 | 1.2289 | 1.2501 | 1.2673 | 1.2889 | 1.307 | 1.3263
Chapleau MTS | 0.019922 | 0.038619 | 0.059135 | 0.078107 | 0.104 | 0.12762 | 0.15082 | 0.17206 | 0.19061 | 0.20785 | 0.21865 | 0.22758 | 0.23047 | 0.23293 | 0.23636 | 0.24036 | 0.24368 | 0.24783 | 0.25126 | 0.25491
St. Mary's MTS | 0.34155 | 0.68141 | 1.0426 | 0 | 0 | 2.2067 | 2.6032 | 2.9707 | 3.2993 | 3.6186 | 3.8126 | 3.9769 | 4.0277 | 4.0701 | 4.133 | 4.2105 | 4.2719 | 4.354 | 4.4179 | 4.4875
Tarentorus MTS | 0.38584 | 0.76201 | 1.1718 | 1.5565 | 2.0471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tagona West TS | 0 | 0 | 3.6356 | 5.267 | 6.341 | 9.5312 | 11.2336 | 12.6465 | 13.9929 | 15.3447 | 16.0474 | 16.5121 | 16.5461 | 16.5659 | 16.7147 | 16.86 | 16.953 | 17.1805 | 17.228 | 17.2821
SSM PUC Coincident Total | 0.72739 | 1.4434 | 5.85 | 6.8235 | 8.3881 | 11.7379 | 13.8368 | 15.6172 | 17.2922 | 18.9633 | 19.86 | 20.489 | 20.5737 | 20.636 | 20.8477 | 21.0705 | 21.2249 | 21.5346 | 21.6459 | 21.7697
Total Region | 1.1346 | 2.2412 | 7.0805 | 8.4479 | 10.5188 | 14.3438 | 16.9193 | 19.1377 | 21.1975 | 23.2912 | 24.4631 | 25.3361 | 25.539 | 25.7083 | 26.0657 | 26.4481 | 26.7284 | 27.2057 | 27.4662 | 27.7494
DRAFT

## Summer CDM
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology will be provided in the final report.
Transformer Station | SUMMER: Total Conservation and Demand Management (CDM) Forecast (MW)
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044
Batchawana TS | 0.019616 | 0.037599 | 0.060106 | 0.0787 | 0.10477 | 0.14073 | 0.16376 | 0.19316 | 0.21043 | 0.23635 | 0.24421 | 0.26238 | 0.2745 | 0.27504 | 0.28735 | 0.30096 | 0.3138 | 0.316 | 0.32915 | 0.34266
DA Watson TS | 0.080222 | 0.16391 | 0.2578 | 0.34706 | 0.47153 | 0.58106 | 0.69958 | 0.80542 | 0.91149 | 1.018 | 1.0778 | 1.1473 | 1.1864 | 1.2252 | 1.265 | 1.3248 | 1.3676 | 1.4165 | 1.473 | 1.5195
Echo River TS | 0.10462 | 0.20661 | 0.31839 | 0.42833 | 0.57647 | 0.71704 | 0.85153 | 0.98063 | 1.0893 | 1.2051 | 1.2827 | 1.3569 | 1.4055 | 1.4459 | 1.4954 | 1.5509 | 1.6034 | 1.6613 | 1.7229 | 1.7779
Goulais Bay TS | 0.075604 | 0.1497 | 0.22964 | 0.30581 | 0.40822 | 0.49879 | 0.58821 | 0.67133 | 0.74435 | 0.82622 | 0.88002 | 0.93209 | 0.96018 | 1.0005 | 1.0292 | 1.0767 | 1.1075 | 1.1559 | 1.1879 | 1.2346
No. 4 Circuit | 0.054585 | 0.10759 | 0.16905 | 0.22201 | 0.2726 | 0.3353 | 0.39467 | 0.44315 | 0.49004 | 0.53463 | 0.55647 | 0.57905 | 0.57994 | 0.58067 | 0.58412 | 0.58675 | 0.59238 | 0.60091 | 0.60626 | 0.61329
Andrews TS | 0.0038007 | 0.0078983 | 0.012443 | 0.01702 | 0.02276 | 0.028252 | 0.033849 | 0.039493 | 0.044849 | 0.049881 | 0.053685 | 0.056739 | 0.059033 | 0.061014 | 0.063038 | 0.068304 | 0.070972 | 0.073431 | 0.074494 | 0.078188
MacKay TS | 0.00060099 | 0.0012452 | 0.001877 | 0.0024681 | 0.0030845 | 0.0036401 | 0.0041949 | 0.0047321 | 0.0052277 | 0.0057672 | 0.0060229 | 0.0062738 | 0.0063028 | 0.00633 | 0.0063573 | 0.0064547 | 0.0064996 | 0.0065923 | 0.0066418 | 0.0067076
Northern Avenue TS | 0.005555 | 0.011676 | 0.017528 | 0.022947 | 0.027297 | 0.033221 | 0.038852 | 0.043682 | 0.048396 | 0.053433 | 0.055865 | 0.058203 | 0.058324 | 0.058438 | 0.058551 | 0.058957 | 0.059338 | 0.060104 | 0.060449 | 0.060723
Chapleau DS | 0.15047 | 0.29101 | 0.44326 | 0.58541 | 0.78666 | 0.96106 | 1.1294 | 1.2803 | 1.4074 | 1.5219 | 1.5865 | 1.6445 | 1.6633 | 1.6811 | 1.7006 | 1.7269 | 1.7486 | 1.7756 | 1.7983 | 1.8223
Chapleau MTS | 0.016983 | 0.0327 | 0.049816 | 0.065785 | 0.088515 | 0.10843 | 0.12758 | 0.14463 | 0.15896 | 0.17172 | 0.17897 | 0.18546 | 0.18759 | 0.18961 | 0.19184 | 0.19472 | 0.1972 | 0.20021 | 0.20279 | 0.20546
St. Mary's MTS | 0.45147 | 0.88303 | 1.3455 | 0 | 0 | 2.9586 | 3.477 | 3.9463 | 4.3535 | 4.7368 | 4.9529 | 5.1528 | 5.2182 | 5.2815 | 5.3499 | 5.4443 | 5.5235 | 5.6239 | 5.7071 | 5.7952
Tarentorus MTS | 0.49584 | 0.97464 | 1.4925 | 1.984 | 2.6384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tagona West TS | 0 | 0 | 4.4912 | 6.392 | 7.8723 | 11.9075 | 13.9883 | 15.7152 | 17.3028 | 18.8528 | 19.6265 | 20.334 | 20.3801 | 20.42 | 20.4697 | 20.5609 | 20.6857 | 20.9022 | 21.0137 | 21.0875
SSM PUC Coincident Total | 0.9473 | 1.8577 | 7.3292 | 8.376 | 10.5108 | 14.8661 | 17.4653 | 19.6615 | 21.6563 | 23.5896 | 24.5794 | 25.4868 | 25.5984 | 25.7015 | 25.8197 | 26.0052 | 26.2092 | 26.5261 | 26.7208 | 26.8828
Total Region | 1.4594 | 2.8676 | 8.8891 | 10.4515 | 13.2727 | 18.2736 | 21.4969 | 24.268 | 26.7667 | 29.2125 | 30.5017 | 31.7157 | 31.9795 | 32.2253 | 32.5011 | 32.9007 | 33.2764 | 33.7927 | 34.1827 | 34.5441
DRAFT