## Menu
Sudbury Algoma Area Integrated Regional Resource Plan Data Tables 2026 - Summer
Table 1 Distributed Generation Contribution Factor Assumptions
Table 2: IRRP eDSM (Codes and Standards + Energy Efficiency) Forecast
Table 3: Effective DG Contribution to Coincident Peak
Table 4: Extreme-weather Net Coincident Demand - Reference Forecast
Table 5: Extreme-weather Net Concident Demand - High Growth Scenario
Table 6: Extreme-weather Net Non-coincident Demand - Reference Forecast
Table 7: Extreme-weather Net Non-concident Demand - High Growth Scenario
Table 8: Historical Weather-Corrected Gross Coincident Demand
Table 9: Historical Power Factor at the LV Terminal
This document and the information contained herein is provided for informational purposes only. The IESO has prepared this document based on information currently available to the IESO and reasonable assumptions associated therewith, including relating to electricity supply and demand. The information, statements and conclusions contained in this document are subject to risks, uncertainties and other factors that could cause actual results or circumstances to differ materially from the information, statements and assumptions contained herein. The IESO provides no guarantee, representation, or warranty, express or implied, with respect to any statement or information contained herein and disclaims any liability in connection therewith. Readers are cautioned not to place undue reliance on forward-looking information contained in this document, as actual results could differ materially from the plans, expectations, estimates, intentions and statements expressed herein. The IESO undertakes no obligation to revise or update any information contained in this document as a result of new information, future events or otherwise. In the event there is any conflict or inconsistency between this document and the IESO market rules, any IESO contract, any legislation or regulation, or any request for proposals or other procurement document, the terms in the market rules, or the subject contract, legislation, regulation, or procurement document, as applicable, govern.
DRAFT

## Table 1
Distributed Generation Contribution Factors used to develop the effective DG contribution to coincident peak
Resource Type | Table 1 Distributed Generation Contribution Factor Assumptions - Summer
Contribution Factor (%)
Hydroelectric | 64
Thermal | 94
Solar | 23
Wind | 12

## Table 2
Peak demand savings from codes and standards, as well as the delivery of conservation programs, were estimated for each sector and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology are provided in the methodology document.
Transformer Station | Table 2 IRRP eDSM Forecast (MW) - Summer
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Clarabelle TS | 1.033 | 2.2783 | 3.4102 | 5.3517 | 7.0281 | 8.4996 | 9.1524 | 9.7983 | 10.4805 | 10.9276 | 11.3435 | 11.8402 | 12.1122 | 12.4432 | 12.637 | 12.8461 | 13.0411 | 13.2366 | 13.44 | 13.6367
Elliott Lake TS | 0.14482 | 0.31914 | 0.47359 | 0.73381 | 0.95598 | 1.1518 | 1.2431 | 1.3293 | 1.4058 | 1.4501 | 1.4975 | 1.5459 | 1.5685 | 1.5935 | 1.6047 | 1.6159 | 1.6273 | 1.6387 | 1.6502 | 1.6617
Espanola TS | 0.10635 | 0.23183 | 0.34291 | 0.54439 | 0.71533 | 0.86341 | 0.91957 | 0.97333 | 1.0211 | 1.0497 | 1.0812 | 1.1131 | 1.1301 | 1.1508 | 1.1593 | 1.1679 | 1.1765 | 1.1852 | 1.1939 | 1.2026
Larchwood TS | 0.18188 | 0.39976 | 0.59436 | 0.93806 | 1.2332 | 1.493 | 1.6046 | 1.7119 | 1.8085 | 1.8688 | 1.9342 | 2.0009 | 2.0385 | 2.0817 | 2.1047 | 2.1279 | 2.1513 | 2.1748 | 2.1987 | 2.2227
Manitoulin TS | 0.24219 | 0.53371 | 0.795 | 1.2537 | 1.6493 | 1.9994 | 2.1548 | 2.3046 | 2.4402 | 2.5261 | 2.6189 | 2.714 | 2.7689 | 2.8309 | 2.8662 | 2.9019 | 2.938 | 2.9744 | 3.0112 | 3.0484
Martindale TS | 0.9828 | 2.2624 | 3.418 | 5.4251 | 7.2867 | 8.9024 | 9.599 | 10.2963 | 10.8614 | 11.1941 | 11.5538 | 11.9678 | 12.2013 | 12.4711 | 12.6392 | 12.8076 | 12.9761 | 13.1449 | 13.3281 | 13.5045
Massey DS | 0.039811 | 0.086463 | 0.12771 | 0.20345 | 0.26753 | 0.32277 | 0.34274 | 0.36189 | 0.37884 | 0.38899 | 0.40024 | 0.41161 | 0.41766 | 0.42526 | 0.42822 | 0.43119 | 0.43418 | 0.43719 | 0.44021 | 0.44326
Northshore DS | 0.050438 | 0.11627 | 0.1758 | 0.25194 | 0.3202 | 0.38575 | 0.44072 | 0.49215 | 0.53856 | 0.56538 | 0.59266 | 0.62104 | 0.633 | 0.64219 | 0.6499 | 0.65771 | 0.6656 | 0.67358 | 0.68164 | 0.6898
Sowerby DS | 0.026722 | 0.05832 | 0.086352 | 0.13682 | 0.17965 | 0.21675 | 0.23102 | 0.24459 | 0.25653 | 0.26349 | 0.27113 | 0.27886 | 0.28273 | 0.28749 | 0.28925 | 0.29102 | 0.29279 | 0.29456 | 0.29634 | 0.29812
Spanish DS | 0.021065 | 0.046272 | 0.068742 | 0.10801 | 0.14162 | 0.17116 | 0.18401 | 0.19628 | 0.20728 | 0.21398 | 0.22122 | 0.22862 | 0.23257 | 0.23708 | 0.23935 | 0.24164 | 0.24395 | 0.24627 | 0.24862 | 0.25098
Striker DS | 0.034877 | 0.077071 | 0.1147 | 0.17781 | 0.23204 | 0.28014 | 0.30336 | 0.3254 | 0.34512 | 0.35687 | 0.36942 | 0.38226 | 0.38868 | 0.39565 | 0.39928 | 0.40294 | 0.40663 | 0.41034 | 0.41408 | 0.41784
Verner DS | 0.045923 | 0.099641 | 0.1474 | 0.23737 | 0.31383 | 0.37988 | 0.40271 | 0.42488 | 0.44476 | 0.45738 | 0.47144 | 0.48569 | 0.49426 | 0.50503 | 0.50999 | 0.51499 | 0.52004 | 0.52513 | 0.53026 | 0.53543
Warren DS | 0.056537 | 0.12344 | 0.18309 | 0.29171 | 0.38452 | 0.46549 | 0.49703 | 0.52749 | 0.55487 | 0.57208 | 0.59098 | 0.61022 | 0.62138 | 0.63475 | 0.64143 | 0.64819 | 0.655 | 0.66188 | 0.66882 | 0.67584
Wharncliffe DS | 0.032332 | 0.073065 | 0.10984 | 0.1645 | 0.21267 | 0.25721 | 0.28627 | 0.3138 | 0.33875 | 0.35379 | 0.36945 | 0.38566 | 0.39361 | 0.40103 | 0.40631 | 0.41164 | 0.41704 | 0.42249 | 0.42801 | 0.43208
Whitefish DS | 0.053761 | 0.11645 | 0.17201 | 0.2767 | 0.36539 | 0.44166 | 0.46745 | 0.49242 | 0.51467 | 0.52851 | 0.54397 | 0.55961 | 0.56869 | 0.5803 | 0.58518 | 0.59011 | 0.59506 | 0.60005 | 0.60508 | 0.61014
Total Region | 3.0525 | 6.8221 | 10.2197 | 16.0951 | 21.286 | 25.8305 | 27.8287 | 29.7926 | 31.597 | 32.7168 | 33.8596 | 35.1455 | 35.852 | 36.6799 | 37.1601 | 37.6567 | 38.1405 | 38.6261 | 39.1351 | 39.63

## Table 3
Peak demand contribution from contracted, existing distributed generation was estimated based on technology type and totalled for each station in the region. The resulting forecast savings were applied to gross demand to help determine the net peak demand for the IRRP planning forecast. Additional details on the overall IRRP forecast methodology are provided in the methodology document.
Transformer Station | Table 3 Effective DG Contribution to Coincident Peak (MW) - Summer
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Clarabelle TS | 0.4968 | 0.4968 | 0.4968 | 0.4968 | 0.4968 | 0.4393 | 0.4393 | 0.3611 | 0.3059 | 0.2668 | 0.1725 | 0.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elliott Lake TS | 0.023 | 0.023 | 0.023 | 0.023 | 0.023 | 0.023 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Espanola TS | 0.1725 | 0.1725 | 0.1725 | 0.1725 | 0.1725 | 0.1725 | 0.1725 | 0.1725 | 0.1725 | 0.1725 | 0.1725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Larchwood TS | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manitoulin TS | 0.96 | 0.96 | 0.96 | 0.96 | 0.48 | 0.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Martindale TS | 14.4451 | 12.9411 | 12.9411 | 12.9411 | 12.9411 | 12.0771 | 12.0771 | 12.0771 | 9.7127 | 9.7127 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
Massey DS | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Northshore DS | 2.5152 | 2.5152 | 2.5152 | 2.5152 | 1.056 | 1.056 | 1.056 | 1.056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sowerby DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spanish DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Striker DS | 1.1408 | 1.1408 | 1.1408 | 1.1408 | 1.1408 | 1.1408 | 1.1063 | 1.1063 | 1.1063 | 1.081 | 0.575 | 0.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Verner DS | 0.0805 | 0.0805 | 0.0805 | 0.0805 | 0.0805 | 0.0805 | 0.0805 | 0.0805 | 0.0805 | 0.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warren DS | 0.0161 | 0.0161 | 0.0161 | 0.0161 | 0.0161 | 0.0161 | 0.0161 | 0.0161 | 0.0161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wharncliffe DS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Whitefish DS | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0.115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Region | 20.195 | 18.691 | 18.691 | 18.691 | 16.7518 | 15.8303 | 15.3158 | 15.2146 | 11.739 | 11.6355 | 10.75 | 9.8875 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6

## Table 4
The IRRP planning forecast accounts for the median weather gross forecasts provided by the local distributors, savings from distributed generation and electrical demand management, as well as extreme weather adjustments. Additional details on the overall IRRP forecast methodology are provided in the methodology document.
Transformer Station | Table 4 Extreme-weather Net Coincident Demand - Reference Forecast (MW) - Summer
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Clarabelle TS | 122.3554 | 123.0227 | 124.1747 | 123.8057 | 123.6035 | 123.6679 | 124.2939 | 125.3159 | 127.8155 | 130.2328 | 131.822 | 134.3778 | 136.4929 | 138.9056 | 141.1542 | 143.5973 | 145.8557 | 148.119 | 150.482 | 152.7553
Elliott Lake TS | 14.0796 | 14.0217 | 13.9704 | 13.8121 | 13.6921 | 13.6016 | 13.616 | 13.6589 | 13.6891 | 13.7519 | 13.8122 | 13.8721 | 13.9583 | 14.0427 | 14.1415 | 14.2409 | 14.3408 | 14.4413 | 14.5424 | 14.644
Espanola TS | 10.5172 | 10.4874 | 10.4621 | 10.3463 | 10.2612 | 10.1991 | 10.2291 | 10.2618 | 10.3008 | 10.3592 | 10.415 | 10.6432 | 10.7142 | 10.7818 | 10.862 | 10.9424 | 11.0232 | 11.1043 | 11.1858 | 11.2675
Larchwood TS | 17.9416 | 17.9514 | 17.9688 | 17.8384 | 17.7581 | 17.7146 | 17.8211 | 17.9336 | 18.0585 | 18.2217 | 18.3816 | 18.657 | 18.8486 | 19.0367 | 19.2469 | 19.459 | 19.6729 | 19.8887 | 20.1064 | 20.326
Manitoulin TS | 23.0283 | 23.0758 | 23.1334 | 22.996 | 23.4043 | 23.3808 | 24.035 | 24.2178 | 24.4179 | 24.6709 | 24.9201 | 25.1707 | 25.465 | 25.7558 | 26.0771 | 26.4017 | 26.7297 | 27.0612 | 27.3961 | 27.7346
Martindale TS | 111.1903 | 120.3397 | 123.2762 | 124.9266 | 128.5741 | 131.4821 | 132.5961 | 134.1465 | 137.1066 | 137.9367 | 138.8544 | 140.3692 | 142.1754 | 144.0563 | 146.2589 | 148.4634 | 150.67 | 152.8786 | 155.2927 | 157.607
Massey DS | 3.9347 | 3.9176 | 3.9059 | 3.8598 | 3.8254 | 3.7999 | 3.8099 | 3.8208 | 3.8341 | 3.8543 | 3.8735 | 4.0078 | 4.0326 | 4.056 | 4.0842 | 4.1126 | 4.1411 | 4.1698 | 4.1987 | 4.2277
Northshore DS | 1.816 | 1.8061 | 1.8023 | 1.7818 | 3.2282 | 3.2187 | 3.2204 | 3.2261 | 4.2934 | 4.325 | 4.3567 | 4.3879 | 4.4363 | 4.4881 | 4.542 | 4.5965 | 4.6517 | 4.7074 | 4.7638 | 4.8208
Sowerby DS | 2.6882 | 2.6809 | 2.6762 | 2.6482 | 2.627 | 2.6108 | 2.6166 | 2.6225 | 2.6293 | 2.6404 | 2.651 | 2.6614 | 2.6757 | 2.6892 | 2.7057 | 2.7222 | 2.7388 | 2.7554 | 2.772 | 2.7886
Spanish DS | 2.0824 | 2.079 | 2.0781 | 2.0603 | 2.0479 | 2.0397 | 2.0484 | 2.0578 | 2.0687 | 2.084 | 2.0989 | 2.1138 | 2.1324 | 2.1506 | 2.1712 | 2.1919 | 2.2129 | 2.234 | 2.2552 | 2.2766
Striker DS | 2.2497 | 2.2416 | 2.2377 | 2.208 | 2.1869 | 2.1722 | 2.217 | 2.2287 | 2.243 | 2.2908 | 2.8187 | 3.1856 | 3.4441 | 3.4724 | 3.5043 | 3.5364 | 3.5687 | 3.6013 | 3.6341 | 3.6672
Verner DS | 4.6193 | 4.6136 | 4.6141 | 4.5727 | 4.5451 | 4.5283 | 4.5551 | 4.5829 | 4.6134 | 4.6746 | 4.7693 | 4.8067 | 4.8503 | 4.892 | 4.9401 | 4.9885 | 5.0374 | 5.0867 | 5.1364 | 5.1865
Warren DS | 5.6765 | 5.6717 | 5.6746 | 5.629 | 5.5997 | 5.5827 | 5.6157 | 5.6504 | 5.6888 | 5.754 | 5.802 | 5.8504 | 5.9074 | 5.9629 | 6.0257 | 6.0891 | 6.1531 | 6.2178 | 6.283 | 6.3489
Wharncliffe DS | 2.9878 | 2.9884 | 2.9933 | 2.9807 | 2.975 | 2.9733 | 2.9875 | 3.0037 | 3.0229 | 3.0526 | 3.082 | 3.1115 | 3.1497 | 3.1889 | 3.2309 | 3.2733 | 3.3162 | 3.3596 | 3.4034 | 3.4358
Whitefish DS | 5.4599 | 5.4462 | 5.4398 | 5.3845 | 5.3454 | 5.319 | 5.3434 | 5.3689 | 5.3975 | 5.4348 | 5.5859 | 5.6221 | 5.6652 | 5.7062 | 5.7542 | 5.8026 | 5.8514 | 5.9005 | 5.9499 | 5.9997
Total LDC Demand | 330.627 | 340.3437 | 344.4077 | 344.85 | 349.6739 | 352.2909 | 355.0053 | 358.0964 | 365.1795 | 369.2836 | 373.2433 | 378.8371 | 383.9482 | 389.1852 | 394.6989 | 400.4181 | 405.9637 | 411.5255 | 417.4019 | 423.0861
Total CTS* Demand | 297.7875 | 300.7386 | 302.7175 | 306.5144 | 319.6619 | 323.9033 | 325.7983 | 327.689 | 333.8526 | 335.7813 | 337.7292 | 339.6967 | 341.6838 | 343.6908 | 345.7179 | 347.7652 | 349.833 | 351.9215 | 354.0308 | 356.1613
Total Region Demand | 628.4145 | 641.0823 | 647.1252 | 651.3644 | 669.3358 | 676.1941 | 680.8036 | 685.7854 | 699.0321 | 705.0649 | 710.9726 | 718.5338 | 725.632 | 732.876 | 740.4167 | 748.1833 | 755.7967 | 763.447 | 771.4327 | 779.2474
*CTS is the abbreviation of: Customer Transformer Station

## Table 5
The IRRP planning forecast accounts for the median weather gross forecasts provided by the local distributors, savings from distributed generation and electrical demand management, as well as extreme weather adjustments. Additional details on the overall IRRP forecast methodology are provided in the methodology document.
Transformer Station | Table 5 Extreme-weather Net Coincident Demand - High Growth Scenario (MW) - Summer
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Clarabelle TS | 122.5725 | 123.5659 | 125.0507 | 125.021 | 125.165 | 125.4804 | 126.5686 | 127.9578 | 130.8319 | 133.7332 | 135.7119 | 140.0948 | 144.0449 | 147.9939 | 151.8892 | 156.0894 | 160.011 | 164.0482 | 168.0917 | 171.952
Elliott Lake TS | 14.1502 | 14.1645 | 14.1868 | 14.1034 | 14.0597 | 14.0471 | 14.1408 | 14.2645 | 14.3769 | 14.5236 | 14.6692 | 14.816 | 14.9906 | 15.1651 | 15.3556 | 15.5483 | 15.7433 | 15.9404 | 16.1399 | 16.3416
Espanola TS | 10.5707 | 10.5956 | 10.6261 | 10.5674 | 10.5404 | 10.5376 | 10.6281 | 10.7224 | 10.8242 | 10.9466 | 11.0677 | 11.3624 | 11.5013 | 11.6379 | 11.7883 | 11.9404 | 12.0941 | 12.2494 | 12.4064 | 12.5651
Larchwood TS | 18.0316 | 18.1342 | 18.2469 | 18.2145 | 18.2348 | 18.2947 | 18.5072 | 18.7285 | 18.9652 | 19.2429 | 19.5203 | 19.9163 | 20.2314 | 20.5461 | 20.8862 | 21.2313 | 21.5815 | 21.9369 | 22.2975 | 22.6635
Manitoulin TS | 23.1478 | 23.3187 | 23.5035 | 23.4971 | 24.0405 | 24.156 | 24.9532 | 25.2832 | 25.6347 | 26.0434 | 26.4528 | 26.8679 | 27.3314 | 27.796 | 28.2959 | 28.8039 | 29.3204 | 29.8452 | 30.3787 | 30.921
Martindale TS | 111.4217 | 121.1345 | 124.7485 | 127.0813 | 133.8116 | 137.3036 | 140.7489 | 143.4383 | 146.9986 | 148.6522 | 151.161 | 154.2724 | 158.2254 | 162.3677 | 166.4021 | 170.5533 | 174.6037 | 178.7711 | 182.9324 | 187.0002
Massey DS | 3.955 | 3.9586 | 3.968 | 3.9433 | 3.9308 | 3.9277 | 3.9604 | 3.9945 | 4.0313 | 4.0755 | 4.1192 | 4.2784 | 4.3285 | 4.3777 | 4.4322 | 4.4873 | 4.543 | 4.5994 | 4.6564 | 4.714
Northshore DS | 1.8376 | 1.85 | 1.8692 | 1.8723 | 3.343 | 3.3585 | 3.3859 | 3.418 | 4.5125 | 4.5719 | 4.6323 | 4.693 | 4.7716 | 4.8544 | 4.9402 | 5.0275 | 5.1162 | 5.2065 | 5.2982 | 5.3915
Sowerby DS | 2.7016 | 2.7081 | 2.7175 | 2.7038 | 2.6973 | 2.6959 | 2.7169 | 2.7382 | 2.7607 | 2.7878 | 2.8145 | 2.8414 | 2.8724 | 2.9029 | 2.9366 | 2.9707 | 3.0051 | 3.0398 | 3.0748 | 3.1101
Spanish DS | 2.0928 | 2.1001 | 2.1102 | 2.1035 | 2.1026 | 2.1062 | 2.1269 | 2.1486 | 2.1721 | 2.2003 | 2.2284 | 2.2568 | 2.2892 | 2.3215 | 2.3565 | 2.3921 | 2.4281 | 2.4646 | 2.5016 | 2.5391
Striker DS | 2.2666 | 2.2759 | 2.2899 | 2.2784 | 2.2759 | 2.2802 | 2.3446 | 2.3763 | 2.4109 | 2.4796 | 3.0289 | 3.4175 | 3.6984 | 3.7494 | 3.8046 | 3.8604 | 3.9171 | 3.9744 | 4.0326 | 4.0915
Verner DS | 4.6428 | 4.6611 | 4.6863 | 4.6702 | 4.6685 | 4.6783 | 4.7322 | 4.7879 | 4.8469 | 4.9373 | 5.0618 | 5.1298 | 5.2046 | 5.2784 | 5.3591 | 5.441 | 5.5241 | 5.6084 | 5.6938 | 5.7805
Warren DS | 5.7049 | 5.7293 | 5.7622 | 5.7473 | 5.7495 | 5.7649 | 5.8311 | 5.8998 | 5.973 | 6.074 | 6.1586 | 6.2445 | 6.3399 | 6.4348 | 6.5379 | 6.6426 | 6.7489 | 6.8568 | 6.9664 | 7.0776
Wharncliffe DS | 3.0027 | 3.0186 | 3.0394 | 3.0432 | 3.0543 | 3.0701 | 3.1022 | 3.1369 | 3.1752 | 3.2244 | 3.274 | 3.3242 | 3.3838 | 3.445 | 3.5095 | 3.5752 | 3.642 | 3.7099 | 3.779 | 3.836
Whitefish DS | 5.4878 | 5.5026 | 5.5253 | 5.4998 | 5.4912 | 5.4959 | 5.5521 | 5.6101 | 5.6718 | 5.7429 | 5.9285 | 6 | 6.0791 | 6.1568 | 6.2424 | 6.329 | 6.4168 | 6.5056 | 6.5957 | 6.6868
Total LDC Demand | 331.5863 | 342.7177 | 348.3304 | 350.3466 | 359.1652 | 363.1971 | 369.2991 | 374.5051 | 383.186 | 389.2357 | 395.8291 | 405.5154 | 415.2925 | 425.0277 | 434.7364 | 444.8925 | 454.6951 | 464.7566 | 474.845 | 484.6705
Total CTS* Demand | 306.3375 | 321.8886 | 330.2575 | 334.0544 | 347.2019 | 351.4433 | 353.3383 | 355.229 | 361.3926 | 363.3213 | 365.2692 | 367.2367 | 369.2238 | 371.2308 | 373.2579 | 375.3052 | 377.373 | 379.4615 | 381.5708 | 383.7013
Total Region Demand | 637.9238 | 664.6063 | 678.5879 | 684.401 | 706.3672 | 714.6404 | 722.6374 | 729.734 | 744.5787 | 752.5569 | 761.0983 | 772.7521 | 784.5163 | 796.2585 | 807.9943 | 820.1976 | 832.0681 | 844.2181 | 856.4158 | 868.3718
*CTS is the abbreviation of: Customer Transformer Station
Note on B22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: why do we include CTS for table 5 but then stop for table 6?

## Table 6
The IRRP planning forecast accounts for the median weather gross forecasts provided by the local distributors, savings from distributed generation and electrical demand management, as well as extreme weather adjustments. Additional details on the overall IRRP forecast methodology are provided in the methodology document.
Transformer Station | Table 6 Extreme-weather Net Non-coincident Demand - Reference Forecast - Summer
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Clarabelle TS | 130.4998 | 131.2929 | 132.5951 | 132.3294 | 132.2242 | 132.3858 | 133.0958 | 134.2223 | 136.9275 | 139.5305 | 141.2454 | 143.9942 | 146.2626 | 148.8555 | 151.2648 | 153.8823 | 156.3019 | 158.7269 | 161.2586 | 163.6942
Elliott Lake TS | 14.7187 | 14.6659 | 14.6194 | 14.4656 | 14.3501 | 14.2644 | 14.2836 | 14.3312 | 14.3662 | 14.4338 | 14.4989 | 14.5637 | 14.6547 | 14.7441 | 14.8478 | 14.9522 | 15.0571 | 15.1626 | 15.2687 | 15.3754
Espanola TS | 10.6349 | 10.6062 | 10.5818 | 10.467 | 10.3828 | 10.3216 | 10.3526 | 10.3862 | 10.4262 | 10.4855 | 10.5422 | 10.7714 | 10.8434 | 10.912 | 10.9931 | 11.0745 | 11.1563 | 11.2383 | 11.3208 | 11.4035
Larchwood TS | 21.2392 | 21.2901 | 21.3459 | 21.2541 | 21.2126 | 21.2083 | 21.3541 | 21.5064 | 21.6714 | 21.8749 | 22.0755 | 22.3921 | 22.6251 | 22.855 | 23.1074 | 23.362 | 23.6188 | 23.8779 | 24.1392 | 24.4028
Manitoulin TS | 24.8441 | 24.9169 | 24.9984 | 24.8851 | 25.3177 | 25.3187 | 25.9975 | 26.2053 | 26.4305 | 26.7089 | 26.9838 | 27.2602 | 27.5807 | 27.898 | 28.2459 | 28.5976 | 28.9529 | 29.3119 | 29.6747 | 30.0413
Martindale TS | 111.1903 | 120.3397 | 123.2762 | 124.9266 | 128.5741 | 131.4821 | 132.5961 | 134.1465 | 137.1066 | 137.9367 | 138.8544 | 140.3692 | 142.1754 | 144.0563 | 146.2589 | 148.4634 | 150.67 | 152.8786 | 155.2927 | 157.607
Massey DS | 4.2961 | 4.2816 | 4.2725 | 4.229 | 4.1972 | 4.1744 | 4.187 | 4.2006 | 4.2165 | 4.2394 | 4.2613 | 4.3983 | 4.4259 | 4.452 | 4.483 | 4.5141 | 4.5454 | 4.5769 | 4.6086 | 4.6404
Northshore DS | 4.9409 | 4.9709 | 5.0069 | 5.026 | 6.5121 | 6.5425 | 6.5845 | 6.631 | 7.7396 | 7.8127 | 7.8865 | 7.9603 | 8.0516 | 8.1469 | 8.2448 | 8.3438 | 8.4439 | 8.5451 | 8.6474 | 8.7509
Sowerby DS | 4.5373 | 4.5466 | 4.5578 | 4.5451 | 4.5386 | 4.5366 | 4.5561 | 4.5752 | 4.5948 | 4.6183 | 4.6412 | 4.664 | 4.6907 | 4.7166 | 4.7456 | 4.7746 | 4.8036 | 4.8327 | 4.8618 | 4.891
Spanish DS | 2.5059 | 2.5069 | 2.5104 | 2.4968 | 2.4887 | 2.4849 | 2.4979 | 2.5116 | 2.5269 | 2.5466 | 2.566 | 2.5854 | 2.6085 | 2.6313 | 2.6565 | 2.6819 | 2.7075 | 2.7333 | 2.7593 | 2.7855
Striker DS | 4.4185 | 4.432 | 4.4494 | 4.4409 | 4.4408 | 4.4471 | 4.5132 | 4.5463 | 4.5821 | 4.6515 | 5.2013 | 5.5901 | 5.8708 | 5.9214 | 5.9758 | 6.0305 | 6.0857 | 6.1412 | 6.1972 | 6.2536
Verner DS | 4.9601 | 4.9579 | 4.9618 | 4.9239 | 4.8999 | 4.8866 | 4.9169 | 4.9484 | 4.9825 | 5.0474 | 5.1457 | 5.1868 | 5.2341 | 5.2797 | 5.3315 | 5.3838 | 5.4366 | 5.4897 | 5.5434 | 5.5975
Warren DS | 6.2639 | 6.2655 | 6.2748 | 6.2356 | 6.2128 | 6.2024 | 6.242 | 6.2833 | 6.3284 | 6.4004 | 6.4553 | 6.5105 | 6.5745 | 6.637 | 6.707 | 6.7775 | 6.8488 | 6.9207 | 6.9934 | 7.0667
Wharncliffe DS | 3.4518 | 3.4587 | 3.47 | 3.4639 | 3.4647 | 3.4696 | 3.4905 | 3.5134 | 3.5394 | 3.5759 | 3.6123 | 3.6487 | 3.694 | 3.7405 | 3.7897 | 3.8394 | 3.8897 | 3.9406 | 3.992 | 4.0301
Whitefish DS | 5.8897 | 5.8798 | 5.8771 | 5.8256 | 5.7903 | 5.7677 | 5.796 | 5.8254 | 5.8578 | 5.899 | 6.054 | 6.0942 | 6.1413 | 6.1863 | 6.2384 | 6.2908 | 6.3437 | 6.3969 | 6.4505 | 6.5044

## Table 7
The IRRP planning forecast accounts for the median weather gross forecasts provided by the local distributors, savings from distributed generation and electrical demand management, as well as extreme weather adjustments. Additional details on the overall IRRP forecast methodology are provided in the methodology document.
Transformer Station | Table 7 Extreme-weather Net Non-coincident Demand - High Growth Scenario - Summer
| 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
Clarabelle TS | 130.7312 | 131.8718 | 133.5286 | 133.6246 | 133.8883 | 134.3174 | 135.52 | 137.0379 | 140.1422 | 143.2611 | 145.3909 | 150.087 | 154.3109 | 158.5414 | 162.7055 | 167.1955 | 171.3878 | 175.7033 | 180.0259 | 184.1529
Elliott Lake TS | 14.7925 | 14.8152 | 14.8454 | 14.77 | 14.7343 | 14.7299 | 14.8319 | 14.964 | 15.0848 | 15.2401 | 15.3943 | 15.5499 | 15.7334 | 15.9168 | 16.1164 | 16.3182 | 16.5224 | 16.7289 | 16.9378 | 17.1491
Espanola TS | 10.689 | 10.7156 | 10.7476 | 10.6904 | 10.665 | 10.6638 | 10.7559 | 10.8518 | 10.9553 | 11.0794 | 11.2021 | 11.4985 | 11.639 | 11.7774 | 11.9295 | 12.0833 | 12.2388 | 12.3959 | 12.5547 | 12.7153
Larchwood TS | 21.3455 | 21.506 | 21.6743 | 21.6982 | 21.7755 | 21.8932 | 22.1643 | 22.445 | 22.7419 | 23.0807 | 23.4202 | 23.879 | 24.2579 | 24.6373 | 25.043 | 25.4547 | 25.8724 | 26.2964 | 26.7265 | 27.163
Manitoulin TS | 24.9725 | 25.178 | 25.3962 | 25.4238 | 26.0015 | 26.1519 | 26.9845 | 27.3505 | 27.7385 | 28.1843 | 28.6313 | 29.0846 | 29.587 | 30.0911 | 30.631 | 31.1798 | 31.7376 | 32.3046 | 32.8808 | 33.4665
Martindale TS | 111.4217 | 121.1345 | 124.7485 | 127.0813 | 133.8116 | 137.3036 | 140.7489 | 143.4383 | 146.9986 | 148.6522 | 151.161 | 154.2724 | 158.2254 | 162.3677 | 166.4021 | 170.5533 | 174.6037 | 178.7711 | 182.9324 | 187.0002
Massey DS | 4.3182 | 4.3262 | 4.34 | 4.3199 | 4.312 | 4.3135 | 4.3508 | 4.3896 | 4.4312 | 4.4802 | 4.5288 | 4.6928 | 4.7479 | 4.8021 | 4.8617 | 4.9219 | 4.9828 | 5.0444 | 5.1067 | 5.1697
Northshore DS | 4.978 | 5.0461 | 5.1215 | 5.1811 | 6.7087 | 6.782 | 6.868 | 6.9598 | 8.1148 | 8.2358 | 8.3587 | 8.4829 | 8.626 | 8.7745 | 8.927 | 9.0821 | 9.2398 | 9.4 | 9.563 | 9.7287
Sowerby DS | 4.5599 | 4.5923 | 4.6272 | 4.6386 | 4.6567 | 4.6797 | 4.7248 | 4.7698 | 4.8157 | 4.866 | 4.9161 | 4.9665 | 5.0214 | 5.0758 | 5.1338 | 5.1923 | 5.2513 | 5.3108 | 5.3708 | 5.4314
Spanish DS | 2.5184 | 2.5322 | 2.5488 | 2.5488 | 2.5545 | 2.5647 | 2.5922 | 2.6207 | 2.6511 | 2.6864 | 2.7216 | 2.7572 | 2.7969 | 2.8366 | 2.8792 | 2.9223 | 2.966 | 3.0103 | 3.0553 | 3.1008
Striker DS | 4.4461 | 4.488 | 4.5346 | 4.5558 | 4.5861 | 4.6236 | 4.7215 | 4.7872 | 4.8564 | 4.9599 | 5.5445 | 5.969 | 6.2861 | 6.3738 | 6.4662 | 6.5597 | 6.6545 | 6.7506 | 6.8479 | 6.9465
Verner DS | 4.9853 | 5.0088 | 5.0393 | 5.0284 | 5.0322 | 5.0473 | 5.1068 | 5.1681 | 5.2328 | 5.3289 | 5.4593 | 5.5331 | 5.6139 | 5.6937 | 5.7807 | 5.8688 | 5.9582 | 6.0489 | 6.1409 | 6.2342
Warren DS | 6.2953 | 6.329 | 6.3713 | 6.366 | 6.378 | 6.4032 | 6.4794 | 6.5582 | 6.6417 | 6.7531 | 6.8483 | 6.9449 | 7.0513 | 7.1572 | 7.2715 | 7.3876 | 7.5055 | 7.6251 | 7.7466 | 7.8698
Wharncliffe DS | 3.469 | 3.4936 | 3.5232 | 3.536 | 3.5562 | 3.5812 | 3.6228 | 3.667 | 3.715 | 3.7741 | 3.8338 | 3.8942 | 3.9641 | 4.0359 | 4.1111 | 4.1877 | 4.2656 | 4.3448 | 4.4253 | 4.4917
Whitefish DS | 5.9197 | 5.9405 | 5.9692 | 5.9498 | 5.9473 | 5.9582 | 6.0206 | 6.0849 | 6.153 | 6.2307 | 6.4228 | 6.5009 | 6.5868 | 6.6713 | 6.7638 | 6.8574 | 6.9522 | 7.0483 | 7.1456 | 7.2441

## Table 8
The starting points used to develop the IRRP planning forecast were based off of the historical weather-corrected gross coincident demand (MW).
Transformer Station | Table 8 Historical Weather-Corrected Gross Coincident Demand (MW) - Summer
| 2021 | 2022 | 2023 | 2024 | 2025
Clarabelle TS | 95.1172 | 95.4463 | 99.3479 | 102.114 | 109.8396
Elliott Lake TS | 13.1394 | 12.5355 | 12.443 | 13.0056 | 12.1974
Espanola TS | 9.6197 | 8.8337 | 8.9379 | 9.415 | 9.934
Larchwood TS | 10.2135 | 9.8538 | 9.8966 | 10.2918 | 10.437
Manitoulin TS | 20.0059 | 18.2879 | 19.0614 | 23.2974 | 22.1943
Martindale TS | 126.8698 | 111.957 | 110.626 | 109.5354 | 115.2676
Massey DS | 3.1094 | 2.8815 | 3.371 | 3.4654 | 4.0553
Northshore DS | 1.0473 | 1.8824 | 5.1133 | 3.7785 | 4.9984
Sowerby DS | 1.3064 | 0.010516 | 1.2989 | 1.4196 | 1.4146
Spanish DS | 2.0405 | 1.8824 | 1.8865 | 2.0458 | 2.232
Striker DS | 2.3428 | 1.0096 | 4.237 | 3.7159 | 4.464
Verner DS | 3.8328 | 3.6176 | 3.7525 | 4.3526 | 4.5269
Warren DS | 4.8044 | 4.5746 | 4.7731 | 5.3233 | 5.5014
Wharncliffe DS | 3.0878 | 4.0593 | 3.0721 | 3.1314 | 2.8503
Whitefish DS | 4.7397 | 4.4694 | 4.6184 | 5.219 | 5.4176
Total Region | 301.2766 | 281.3016 | 292.4356 | 300.1106 | 315.3303

## Table 9
The power factor is used to develop the IRRP planning forecast were based off of the historical measurements.
Transformer Station | Table 9 Historical Power Factor at the LV Terminal - Summer
| 2021 | 2022 | 2023 | 2024 | 2025 | Average
Clarabelle TS | 0.934 | 0.955 | 0.953 | 0.951 | 0.949 | 0.94864
Elliott Lake TS | 0.946 | 0.951 | 0.951 | 0.955 | 0.961 | 0.95293
Espanola TS | 0.923 | 0.922 | 0.922 | 0.953 | 0.957 | 0.93644
Larchwood TS | 0.965 | 0.987 | 0.963 | 0.967 | 0.96 | 0.96935
Manitoulin TS | 0.987 | 0.999 | 0.98 | 0.977 | 0.974 | 0.98559
Martindale TS | 0.952 | 0.941 | 0.952 | 0.941 | 0.947 | 0.94671
Massey DS | 0.975 | 0.993 | 0.98 | 0.984 | 0.975 | 0.98215
Northshore DS | 0.974 | 0.985 | 0.97 | 0.977 | 0.971 | 0.97573
Sowerby DS | -0.999 | 0.955 | -0.999 | -1 | -0.995 | 0.99975
Spanish DS | 0.985 | 0.992 | 0.978 | 0.992 | 0.982 | 0.98636
Striker DS | 0.989 | 0.989 | 0.987 | 0.985 | 0.988 | 0.98764
Verner DS | 0.996 | -1 | 0.999 | 0.997 | 0.98 | 0.99661
Warren DS | 0.959 | 0.964 | 0.965 | 0.957 | 0.97 | 0.96314
Wharncliffe DS | 0.994 | 0.996 | 0.997 | 1 | -0.998 | 0.99909
Whitefish DS | 0.991 | 0.993 | 0.993 | 0.992 | 0.994 | 0.99263
Note on C14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: there are a few negative numbers Reply: Yes this reflects a leading power factor based on billing data. I.e. all conductors have a capacitive effect which can result in leading pf when the station is not heavily loaded. Especially when there is a long distance of collector ckts as the B value is proportional to distance. we are not seeing significantly high leading pf, It looks like the highest may be -.99. This does however stress that .9 lag at the dmp is a little too conservative